Guide Specifications

High Wall Indoor Unit

Size Range:

Nominal Cooling Capacity Range: 7,500 to 24,000 Btu/h

Nominal Heating Capacity Range: 8,500 to 27,000 Btu/h

Toshiba Carrier Model Number:

MMK-AP---7HPUL

Part 1 - General

1.01 SYSTEM DESCRIPTION

Indoor, high wall mounted, direct-expansion indoor units are matched with heat pump or heat recovery VRF (variable refrigerant flow) outdoor unit.

1.02 QUALITY ASSURANCE

Unit shall be ETL (Engineering Testing Laboratory) listed and certified to UL 1995 4th edition standard.

1.03 DELIVERY, STORAGE, AND HANDLING

Units shall be stored and handled per unit manufacturer's recommendations.

1.04 Warranty (For Inclusion by Specifying Engineer)

Part 2 - Products

2.01 EQUIPMENT

A.	General:

Indoor, direct-expansion, wall-mounted fan coil. Unit shall be complete with coil, fan driven by DC inverter motor, PMV (pulse modulating valve), piping connectors, electrical controls, microprocessor control system, and integral temperature sensing. Unit shall be furnished with integral wall mounting bracket and mounting hardware.

B.	Unit Cabinet:

Cabinet discharge and inlet grilles shall be attractively styled, high-impact nonmetallic material.

C.	Fans:

1.	Fan shall be tangential direct-drive blower type with air intake at the top of the unit and discharge at the bottom front. Automatic, motor-driven vertical air sweep shall be standard.

2.	Vertical air sweep operation shall be user selectable using the remote control and the horizontal air direction may be set manually.

D.	Coil:

Coil shall be copper tube with aluminum fins and galvanized steel tube sheets. Fins shall be bonded to the tubes by mechanical expansion and specially coated for enhanced wettability.  A drip pan under the coil shall have a factory-installed drain connection (on both ends) for hose attachment to remove condensate.

E.	Motors:

Motors shall be totally enclosed, permanently lubricated ball bearing with inherent overload protection. Fan motors shall be inverter controlled variable speed.

F.	Controls:

The system shall be microprocessor-controlled to maintain precise room temperature and minimum power consumption. The controls system shall employ a genetic algorithm for temperature control.

Any of the following user interface accessories shall be compatible with the unit.

1.	Wireless Remote Controller

Wireless remote controller kit shall include a handheld device and a receiver integral to the unit.

2.	Wired Remote Controller

Wired remote controller shall communicate over two-core shielded wire up to 1640 ft. It shall be capable of controlling groups of up to 8 indoor units. It shall be able to operate as a primary or secondary controller when two remote controllers are connected to a single indoor unit or group. The system shall be able to be configured so that the return air (TA) can be sensed at the unit, at the remote controller or through a remote sensor. The local controller shall minimally be able to control On-OFF, set point, mode, and be able to display system generated error codes.

3.	Central Controller (Smart Manager)

Central controller shall communicate over two-core shielded wire up to 6500 ft and use existing indoor – outdoor communication protocol to communicate. A single central controller shall be capable of controlling up to 128 indoor units individually with capability to program maximum of 10 setups for each day. It shall be able to create 2 indoor unit line-ups with 64 units on each line.  It shall provide master, weekly, four special day and monthly scheduling feature. During schedule operation, user can set the power status (ON/OFF), operation mode, temperature setup, and remote control operation, restricted / allowed, return back and ventilation operation. It shall provide a web interface for remote monitoring, control, and scheduling. It shall be capable of monitoring energy consumption for each tenant and generate monthly billing reports.

4.	Central Controller (Touch Screen)

Central controller shall communicate over two-core shielded wire up to 1600 ft and use existing indoor – outdoor communication protocol to communicate. A single central controller shall be capable of controlling up to 512 indoor units individually with capability to program maximum of 20 setups for each day. It shall provide master, weekly, five special day and monthly scheduling feature.  In addition, an optional digital I/O interface shall provide alarm, fire and locking signals. It shall provide a web interface for remote monitoring, control, and scheduling. It shall be capable of monitoring energy consumption for each tenant and generate monthly billing reports.

5.	Management Systems

The system shall be able to be controlled by BACnet* or LonWorks† protocols either directly or through an external gateway.

BACnet and LonWorks shall be able to control:

- ON / OFF

- operation mode

- fan speed

- louver

- set temperature

- permit / prohibit local operation

BACnet and LonWorks shall be able to monitor:

- ON / OFF

- operation mode

- fan speed

- louver

- set temperature

- permit / prohibit local operation

- room temperature

- error status

- error code

6.	The unit shall have the following functions as a minimum:

a.	Selectable automatic restart. After power failure the system will restart at the same operating conditions as before the failure.

b.	Temperature-sensing controls shall sense return air temperature at the unit or at the remote control

c.	Indoor coil freeze protection in both cooling and heating (reversing valve failure) modes.

d.	Automatic air sweep control to provide multiple operating modes of the air sweep louvers.

e.	Dehumidification mode shall provide increased latent removal through total system modulation.

f.	Fan-only operation to provide room air circulation when no cooling is required.

g.	Fan speed control shall be user-selectable: high, medium, low, or microprocessor determined (Auto) based on the differential between the room temperature and the set point during all modes of operations.

h.	Indoor coil high temperature protection shall be provided to detect excessive indoor discharge temperature in heating.

i.	Cold blow prevention in heating.

j.	Adjustable compensation for air stratification in heating.

G.	Filters:

Unit shall have factory-supplied resin net (cleanable) type filters. The return air filter material shall have the following characteristics:

1.	Odorless

2.	Temperature resistant to 185 F

3.	Humidity resistant up to 95% RH

H.	Electrical Requirements:

Indoor units are 208/230-1-60 (V-Ph-Hz).

I.	Special Features (Accessories):

Condensate pump