Guide Specifications

Floor Console Exposed Indoor Unit

Size Range:

Nominal Cooling Capacity Range: 7,500 to 24,000 Btu/h

Nominal Heating Capacity Range: 8,500 to 27,000 Btu/h

Toshiba Carrier Model Number:

MML-UP---1H-UL

Part 1 - General

1.01 SYSTEM DESCRIPTION

Indoor, floor console exposed, direct-expansion units are matched with a heat pump or a heat recovery VRF (variable refrigerant flow) outdoor unit.

1.02 QUALITY ASSURANCE

Unit shall be ETL (Engineering Testing Laboratory) listed and certified to UL 60335-2-40 3rd edition standard.

1.03 DELIVERY, STORAGE, AND HANDLING

Units shall be stored and handled per unit manufacturer's recommendations.

1.04 WARRANTY (For Inclusion by Specifying Engineer)

Part 2 - Products

2.01 EQUIPMENT

A.	General:

Indoor, direct-expansion, floor console exposed fan coils. Unit shall be complete with a coil, fan driven by AC induction motor, PMV (pulse modulating valve), piping connectors, electrical controls, microprocessor control system, integral temperature sensing, and hanging brackets.

B.	Unit Cabinet:

Cabinet shall be constructed of zinc-coated steel and configured for bottom return.

C.	Fans:

The fan shall be of the multi-blade type with performance designed to match the coil performance. The fan shall be statically and dynamically balanced to ensure low noise and vibration.

D.	Coil:

Coil shall be copper tube with aluminum fins and galvanized steel tube sheets. Fins shall be bonded to the tubes by mechanical expansion and specially coated for enhanced wettability. A drip pan under the coil shall have a factory-installed drain connection for hose attachment to remove condensate.

E.	Motors:

Motors shall be totally enclosed, permanently lubricated ball bearing with inherent overload protection.

F.	Controls:

The system shall be microprocessor controlled to maintain precise room temperature and minimum power consumption. The controls system shall employ a genetic algorithm for temperature control.

Any of the following user interface accessories shall be compatible with the unit.

- Wired Remote Controller

Wired remote controller shall communicate over two-core shielded wire up to 1640 ft. It shall be capable of controlling groups of up to 8 indoor units. It shall be able to operate as a primary or secondary controller when two remote controllers are connected to a single indoor unit or group. The system shall be able to be configured so that the return air (TA) can be sensed at the unit, at the remote controller or through a remote sensor. The local controller shall minimally be able to control On-OFF, set point, mode, and be able to display system generated error codes.

- Central Controller

Central controller shall communicate over two-core shielded wire up to 6500 ft and use existing indoor – outdoor communication protocol to communicate. A single central controller shall be capable of controlling up to 256 indoor units individually with capability to program multiple schedules. It shall be able to create 2 indoor unit line-ups with 128 units on each line.  It shall provide weekly, special day and operational scheduling feature. During schedule operation, user can set the power status (ON/OFF), operation mode, temperature setup, and remote-control operation, restricted / allowed, return back and ventilation operation. It shall provide a web interface for remote monitoring, control, and scheduling. It shall be capable of monitoring energy consumption for each tenant and generate monthly KW usage reports. In addition, an optional digital I/O interface shall provide alarm, fire and locking signals.

3.	Building Management Systems

The system shall be able to be controlled by BACnet* or LonWorks† protocols either directly or through an external gateway.

BACnet and LonWorks shall be able to control:

- ON / OFF

- operation mode

- fan speed

- louver

- set temperature

- permit / prohibit local operation

BACnet and LonWorks shall be able to monitor:

- ON / OFF

- operation mode

- fan speed

- louver

- set temperature

- permit / prohibit local operation

- room temperature

- error status

- error code

5.	The unit shall have the following functions as a minimum:

- Selectable automatic restart. After power failure the system will restart at the same operating conditions as before the failure.

- Temperature-sensing controls shall sense return air temperature at the unit or at the remote control

- Indoor coil freeze protection in both cooling and heating (reversing valve failure) modes.

- Dehumidification (Dry) mode shall provide increased latent removal through total system modulation.

- Fan-only operation to provide room air circulation when no cooling is required.

- Fan speed control shall be user set to one of three speeds by using the taps on the motor.

- Indoor coil high temperature protection shall be provided to detect excessive indoor discharge temperature in heating.

- Cold blow prevention in heating.

- Adjustable compensation for air stratification in heating.

G.	Filters:

The filters shall be field supplied.

H.	Electrical Requirements:

Indoor units are 208/230-1-60 (V-Ph-Hz).