Guide Specifications

4-Way Cassette Indoor Unit

Size Range:

Nominal Cooling Capacity Range: 7,500 to 54,000 Btu/h

Nominal Heating Capacity Range: 8,500 to 60,000 Btu/h

Toshiba Carrier Model Number:

MMU-UP---1HP-UL

Part 1 - General

1.01 SYSTEM DESCRIPTION

Indoor, in-ceiling mounted, direct-expansion 4-way cassette units are matched with a heat pump or a heat recovery VRF (variable refrigerant flow) outdoor unit.

1.02 QUALITY ASSURANCE

Unit shall be ETL (Engineering Testing Laboratory) listed and certified to UL 60335-2-40 3rd edition standard.

1.03 DELIVERY, STORAGE, AND HANDLING

Units shall be stored and handled per unit manufacturer's recommendations.

1.04 WARRANTY (For Inclusion by Specifying Engineer)

Part 2 - Products

2.01 EQUIPMENT

A.	General:

Indoor, direct-expansion, low profile (10.1 in.) in-ceiling fan coil. Unit shall be complete with a coil, fan driven by DC inverter-motor, PMV (pulse modulating valve), piping connectors, electrical controls, microprocessor control system, integral temperature sensing, condensate lift mechanism with a lift capability of 26 in and hanging brackets.

B.	Unit Cabinet:

Cabinet shall be constructed of zinc-coated steel.  Fully insulated discharge and inlet grilles shall be attractively styled, high-impact non- metallic material. The inlet grille shall have hinges and can be opened to obtain access to the cleanable filters, indoor fan motor and control box. Fresh air can be introduced in two ways:

1. 	Use an auxiliary fresh air intake flange to condition the outside air before it is introduced into the space.

2. 	Use a fresh air inlet and filter chamber to introduce unconditioned outside into the space.

C.	Fans:

1.	Fan shall be centrifugal direct-drive blower type with air intake in the center of the unit and discharge at the perimeter. Automatic, motor-driven vertical air louver shall be provided standard.   Automatic motor-driven louvers shall be provided standard and shall be adjustable for 2, 3 or 4-way discharge.

2.	Air louver operation shall provide three user selectable modes.

D.	Coil:

Coil shall be copper tube with aluminum fins and galvanized steel tube sheets. Fins shall be bonded to the tubes by mechanical expansion and specially coated for enhanced wettability.  A drip pan under the coil shall have a factory-installed condensate lift mechanism with a lift capacity of 26” and drain connection for hose attachment to remove condensate.

E.	Motors:

Motors shall be totally enclosed, permanently lubricated ball bearing with inherent overload protection. Fan motors shall be inverter controlled variable speed.

F.	Controls:

The system shall be microprocessor-controlled to maintain precise room temperature and minimum power consumption. The controls system shall employ a genetic algorithm for temperature control

Any of the following user interface accessories shall be compatible with the unit.

1.	Wireless Remote Controller

Wireless remote controller kit shall include a handheld device and a receiver not integral to the unit. The receiver shall be field installed on the panel / grille or on the wall depending upon the type of kit selected.

- Wired Remote Controller

Wired remote controller shall communicate over two-core shielded wire up to 1640 ft. It shall be capable of controlling groups of up to 8 indoor units. It shall be able to operate as a primary or secondary controller when two remote controllers are connected to a single indoor unit or group. The system shall be able to be configured so that the return air (TA) can be sensed at the unit, at the remote controller or through a remote sensor. The local controller shall minimally be able to control On-OFF, set point, mode, and be able to display system generated error codes.

- Central Controller

Central controller shall communicate over two-core shielded wire up to 6500 ft and use existing indoor – outdoor communication protocol to communicate. A single central controller shall be capable of controlling up to 256 indoor units individually with capability to program multiple schedules. It shall be able to create 2 indoor unit line-ups with 128 units on each line.  It shall provide weekly, special day and operational scheduling feature. During schedule operation, user can set the power status (ON/OFF), operation mode, temperature setup, and remote-control operation, restricted / allowed, return back and ventilation operation. It shall provide a web interface for remote monitoring, control, and scheduling. It shall be capable of monitoring energy consumption for each tenant and generate monthly KW usage reports. In addition, an optional digital I/O interface shall provide alarm, fire and locking signals.

5.	Building Management Systems

The system shall be able to be controlled by BACnet* or LonWorks† protocols either directly or through an external gateway.

BACnet and LonWorks shall be able to control:

- ON / OFF

- operation mode

- fan speed

- louver

- set temperature

- permit / prohibit local operation

BACnet and LonWorks shall be able to monitor:

- ON / OFF

- operation mode

- fan speed

- louver

- set temperature

- permit / prohibit local operation

- room temperature

- error status

- error code

6.	The unit shall have the following functions as a minimum:

- Selectable automatic restart. After power failure the system will restart at the same operating conditions as before the failure.

- Temperature-sensing controls shall sense return air temperature at the unit or at the remote control

- Indoor coil freeze protection in both cooling and heating (reversing valve failure) modes.

- Automatic air sweep control to provide multiple operating modes of the air sweep louvers.

- Dehumidification (Dry) mode shall provide increased latent removal through total system modulation.

- Fan-only operation to provide room air circulation when no cooling is required.

- Fan speed control shall be user-selectable: high, medium, low, or microprocessor determined (Auto) based on the differential between the room temperature and the set point during all modes of operations.

- Indoor coil high temperature protection shall be provided to detect excessive indoor discharge temperature in heating.

- Cold blow prevention in heating.

- Adjustable compensation for air stratification in heating.

G.	Filters:

Unit shall have factory-supplied resin net (cleanable) type filters. The return air filter material shall have the following characteristics:

1.	Odorless

2.	Temperature resistant to 185 F

3.	Humidity resistant up to 95% RH

H.	Electrical Requirements:

Indoor units are 208/230-1-60 (V-Ph-Hz).

- Special Accessories (sold separately):

  - Ceiling Panel (Grille) – required for proper operation of the unit

  - Spacer for height adjustment

  - OA chamber

  - OA inlet box

  - Air discharge direction kit

  - Auxiliary OA flange