Note about this specification:

This specification is in the “Masterformat” as published by the Construction Specification Institute. Please feel free to copy this specification directly into your building spec.

WeatherExpert Ultra High-Efficiency Gas Heat/Electric Cooling Packaged Rooftop

HVAC Guide Specifications:

Size Range: 12.5 to 23 Nominal Tons

Carrier Model Number: 48LC

- 23 06 80 Schedules for Decentralized HVAC Equipment

- 23 06 80.13 Decentralized Unitary HVAC Equipment Schedule:

- 23 06 80.13.A. Rooftop unit schedule:

- Schedule is per the project specification requirements.

- 23 07 16 HVAC Equipment Insulation

- 23 07 16.13 Decentralized, Rooftop Units:

- 23 07 16.13.A. Evaporator fan compartment:

- Interior cabinet surfaces shall be insulated with a minimum 1/2-in. thick, minimum 1-1/2 lb density aluminum foil-faced insulation on the air side.

- Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

- Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

- 23 07 16.13.B. Gas heat compartment:

- Aluminum foil-faced fiberglass insulation shall be used.

- Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

- 23 09 13 Instrumentation and Control Devices for HVAC

- 23 09 13.23 Sensors and Transmitters:

- 23 09 13.23.A. Thermostats:

- Thermostat must

- energize both “W” and “G” when calling for heat.

- have capability to energize 3 different stages of cooling, and 2 different stages of heating.

- include capability for occupancy scheduling.

- 23 09 23 Direct Digital Control (DDC) System for HVAC

- 23 09 23.13 Decentralized, Rooftop Units:

- 23 09 23.13.A. SystemVu™ intelligent integrated Direct Digital Control (DDC) shall provide:

- Integrated unit operation for comfort cooling, heating ventilation as well as all monitoring, recording and reporting capabilities. Controller shall also provide diagnostics and alarms of abnormal unit operation through the controller. Controller shall have an intuitive user display and be able to be used in a standalone operation or via building automation system (BAS).

- Quick Unit Status LEDs of: Run – meaning all systems are go, ALERT - that indicates there is currently a non-critical issue with the unit, like filters need to be replaced and FAULT – that indicates the unit has a critical issue and will possibly shut down.

- Six large navigation keys for easy access. Navigation keys shall consist of: TEST, BACK, ENTER, and MENU along with UP and DOWN arrows.

- Full back lit user display with 4 line by 30 character text capabilities. Display menu shall be designed to provide guided major menus and sub menus main menus provided below:

- Shutdown Unit

- Run Status

- Settings

- Alerts/Faults

- Service

- Inputs

- Outputs

- USB

- The capability for standalone operation with conventional thermostat/sensor or use with building automation systems (BAS) of Carrier i-Vu®, BACnet and Carrier Comfort Network® (CCN) systems. No special modules or boards are required for these capabilities.

- The ability to read refrigerant pressures at display or via BAS network of; Discharge Pressure and Suction Pressure. The need for traditional refrigerant gages is not required.

- USB Data Port for flash drive interaction. This will allow the transfer of data for uploads, downloads, perform software upgrades, back-up and restore data and file transfer data such as component number of starts and run hours.

- Reverse Rotation Protection of compressors if field three phase wiring is misapplied.

- Provide Service Capabilities of:

- Auto run test

- Manual run test

- Component run hours and starts

- Commissioning reports

- Data logging

- Alarm history

- Economizer control and diagnostics. Set up economizer operation, receive feedback from actuator. Also meets the most recent California Title 24 Fault Detection and Diagnostic (FDD) requirements.

- Unit cooling operation down to 0°F (–18°C)

- Controller shall have easy access connections around the controller perimeter area and consist of Mate-N-Lok, terminal block and RJ style modular jack connections.

- 365 day real time clock, 20 holiday schedules along with occupied and unoccupied scheduling.

- Auto-Recognition for easy installation and commissioning of devices like economizers, space sensors, etc.

- A 5°F temperature difference between cooling and heating set points to meet the latest ASHRAE 90.1-2013 Energy Standard.

- Contain return air sensor, supply air sensor and outdoor air sensor to help monitor and provide data for the unit comfort operation, diagnostic and alarms.

- Use of Carrier’s field accessory hand-held Navigator™ display.

- Control of the operation of unit VFD (Variable Frequency Drive) to work in conjunction with the cooling, heating and ventilation modes.

- 3-year limited part warranty

- 23 09 23.13.B. RTU Open - multi-protocol, direct digital controller:

- Shall be ASHRAE 62 compliant.

- Shall accept 18-30VAC, 50-60Hz, and consume 15VA or less power.

- Shall have an operating temperature range from –40°F (–40°C) to 130°F (54°C), 10% - 90% RH (non-condensing).

- Shall include built-in protocol for BACnet (MS/TP and PTP modes), Modbus (RTU and ASCII), Johnson N2 and LonWorks. LonWorks Echelon processor required for all Lon applications shall be contained in separate communication board.

- Shall allow access of up to 62 network variables (SNVT). Shall be compatible with all open controllers.

- Baud rate Controller shall be selectable using a dipswitch.

- Shall have an LED display independently showing the status of serial communication, running, errors, power, all digital outputs, and all analog inputs.

- Shall accept the following inputs: space temperature, setpoint adjustment, outdoor air temperature, indoor air quality, outdoor air quality, compressor lock-out, fire shutdown, enthalpy switch, and fan status/filter status/ humidity/ remote occupancy.

- Shall provide the following outputs: economizer, fan, cooling stage 1, cooling stage 2, heat stage 1, heat stage 2, heat stage 3/ exhaust/ reversing valve.

- Shall have built-in surge protection circuitry through solid state polyswitches. Polyswitches shall be used on incoming power and network connections. Polyswitches will return to normal when the “trip” condition clears.

- Shall have a battery back-up capable of a minimum of 10,000 hours of data and time clock retention during power outages.

- Shall have built-in support for Carrier technician tool.

- Shall include an RS-485 protocol communication port, an access port for connection of either a computer or a Carrier technician tool, an EIA-485 port for network communication to intelligent space sensors and displays, and a port to connect an optional LonWorks communications card.

- Software upgrades will be accomplished by either local or remote download. No software upgrades through chip replacements are allowed.

- 23 09 33 Integrated Staging Control (ISC) Board System for HVAC (Electro-Mechanical units)

- 23 09 33.13 Decentralized, Rooftop Units:

- 23 09 33.13.A. General:

- Shall be complete with self-contained low-voltage control circuit protected by a resettable circuit breaker on the 24-v transformer side. Transformer shall have 75VA capability.

- Shall utilize color-coded wiring.

- Shall include an ISC electro-mechanical control board, to conveniently and safely provide connection points for vital control functions such as: smoke detectors, phase monitor, gas controller, economizer, thermostat, and safety switches. Shall control all three stages of compressor logic, two or three stages of the indoor fan motor logic as well as staging of the outdoor fan motor. Shall also have a green LED indicator to indicate GO operation as well as a fault LED indicator for thermostat mis-wiring, no fan operation and safety.
NOTE: Does not apply to units equipped with SystemVu™ controls.

- The heat exchanger shall be controlled by an integrated gas controller (IGC) microprocessor. See heat exchanger section of this specification.

- 23 09 33.13.B. Safeties:

- Compressor over-temperature, over-current. High internal pressure differential.

- Low-pressure Protection.

- Low-pressure switch shall use different color wire than the high-pressure switch. The purpose is to assist the installer and service technician to correctly wire and or troubleshoot the rooftop unit.
NOTE: Does not apply to units equipped with SystemVu controls.

- High-pressure Protection.

- High-pressure switch shall use different color wire than the low-pressure switch. The purpose is to assist the installer and service technician to correctly wire and or troubleshoot the rooftop unit.

- Automatic reset, motor thermal overload protector.

- Heating section shall be provided with the following minimum protections:

- High-temperature limit switches.

- Induced draft motor speed sensor.

- Flame rollout switch.

- Flame proving controls.

- 23 09 93 Sequence of Operations for HVAC Controls

- 23 09 93.13 Decentralized, Rooftop Units:

- 23 09 93.13.A. INSERT SEQUENCE OF OPERATION

- 23 40 13 Panel Air Filters

- 23 40 13.13 Decentralized, Rooftop Units:

- 23 40 13.13.A. Standard filter section:

- Shall consist of factory-installed, low velocity, disposable 2-in. thick fiberglass filters of commercially available sizes.

- Unit shall use only one filter size. Multiple sizes are not acceptable.

- Filters shall be accessible through a dedicated, weather tight access panel.

- 4-in. filter capabilities shall be capable with pre-engineered and approved Carrier filter track field-installed accessory. This kit requires field furnished filters.

- 23 81 19 Self-Contained Air Conditioners

- 23 81 19.13 Medium-Capacity Self-Contained Air Conditioners (48LC**14-26)

- 23 81 19.13.A. General:

- Outdoor, rooftop mounted, DDC electrically controlled, heating and cooling unit utilizing fully hermetic scroll compressors for cooling duty and gas combustion for heating duty.

- Factory assembled, single-piece heating and cooling rooftop unit. Contained within the unit enclosure shall be all factory wiring, piping, controls, and special features required prior to field start-up.

- Unit shall use Puron® (R-410A) refrigerant.

- Unit shall be installed in accordance with the manufacturer’s instructions.

- Unit must be selected and installed in compliance with local, state, and federal codes.

- 23 81 19.13.B. Quality Assurance:

- Unit meets and exceeds ASHRAE 90.1-2013 minimum efficiency requirements.

- Unit shall be rated in accordance with AHRI Standard 340/360.

- Unit shall be designed to conform to ASHRAE 15.

- Unit shall be ETL-tested and certified in accordance with ANSI Z21.47 Standards and ETL-listed and certified under Canadian standards as a total package for safety requirements.

- Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

- Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

- Unit casing shall be capable of withstanding 500-hour salt spray exposure per ASTM B117 (scribed specimen).

- Roof curb shall be designed to conform to NRCA Standards.

- Unit shall be subjected to a completely automated run test on the assembly line. The data for each unit will be stored at the factory, and must be available upon request.

- Unit shall be designed in accordance with UL Standard 1995, ETL listed including tested to withstand rain.

- Unit shall be constructed to prevent intrusion of snow and tested to prevent snow intrusion into the control box up to 40 mph.

- Unit shake tested to assurance level 1, ASTM D4169 to ensure shipping reliability.

- High-Efficiency Motors listed shall meet section 313 of the Energy Independence and Security Act of 2007 (EISA 2007).

- 23 81 19.13.C. Delivery, Storage, and Handling:

- Unit shall be stored and handled per manufacturer’s recommendations.

- Lifted by crane requires either shipping top panel or spreader bars.

- Unit shall only be stored or positioned in the upright position.

- 23 81 19.13.D. Project Conditions:

- As specified in the contract.

- 23 81 19.13.E. Operating Characteristics:

- Unit shall be capable of starting and running at 125°F (52°C) ambient outdoor temperature, meeting maximum load criteria of AHRI Standard 340/360 at ± 10% voltage.

- Compressor with standard controls shall be capable of operation down to 40°F (4°C), ambient outdoor temperatures. For lower operation, an integrated economizer shall be utilized to allow lower temperatures and accommodate indoor air quality initiatives.

- Unit shall discharge supply air vertically or horizontally as shown on contract drawings.

- Unit shall be factory configured and ordered for vertical supply and return configurations.

- Unit shall be factory furnished for either vertical or horizontal configuration without the use of special conversion kits. No field conversion is possible.

- 23 81 19.13.F. Electrical Requirements:

- Main power supply voltage, phase, and frequency must match those required by the manufacturer.

- 23 81 19.13.G. Unit Cabinet:

- Unit cabinet shall be constructed of galvanized steel, and shall be bonderized and coated with a pre-painted baked enamel finish on all externally exposed surfaces.

- Unit cabinet exterior paint shall be: film thickness, (dry) 0.003-in. minimum, gloss (per ASTM D523, 60°F / 16°C): 60, Hardness: H-2H Pencil hardness.

- Evaporator fan compartment interior cabinet insulation shall conform to AHRI Standard 340/360 minimum exterior sweat criteria. Interior surfaces shall be insulated with a minimum 1/2-in. thick, 1 lb density, aluminum foil-faced fiberglass insulation. Aluminum foil-faced fiberglass insulation shall also be used in the gas heat compartment.

- Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in -accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

- Base of unit shall have a minimum of four locations for thru-the-base gas and electrical connections standard. Both gas and electric connections shall be internal to the cabinet to protect from environmental issues.

- Base Rail:

- Unit shall have base rails on a minimum of 2 sides.

- Holes shall be provided in the base rails for rigging shackles to facilitate maneuvering and overhead rigging.

- Holes shall be provided in the base rail for moving the rooftop by fork truck.

- Base rail shall be a minimum of 16 gage thickness.

- Condensate Pan and Connections:

- Shall be a sloped condensate drain pan made of a non-corrosive material.

- Shall comply with ASHRAE Standard 62.

- Shall use a 3/4-in. -14 NPT drain connection, through the side of the drain pan. Connection shall be made per manufacturer’s recommendations.

- Top Panel:

- Shall be a multi-piece top panel linked with water tight flanges and locking systems.

- Gas Connections:

- All gas piping connecting to unit gas valve shall enter the unit cabinet at a single location on side of unit (horizontal plane).

- Thru-the-base capability

- Standard unit shall have a thru-the-base gas-line location using a raised, embossed portion of the unit basepan.

- Thru-the-base provisions/connections are available as standard with every unit. When bottom connections are required, field furnished couplings are required.

- No basepan penetration, other than those authorized by the manufacturer, is permitted.

- Electrical Connections:

- All unit power wiring shall enter unit cabinet at a single, factory-prepared, knockout location.

- Thru-the-base capability.

- Thru-the-base provisions/connections are available as standard with every unit. When bottom connections are required, field furnished couplings are required.

- No basepan penetration, other than those authorized by the manufacturer, is permitted.

- Component Access Panels (standard):

- Cabinet panels shall be easily removable for servicing.

- Unit shall have one factory installed, tool-less, removable, filter access panel.

- Panels covering control box and filter shall have molded composite handles while the blower access door shall have an integrated flange for easy removal.

- Handles shall be UV modified, composite, permanently attached, and recessed into the panel.

- Screws on the vertical portion of all removable access panel shall engage into heat resistant, molded composite collars.

- Collars shall be removable and easily replaceable using manufacturer recommended parts.

- 23 81 19.13.H. Gas Heat:

- General:

- Heat exchanger shall be an induced draft design. Positive pressure heat exchanger designs shall not be allowed.

- Shall incorporate a direct-spark ignition system and redundant main gas valve.

- Gas supply pressure at the inlet to the rooftop unit gas valve must match that required by the manufacturer.

- The heat exchanger shall be controlled by an integrated gas controller (IGC) microprocessor.

- IGC board shall notify users of fault using an LED (light-emitting diode).

- The LED shall be visible without removing the control box access panel.

- IGC board shall contain algorithms that modify evaporator-fan operation to prevent future cycling on high temperature limit switch.

- Unit shall be equipped with anti-cycle protection with one short cycle on unit flame rollout switch or 4 continuous short cycles on the high temperature limit switch. Fault indication shall be made using an LED.

- Standard Heat Exchanger Construction:

- Heat exchanger shall be of the tubular-section type constructed of a minimum of 20-gage steel coated with a nominal 1.2 mil aluminum-silicone alloy for corrosion resistance.

- Burners shall be of the in-shot type constructed of aluminum-coated steel.

- Burners shall incorporate orifices for rated heat output up to 2000 ft (610 m) elevation. Additional accessory kits may be required for applications above 2000 ft (610 m) elevation, depending on local gas supply conditions.

- Each heat exchanger tube shall contain multiple dimples for increased heating effectiveness.

- Optional Stainless Steel Heat Exchanger Construction:

- Use energy saving, direct-spark ignition system.

- Use a redundant main gas valve.

- Burners shall be of the in-shot type constructed of aluminum-coated steel.

- All gas piping shall enter the unit cabinet at a single location on side of unit (horizontal plane).

- The optional stainless steel heat exchanger shall be of the tubular-section type, constructed of a minimum of 20-gage type 409 stainless steel.

- Type 409 stainless steel shall be used in heat exchanger tubes and vestibule plate.

- Complete stainless steel heat exchanger allows for greater application flexibility.

- Induced Draft Combustion Motor and Blower:

- Shall be a direct-drive, single inlet, forward-curved centrifugal type.

- Shall be made from steel with a corrosion-resistant finish.

- Shall have permanently lubricated sealed bearings.

- Shall have inherent thermal overload protection.

- Shall have an automatic reset feature.

- 23 81 19.13.I. Coils:

- Standard Aluminum Fin/Copper Tube Coils:

- Standard evaporator and condenser coils shall have aluminum lanced plate fins mechanically bonded to seamless internally grooved 5/16-in. diameter copper tubes with all joints brazed.

- Evaporator coils shall be leak tested to 150 psig, pressure tested to 450 psig, and qualified to UL 1995 burst test at 1775 psig.

- Condenser coils shall be leak tested to 150 psig, pressure tested to 650 psig, and qualified to UL 1995 burst test at 1980 psig.

- Optional Pre-coated Aluminum-Fin Condenser Coils:

- Shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments.

- Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube.

- Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.

- Corrosion durability of fin stock shall be confirmed through testing to be no less than 1000 hours salt spray per ASTM B117-90.

- Corrosion durability of fin stock shall be confirmed through testing to have no visible corrosion after 48 hour immersion in a room temperature solution of 5% salt, 1% acetic acid.

- Fin stock coating shall pass 2000 hours of the following: one week exposure in the prohesion chamber followed by one week of accelerated ultraviolet light testing. Prohesion chamber: the solution shall contain 3.5% sodium chloride and 0.35% ammonium sulfate. The exposure cycle is one hour of salt fog application at ambient followed by one hour drying at 95°F (35°C).

- Optional Copper-Fin Evaporator and Condenser Coils:

- Shall be constructed of copper fins mechanically bonded to copper tubes and copper tube sheets.

- Galvanized steel tube sheets shall not be acceptable.

- A polymer strip shall prevent coil assembly from contacting the sheet metal coil pan to minimize potential for galvanic corrosion between coil and pan.

- Optional e-coated Aluminum-Fin Evaporator and Condenser Coils:

- Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins.

- Coating process shall ensure complete coil encapsulation of tubes, fins and headers.

- Color shall be high gloss black with gloss per ASTM D523-89.

- Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges.

- Superior hardness characteristics of 2H per ASTM D3363-92A and cross-hatch adhesion of 4B-5B per ASTM D3359-93.

- Impact resistance shall be up to 160 in. lb. (ASTM D2794-93).

- Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92).

- Corrosion durability shall be confirmed through testing to be no less than 6000 hours salt spray per ASTM B117-90.

- 23 81 19.13.J. Refrigerant Components:

- Refrigerant circuit shall include the following control, safety, and maintenance features:

- Thermostatic Expansion Valve (TXV) shall help provide optimum performance across the entire operating range. Shall contain removable power element to allow change out of power element and bulb without removing the valve body.

- Refrigerant filter drier - Solid core design.

- Service gage connections on suction and discharge lines.

- Pressure gage access through a specially designed access screen on the side of the unit.

- Single circuit design with tandem compressor and fully activated evaporator coil.

- Compressors:

- Models shall use fully hermetic tandem scroll compressors optimized for comfort staging and IEER energy savings.

- Models shall be available with a single refrigerant circuit and three-stage cooling operation on all models.

- Compressor motors shall be cooled by refrigerant gas passing through motor windings.

- Compressors shall be internally protected from high discharge temperature conditions.

- Compressors shall be protected from an over-temperature and over-amperage conditions by an internal, motor overload device.

- Compressor shall be factory mounted on rubber grommets.

- Compressor motors shall have internal line break thermal, current overload and high pressure differential protection.

- Crankcase heaters shall be standard on each compressor and deactivated whenever the compressor is in operation.

- 23 81 19.13.K. Filter Section:

- Filters access is specified in the unit cabinet section of this specification.

- Filters shall be held in place by a preformed, slide-out filter tray, facilitating easy removal and installation.

- Shall consist of factory-installed, low velocity, throw-away 2-in. thick fiberglass filters.

- Filters shall be standard, commercially available sizes.

- Only one size filter per unit is allowed.

- 4-in. filter capability is possible with a field-installed pre-engineered slide out filter track accessory. 4-in. filters are field furnished.

- 23 81 19.13.L. Evaporator Fan and Motor:

- Evaporator Fan Motor:

- Shall have permanently lubricated bearings.

- Shall have inherent automatic-reset thermal overload protection or circuit breaker.

- Shall have a maximum continuous bhp rating for continuous duty operation; no safety factors above that rating shall be required.

- Shall be Variable Frequency duty to match the three-stage compression logic.

- Shall contain motor shaft grounding ring to prevent electrical bearing fluting damage by safely diverting harmful shaft voltages and bearing currents to ground.

- Variable Frequency Drive (VFD). For indoor fan motor Staged Air Volume (SAV™) operation:

- Shall be installed inside the unit cabinet, mounted, wired and tested.

- Shall contain Electromagnetic Interference (EMI) frequency protection.

- Insulated Gate Bi-Polar Transistors (IGBT) used to produce the output pulse width modulated (PWM) waveform, allowing for quiet motor operation.

- Self-diagnostics with fault and power code LED indicator. Field accessory Display Kit available for further diagnostics and special setup applications.

- RS485 capability standard.

- Electronic thermal overload protection.

- 5% swinging chokes for harmonic reduction and improved power factor.

- All printed circuit boards shall be conformal coated.

- Shall not contain visual display to adjust internal setting. Available only as field-installed kit.

- Belt-Driven Evaporator Fan:

- Belt drive shall include an adjustable-pitch motor pulley.

- Shall use sealed, permanently lubricated ball-bearing type.

- Blower fan shall be double-inlet type with forward-curved blades.

- Shall be constructed from steel with a corrosion resistant finish and dynamically balanced.

- 23 81 19.13.M. Condenser Fans and Motors:

- Condenser Fan Motors:

- Shall be a totally enclosed – multi speed ECM motor.

- Shall use permanently lubricated bearings.

- Shall have inherent thermal overload protection with an automatic reset feature.

- Shall use a shaft-down design.

- Condenser Fans:

- Shall be a direct-driven propeller type fan.

- Shall have galvanized aluminum (galvalum) blades riveted to corrosion-resistant steel spiders and shall be dynamically balanced.

- 23 81 19.13.N. Special Features Options and Accessories:

- Low Leak Economizers:

- Available as factory-installed option (vertical or horizontal) or field-installed accessory (vertical or horizontal) on all electro-mechanical, RTU Open, and SystemVu™ models.

- Low leak economizers are available with EconoMi$er X controls for electro-mechanical units, or EconoMi$er2 controls for RTU Open or SystemVu units.

- Integrated, gear driven opposed blade design type capable of simultaneous economizer and compressor operation.

- Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

- Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

- Low leak rate models shall be equipped with leakage dampers, not to exceed 2% leakage at 1 in. wg pressure differential.

- Shall be capable of introducing up to 100% outdoor air.

- Economizer’s barometric relief dampers shall be sized to allow up to 100% relief (actual results will be based on specific job conditions).

- Ultra-Low Leak Economizers:

- Available as a factory-installed option (vertical or horizontal) or field-installed accessory (vertical or horizontal) on all models including: electro-mechanical, RTU Open, and SystemVu.

- Ultra-Low Leak economizer dampers meet California’s Title 24 section 140.4 prescriptive requirements for leakage, reliability testing, etc., and ASHRAE 90.1-2013 requirements for damper leakage.

- Economizers are available with EconoMi$er X controls for electro-mechanical units, or EconoMi$er2 controls for RTU Open or SystemVu units.

- Integrated, gear driven opposed blade design type capable of simultaneous economizer and compressor operation.

- Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

- Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

- Shall be capable of introducing up to 100% outdoor air.

- Economizer’s barometric relief dampers shall be sized to allow up to 100% relief (actual results will be based on specific job conditions).

- EconoMi$er X Economizer Controls:

- For use with factory-installed (vertical or horizontal) or field-installed accessory (vertical or horizontal) on electromechanical units with low leak or ultra-low leak economizers.

- Meets California’s Title 24 section 120.2 mandatory requirements for economizer Fault Detection and Diagnosis (FDD).

- Economizer controller shall be Honeywell W7220 that provides:

- 2-line LCD interface screen for setup, configuration and troubleshooting.

- On-board FDD detects and alerts when economizer is not operating properly.

- Sensor failure loss of communication identification.

- Automatic sensor detection.

- Capabilities for use with multi-speed indoor fan units.

- Compressor lockout temperature on W7220 is adjustable from –45°F to 80°F (–43°C to 27°C), set at a factory default of 32°F (0°C).

- Shall be designed to spring return close outside air damper during loss of power.

- Actuator shall be direct coupled to economizer gear. No linkage arms or control rods shall be acceptable.

- Utilizes digital dry bulb or enthalpy outside air sensors. Factory-installed economizers available with dry bulb or enthalpy. Dry bulb sensors installed on all field-installed economizer accessories.

- EconoMi$er2 Economizer Controls:

- For use with factory-installed (vertical or horizontal) or field-installed accessory (vertical or horizontal) on RTU Open or SystemVu units with low leak or ultra-low leak economizers.
NOTE: Factory-installed EconoMi$er2 is available on SystemVu units with Ultra-Low Leak economizers only.

- EconoMi$er2 economizers are controlled by RTU Open or SystemVu unit controllers, which shall be 4 to 20mA design.

- RTU Open and SystemVu controls meet California’s Title 24 section 120.2 mandatory requirements for economizer Fault Detection and Diagnosis.

- Available on factory-installed (vertical only) economizers with dry bulb or enthalpy outside air sensors. Field-installed accessories (vertical or horizontal) are available with dry bulb outside air sensors only.

- Outdoor air sensor setpoint shall be adjustable and shall range from 40°F to 100°F (4°C to 38°C). Additional sensor options shall be available as accessories.

- Shall be designed to spring return close outside air damper during loss of power.

- Actuator shall be direct coupled to economizer gear. No linkage arms or control rods shall be acceptable.

- The economizer controller shall also provide control of an accessory power exhaust unit function. Factory set at 100%, with a range of 0% to 100%.

- The economizer shall maintain minimum airflow into the building during occupied period and provide design ventilation rate for full occupancy.

- Controller shall drive outside air dampers completely closed when the unit is in the unoccupied mode.

- Economizer controller shall accept a 4 to 20mA CO2 sensor input for IAQ/DCV control. In this mode, dampers shall modulate the outdoor air damper to provide ventilation based on the sensor input.

- Economizer controller shall provide indications when in free cooling mode, in the DCV mode, or the exhaust fan contact is closed.

- Propane Conversion Kit:

- Package shall contain all the necessary hardware and instructions to convert a standard natural gas unit for use with liquefied propane. Kits shall be available for elevations from 0 up to 14,000 ft (4,276 m).

- Condenser Coil Hail Guard Assembly:

- Shall protect against damage from hail.

- Shall be louvered style design.

- Unit-Mounted, Non-Fused Disconnect Switch:

- Switch shall be factory-installed, internally mounted.

- National Electric Code (NEC) and ETL approved non-fused switch shall provide unit power shutoff.

- Shall be accessible from outside the unit.

- Shall provide local shutdown and lockout capability.

- Sized only for the unit as ordered from the factory. Does not accommodate field-installed devices.

- HACR Breaker:

- These manual reset devices provide overload and short circuit protection for the unit. Factory wired and mounted with the units, with access cover to help provide environmental protection. On 575V applications, HACR breaker can only be used with WYE power distribution systems. Use on Delta power distribution systems is prohibited.

- Sized only for the unit as ordered from the factory. Does not accommodate field-installed devices.

- Convenience Outlet:

- Powered convenience outlet.

- Outlet shall be powered from main line power to the rooftop unit.

- Outlet shall be powered from line side of disconnect by installing contractor, as required by code. If outlet is powered from load side of disconnect, unit electrical ratings shall be ETL certified and rated for additional outlet amperage.

- Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.

- Outlet shall include 15 amp GFI receptacles with independent fuse protection.

- Voltage required to operate convenience outlet shall be provided by a factory-installed step-down transformer.

- Outlet shall be accessible from outside the unit.

- Outlet shall include a field-installed “Wet in Use” cover.

- Non-Powered convenience outlet.

- Outlet shall be powered from a separate 115/120v power source.

- A transformer shall not be included.

- Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.

- Outlet shall include 15 amp GFI receptacles with independent fuse protection.

- Outlet shall be accessible from outside the unit.

- Outlet shall include a field-installed “Wet in Use” cover.

- Flue Discharge Deflector:

- Flue discharge deflector shall direct unit exhaust vertically instead of horizontally.

- Deflector shall be defined as a “natural draft” device by the National Fuel and Gas (NFG) code.

- Centrifugal Propeller Power Exhaust:

- Power exhaust shall be used in conjunction with an integrated economizer.

- Independent modules for vertical or horizontal return configurations shall be available.

- Horizontal power exhaust is shall be mounted in return ductwork.

- Power exhaust shall be controlled by economizer controller operation. Exhaust fans shall be energized when dampers open past the 0 to 100% adjustable set point on the economizer control.

- Roof Curbs (Vertical):

- Full perimeter roof curb with exhaust capability providing separate air streams for energy recovery from the exhaust air without supply air contamination.

- Formed galvanized steel with wood nailer strip and shall be capable of supporting entire unit weight.

- Permits installation and securing of ductwork to curb prior to mounting unit on the curb.

- High-Static Indoor Fan Motor(s) and Drive(s):

- High-static motor(s) and drive(s) shall be factory-installed to provide additional performance range.

- High Altitude Gas Conversion Kit:

- Package shall contain all the necessary hardware and instructions to convert a standard natural gas unit to operate from 3,000 to 10,000 ft (914 to 3048 m) elevation and 10,001 to 14,000 ft (3049 to 4267 m) elevation.

- Outdoor Air Enthalpy Sensor:

- The outdoor air enthalpy sensor shall be used to provide single enthalpy control. When used in conjunction with a return air enthalpy sensor, the unit will provide differential enthalpy control. The sensor allows the unit to determine if outside air is suitable for free cooling.

- Return Air Enthalpy Sensor:

- The return air enthalpy sensor shall be used in conjunction with an outdoor air enthalpy sensor to provide differential enthalpy control.

- Indoor Air Quality (CO2) Sensor:

- Shall be able to provide demand ventilation indoor air quality (IAQ) control.

- The IAQ sensor shall be available in duct mount, wall mount, or wall mount with LED display. The set point shall have adjustment capability.

- Smoke Detectors:

- Shall be a four-wire controller and detector.

- Shall be environmental compensated with differential sensing for reliable, stable, and drift-free sensitivity.

- Shall use magnet-activated test/reset sensor switches.

- Shall have tool-less connection terminal access.

- Shall have a recessed momentary switch for testing and resetting the detector.

- Controller shall include:

- One set of normally open alarm initiation contacts for connection to an initiating device circuit on a fire alarm control panel.

- Two Form-C auxiliary alarm relays for interface with rooftop unit or other equipment.

- One Form-C supervision (trouble) relay to control the operation of the Trouble LED on a remote test/reset station.

- Capable of direct connection to two individual detector modules.

- Can be wired to up to 14 other duct smoke detectors for multiple fan shutdown applications

- Horn/Strobe Annunciator:

- Provides an audible/visual signaling device for use with factory-installed option or field-installed accessory smoke detectors.

- Requires installation of a field-supplied 24-v transformer suitable for 4.2 VA (AC) or 3.0 VA (DC) per horn/strobe accessory.

- Requires field-supplied electrical box, North American 1-gang box, 2-in. (51 mm) x 4-in. (102 mm).

- Shall have a clear colored lens.

- Time Guard Device:

- Shall prevent compressor short cycling by providing a 5 minute delay (± 2 minutes) before restarting a compressor after shutdown for any reason.

- One device shall be required per compressor.

- Barometric Hood (Horizontal Economizer Applications):

- Shall be required when a horizontal economizer and barometric relief are required. Barometric relief damper must be installed in the return air (horizontal) duct work. This hood provides weather protection.

- Hinged Access Panels:

- Shall provide easy access through integrated quarter turn latches.

- Shall be on major panels of – filter, control box, fan motor and compressor.

- Display Kit for Variable Frequency Drive:

- Kit allows the ability to access the VFD controller programs to provide special setup capabilities and diagnostics.

- Kit contains display module and communication cable.

- Display Kit can be permanently installed in the unit or used on any SAV™ system VFD controller as needed.

- Thermostat:

- Due to the three-stage cooling capacity design of these units, a three-stage cooling thermostat is required for the unit to perform at listed operating efficiencies.

- Carrier offers a Honeywell branded T7350D (3 Cool/3 Heat) Commercial Programmable Thermostat. This provides:

- 7-day programmable 365-day clock with holiday programming

- Automatic Daylight Saving Time adjustment

- Backlit display

- Changeover selections: automatic or manual

- Fan configurable: continuous or intermittent during occupied

- Humidi-MiZer® Adaptive Dehumidification System:

- The Humidi-MiZer Adaptive Dehumidification System shall be factory installed, certified and tested to provide greater dehumidification of the occupied space by providing two distinct models of dehumidification operation in addition to its normal design cooling mode:

- Subcooling mode further sub cools the hot liquid refrigerant leaving the condenser coil as well as reheat leaving air stream. It can provide both better cooling capacity as well as dehumidification process when both temperature and humidity in the space are not satisfied.

- Hot gas reheat mode shall mix a portion of the hot gas from the discharge of compressor with the hot liquid refrigerant leaving the condenser coil to create a two-phase warm refrigerant in the reheat coil which results in a neutral leaving air temperature when only humidity in the space is not satisfied.

- High Short Circuit Current Rating (SCCR):

- An optional SCCR of 65kA shall be provided for 460 volt and 60kA for 208/230 volt units.

BACnet is a trademark of ASHRAE.

Modbus is a registered trademark of Schneider Electric.

LonWorks is a registered trademark of Echelon Corporation.