Packaged Rooftop Cooling Unit with ComfortLink Controls and Optional Electric or Hydronic Heat

HVAC Guide Specifications —
Section 50P2,P3,P4,P5,P6,P7,P8,P9

Size Range: 30 to 100 Tons, Nominal

Carrier Model Number:

50P2 (Vertical Supply/Return, Constant Volume [CV] Application, Staged Air Volume [SAV™])

50P3 (Vertical Supply/Return, Variable Air Volume [VAV] Application)

50P4 (Horizontal Supply/Return, CV or SAV Application)

50P5 (Horizontal Supply/Return, VAV Application)

50P6 (Vertical Supply/Return, CV or SAV Application, Greenspeed® Intelligence)

50P7 (Vertical Supply/Return, VAV Application, Greenspeed Intelligence)

50P8 (Horizontal Supply/Return, CV or SAV Application, Greenspeed Intelligence)

50P9 (Horizontal Supply/Return, VAV Application, Greenspeed Intelligence)

NOTE: Items throughout the specification which apply only to units with electric or hydronic heat are indicated by single brackets [i.e.].

- General

- SYSTEM DESCRIPTION

Outdoor, roof-curb mounted, electronically controlled cooling [and heating] unit utilizing hermetic scroll compressors with crankcase heaters for cooling duty [and utilizing electric resistance coils for heating duty]. Units shall supply and return air vertically or horizontally as shown on the contract drawings.

- QUALITY ASSURANCE

- Unit shall be rated in accordance with AHRI (Air-Conditioning, Heating and Refrigeration Institute) Standard 340/360, latest edition, and with ASHRAE (American Society of Heating, Refrigerating and Air-Conditioning Engineers) Standard 90.1-2013.

- Unit shall be designed to conform to ANSI (American National Standards Institute)/ASHRAE 15 (latest edition), ASHRAE 62, and UL Standard 1995.

- Unit shall be listed by ETL and ETL, Canada, as a total package.

- Roof curb shall be designed to NRCA (National Roofing Contractor’s Association) criteria per Guideline B-1986.

- Insulation and adhesive shall meet NFPA (National Fire Protection Association) 90A requirements for flame spread and smoke generation.

- The management system governing the manufacture of this product is ISO (International Organization for Standardization) 9001:2015 certified.

- DELIVERY, STORAGE, AND HANDLING

Unit shall be stored and handled per manufacturer’s recommendations.

- Products

- 2.01 EQUIPMENT

- Factory-assembled, single-piece heating and cooling unit. Contained within the unit enclosure shall be all factory wiring, piping, refrigerant charge (R-410A), operating oil charge, dual refrigerant circuits, microprocessor-based control system and associated hardware, and all special features required prior to field start-up.

- Unit Cabinet:

- Constructed of galvanized steel (designated G90 per ASTM [American Society for Testing and Materials] Standard A653 — minimum coating weight of 0.9 oz of zinc per square foot), bonderized and primer-coated on both sides and coated with a baked polyester thermosetting powder coating finish on the outer surface.

- Unit casing shall be capable of withstanding ASTM Standard B117 500-hour salt spray test.

- Sides shall have person size insulated, double wall, hinged access doors for easy access to the control box and other areas requiring servicing. Each door shall seal against a rubber gasket to prevent air and water leakage.

- Interior cabinet surfaces (except heat exchanger section) shall be insulated with flexible fire-retardant dual-density (1.75-lb/cu ft) fiberglass blanket, coated on the air side. Insulation coating shall be cleanable and shall contain an EPA-registered immobilized antimicrobial agent to effectively resist the growth of bacteria and fungi as proven by tests in accordance with ASTM Standards G21 and G22.

- Insulation shall be applied by means of adhesion using a water reducible adhesive sprayed onto interior surface. Adhesive shall maintain a satisfactory adhesion and cohesion within the temperature range of –20 to 180°F and have excellent resistance to water and water vapor when cured.

- Unit shall contain a sloped drain pan, to prevent standing water from accumulating. Pan shall be fabricated of stainless steel. Unit shall contain a factory-installed nonferrous main condensate drain connection.

- Units shall be equipped with lifting lugs to facilitate overhead rigging.

- Fans:

- Supply Fan:

- Unit shall have only one fan wheel, scroll, and motor.

- Fan scroll, wheel, shaft, bearings, drive components and motor shall be mounted on a formed steel assembly which shall be isolated from the unit outer casing with factory-installed 2-in. deflection spring isolators and vibration-absorbent fan discharge seal.

- Fan shall be double-width, double-inlet, centrifugal belt driven forward-curve type with single outlet discharge (standard) or centrifugal belt driven airfoil blade section type with single outlet discharge (optional). Option airfoil fan shall include a high static pressure safety switch installed into the supply air plenum.

- Fan wheel shall be designed for continuous operation at the maximum rated fan speed and motor horsepower.

- Fan wheel and shaft shall be selected to operate at 25% below the first critical speed and shall be statically and dynamically balanced as an assembly.

- Fan shaft shall be solid steel, turned, ground and polished, and coated with rust preventative oil.

- Fan shaft bearings shall be self-aligning, pillow-block, regreasable ball or roller-type selected for a minimum average life of 200,000 hours at design operating conditions in accordance with ANSI B3.15.

- A single motor shall be mounted within the fan section casing on slide rails equipped with adjusting screws. Motor shall be mounted on a horizontal flat surface and shall not be supported by the fan or its structural members.

- Fan drive shall be constant-speed fixed-pitch. All drives shall be factory-mounted, with belts aligned and tensioned.

- Condenser Fans:

- Direct-driven propeller type.

- Units shall have a direct driven, 11-blade airfoil cross section, reinforced polymer construction, and shrouded-axial type fans with inherent corrosion resistance.

- Low sound fans for outdoor sound reduction shall be available as a factory-installed option for all units (except 35 ton units).

- Discharge air vertically upward.

- Protected by PVC-coated steel wire safety guards.

- Statically and dynamically balanced.

- Three-phase, totally enclosed motors.

- Compressors:

- Fully hermetic scroll type compressors with overload protection and short cycle protection with minimum on and off timers.

- Factory rubber-in-shear mounted for vibration isolation.

- Reverse rotation protection capability.

- Crankcase heaters shall only be activated during compressor off mode.

- Coils:

- Evaporator Coil:

- Intertwined circuiting constructed of aluminum fins mechanically bonded to seamless copper tubes.

- Full-face active type during full and part load conditions.

- Coils shall be leak tested at 150 psig and pressure tested at 650 psig.

- Condenser Coils:

- Condenser coils shall be microchannel design. The coils shall have a series of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds. Microchannel coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for the fins, tubes and manifolds.

- Air-cooled condenser coils shall be leak tested at 150 psig and pressure tested at 650 psig.

- Outdoor-Air Hood Assembly:

Factory-installed manual outdoor-air damper shall allow intake of up to 25% nominal airflow (on units not equipped with optional economizer).

- Electric Heating Section:

Electric resistance heaters shall be factory installed, open wire nichrome element type, insulated with ceramic bushings, and shall include operating and safety controls.

- Hydronic Heating Section:

Hydronic heating option shall consist of factory-installed plate fin-tube coil assembly, installed in the extended length section. Coil assembly shall be supplied with die-formed casing and tube sheets of mill galvanized steel. Tubes shall be minimum 1/2-in. OD copper tubes mechanically expanded into aluminum plate fin coils with belled collars. Headers shall be constructed of steel with steel MPT connections. Headers shall have drain and vent connections. Coils shall be suitable for a design working pressure of 300 psig at 200°F. Coils shall be tested at 450 psig air pressure.

- Refrigerant Components:

Unit shall be equipped with dual refrigerant circuits, each containing:

- Filter drier.

- Moisture indicating sight glass.

- Thermostatic expansion valve.

- Fusible plug.

- Filter Section:

- Filter section shall consist of 2-in. thick, MERV (Minimum Efficiency Reporting Value) 7 disposable fiberglass filters of commercially available sizes.

- Factory 2-in. filter track shall allow easy field conversion to accept 4-in. thick, disposable fiberglass filters of commercially available sizes.

- Controls, Safeties, and Diagnostics:

- Controls:

- Control shall be accomplished through the use of a factory-installed, microprocessor-based control system and associated electronic and electrical hardware. Control system shall determine control sequences through monitoring the following operational variables:

- Day and Time.

- Schedule (Unoccupied/Occupied).

- Set points (Unoccupied/Occupied, Economizer, Duct Pressure, others).

- Space temperature.

- Outdoor air temperature.

- Unit supply-air temperature.

- Unit return-air temperature.

- Supply-air fan status.

- Economizer position.

- Compressor suction and discharge pressure.

- Scrolling marquee display.

- Accessory and/or field-supplied sensors, function switches and/or signals.

- Controls shall be capable of performing the following functions:

- Capacity control based on supply-air temperature and compensated by rate of change of return-air temperature (VAV) or room temperature (CV). Capacity control shall be accomplished through the use of compressor staging or optional variable output compressors.

- Perform a quick test to check the status of all input and output signals to the control system using scrolling marquee or Navigator™ display.

- Control of integrated economizer operation, based on unit supply-air temperature.

- Supply fan volume control shall control output from a variable frequency drive to maintain duct static pressure at user-configured set point (VAV). Static pressure reset in conjunction with Carrier communicating terminals to reduce supply fan power requirements. Control system calculates the amount of supply static pressure reduction necessary to cause the most open damper in the system to open more than the minimum value (60%) but not more than the maximum value (90% or negligible static pressure drop).

- Heating control shall provide space temperature control for unoccupied period heating, morning warm-up sequence and occupied period heating (when configured).

- Adaptive optimal start shall determine the time unit will commence cooling (or heating or heating for morning warmup) during the unoccupied mode to ensure occupied space reaches the set point in time for occupied mode.

- Adaptive optimal stop shall turn off the compressors a preset amount of time before the end of the occupied mode to conserve energy (CV only).

- Alerts and Alarms: Control shall continuously monitor all sensor inputs and control outputs to ensure safe and proper system operation. Alerts shall be generated whenever sensor conditions have gone outside criteria for acceptability. Alarms shall be initiated when unit control detects that a sensor input value is outside its valid range (indicating a defective device or connection that prevents full unit operation) or that an output has not functioned as expected or that a safety device has tripped. Current alarms shall be maintained in STATUS function; up to 9 (current or reset) shall be stored in HISTORY function for recall.

- Timed override function shall permit a system in unoccupied mode to be returned to occupied mode for a user-configured period of 1, 2, 3 or 4 hours by pressing the override button on the front of the space temperature sensor.

- Nighttime Free Cooling (NTFC) shall start the supply fan and open the economizer on cool nights to precool the building structure mass using only outdoor air. Function shall be restricted to operation above a user-configured low lockout temperature set point.

- Modulating power exhaust control shall modulate capacity of exhaust fan system in response to building static pressure at user-configured set point. Power exhaust fan operation shall be interlocked with supply fan operation.

- Return fan control (on optional return fan equipped units only) shall measure supply fan CFM and modulate return fan to maintain constant CFM differential between supply and return fan. Return fan operation shall be interlocked with supply fan operation. Capacity of exhaust air shall modulate in response to building static pressure at user-configured set point.

- Smoke control functions: Control shall initiate any of four separate smoke control functions in response to closure of field switches. Functions shall include: Pressurization, Evacuation, Smoke Purge and Fire Shutdown. Should two or more switches be closed simultaneously, Fire Shutdown shall be initiated.

- Support demand controlled ventilation through a reset of the economizer's minimum position. This reset based on differential CO2 ppm (outdoor and indoor) can be chosen as linear or as fast or slow-acting exponential curves.

- Indoor air quality (IAQ) mode shall admit fresh outdoor air into the space whenever space air quality sensors detect unsuitable space conditions, by overriding economizer minimum damper position. IAQ shall be permitted only during occupied periods, unless configured to be allowed during unoccupied periods also.

- Provide control for reheat via auxiliary heating coil during ventilation.

- IAQ pre-occupancy purge function shall provide complete exchange of indoor air with fresh air during unoccupied periods, when outdoor conditions permit. Function shall energize supply fan and open economizer two hours before next occupied period; duration of purge shall be user-configured (5 to 60 minutes).

- Outdoor Air Control (OAC) function shall maintain a minimum quantity of outdoor airflow into an occupied space. OAC mode shall be available only during an occupied period. Outdoor airflow shall be monitored by an airflow station and transducer. Economizer maximum damper opening position during OAC mode shall be user-configured.

- Dehumidification and Reheat (Humidi-MiZer units only): Dehumidification function shall override comfort condition set points to deliver cooler air into the space and satisfy a user-configured humidity set point at the space or return air humidity sensor. Reheat function shall energize an auxiliary heating device should dehumidification operation result in cooling of the space down to the occupied heating set point.

- Supply Air Temperature Set Point Reset: Control shall automatically reset the unit supply air temperature set point on VAV models from either space temperature or return-air temperature, at user-configured rate and limit. Control shall also reset supply air temperature set point via external 2 to 10 vdc signal representing 0° to 20°F range of reset. Control shall respond to higher of either reset if both are active.

- Space Temperature Offset function shall permit occupants to adjust space temperature set point by ±5°F using T-56 space sensor (equipped with sliding scale adjuster).

- Lead-lag function shall distribute starts between the two refrigeration circuits in an effort to equalize the running time on the two circuits.

- Condenser-fan cycling control shall maintain correct head pressure down to 0°F.

- Refrigeration system pressures shall be monitored via pressure transducers. Alarms for low pressure, high pressure will be permitted.

- Timed Discrete Output function shall control an external function or device via user-configured activity schedule. This schedule shall be separate and different from the unit’s occupied/unoccupied time schedule.

- Hydronic heating coil control shall modulate a control valve in a steam or hydronic heat system to maintain space temperature at user-configured set points. Control valve actuator shall communicate via LEN (Local Equipment Network) protocol.

- Humidifier control shall provide control for either LEN communicating control valve or discrete-type output, to maintain space humidity conditions at user-configured set points.

- Two-step demand limit control (when used in conjunction with CEM [controls expansion module]).

- Display in Metric units: Display may be configured to display data in Metric or English (Imperial) units of measure.

- Safeties:

Unit components shall be equipped with the following protections:

- Compressors:

- Overcurrent using calibrated circuit breakers (shuts down individual compressor).

- Crankcase heaters.

- High-pressure switch (shuts down individual circuit, automatic reset type).

- Low-pressure switch (shuts down individual circuit, automatic reset type).

- Check filter switch.

- Belt-Drive Fan Motors:

Overcurrent protection manual reset circuit breakers.

- Airfoil Supply Fan and Airfoil Return Fan (when equipped):

High static pressure safety switch installed into the associated air plenum

- Electric Heating Section:

- Automatic reset high-temperature limit switches.

- Heat limiters (fusible links).

- Overcurrent protection manual reset circuit breakers.

- Branch circuit protection.

- Diagnostics:

- The display shall be capable of indicating a safety lockout condition (alarm) through an expandable scrolling display.

- The display shall also be capable of indicating an alert condition which does not lock out the unit, but informs the system monitor of a condition which could be detrimental to either the unit or the comfort of the occupants if allowed to continue.

- Test mode must also be capable of displaying outputs of microprocessor-controller and to verify operation of every thermistor, actuator motor, fan, and compressor before unit is started.

- Operating Characteristics:

- Unit shall be capable of starting and running at 115°F ambient outdoor temperature per maximum load criteria of AHRI Standard 340/360, latest edition.

- Unit shall be capable of mechanical cooling operation down to 32°F ambient outdoor temperature (–20°F with Greenspeed Intelligence Control option).

- Provides multi-stage cooling capability.

- [Provides 2 stages of electric heating capability.]

- Motors:

- Compressor motors shall be cooled by suction gas passing over motor windings.

- Condenser-fan motors shall be 3-phase, totally enclosed type with permanently lubricated ball bearings and internal over-temperature protection.

- Supply and exhaust fan motors shall be of the 3-phase, NEMA (National Electrical Manufacturers Association) rated, open drip-proof (ODP), ball bearing type, with efficiencies per EISA (Energy Independence and Security Act) of 2007 (U.S.A.) requirements.

- Electrical Requirements:

All unit power wiring shall enter unit cabinet at a single location.

- Special Features:

- Variable Capacity Digital Compressor:

A digital compressor shall be available on the lead circuit for constant volume and variable air volume configurations. The ComfortLink control system shall be capable of unloading this compressor in an infinite number of steps from 100% of unit capacity down to 25% of unit capacity (varies by unit size).

- Humidi-MiZer® Adaptive Dehumidification:

The Humidi-MiZer dehumidification system shall be factory installed with an e-coated reheat coil, and shall provide greater dehumidification of the occupied space by using two modes of dehumidification instead of the normal design cooling mode of the unit.

- Subcooling mode shall further subcool the hot liquid refrigerant leaving the condenser coil when both temperature and humidity in the space are not satisfied.

- Hot gas reheat mode shall mix a portion of the hot gas from the discharge of the compressor with the hot liquid refrigerant leaving the condenser coil to create a two-phase heat transfer in the system, resulting in a neutral leaving-air temperature.

- The system shall be equipped with modulating control valves to provide precise leaving air temperature control. On-off, cycling type control shall not be acceptable.

- Integrated Economizer:

Dry bulb, differential dry bulb temperature, enthalpy, or optional differential enthalpy controlled integrated type consisting of dampers, actuator, and linkages in conjunction with control system to provide primary cooling using outdoor air, enthalpy permitting, supplemented with mechanical cooling when necessary.

- Economizer shall meet the requirements of the California Energy commission airside economizer acceptance test.

- Dampers shall be a gear driven low-leakage type.

- Actuator shall have a spring-return feature which shuts dampers upon a power interruption or unit shutdown. Actuators are capable of internal diagnostics.

- Equipped with a solid-state humidity sensor that is capable of sensing outdoor-air heat content (temperature and humidity) and controlling economizer cut-in point at most economical level. The user can also configure dew point limiting.

- Ultra Low Leak Economizer:

Dry bulb, differential dry bulb temperature, enthalpy, or optional differential enthalpy controlled integrated type consisting of dampers, actuator, and linkages in conjunction with control system to provide primary cooling using outdoor air, enthalpy permitting, supplemented with mechanical cooling when necessary.

- Economizer shall meet the requirements of the California Energy Commission Title 24 economizer requirements.

- Dampers shall be a gear driven ultra low leakage type with blade and edge seals. Dampers shall exhibit a maximum leakage rate of 3 cfm per square foot of area at 1 in. wg pressure differential when tested in accordance with AMCA (Air Movement and Control Association) Standard 500.

- Actuator shall have a spring-return feature which shuts dampers upon a power interruption or unit shutdown. Actuators are capable of internal diagnostics.

- Equipped with a solid-state humidity sensor that is capable of sensing outdoor-air heat content (temperature and humidity) and controlling economizer cut-in point at most economical level. The user can also configure dew point limiting.

- Modulating Power Exhaust with VFD (Variable Frequency Drive):

Package shall include 2 double-width, double-inlet centrifugal belt drive, forward-curved power exhaust fans with variable frequency drive control of each fan to maintain a field-adjustable interior space pressure set point.

- Fan bearings shall be of the pillow block type with an average design life of 200,000 hours.

- Fans shall be statically and dynamically balanced.

- Bypass for the VFD shall be available as a factory-installed option.

- Differential pressure transducer for monitoring space pressure.

- Exhaust air hood assemblies containing backdraft dampers on each fan outlet, factory installed.

- All wiring and pressure tubing (except to space pressure pickup location) shall be factory supplied and installed.

- High-Capacity Modulating Power Exhaust System (75 to 100 ton units only):

High-capacity modulating power exhaust system shall be factory-installed and contain fans and motors, exhaust hoods and controls (including variable frequency drive and staging sequence) to maintain space pressure at user-configured set point.

- Dual fan assemblies with individual motors.

- Variable frequency drive for modulating capacity of lead fan.

- Staged control on lag fan.

- Differential pressure transducer for monitoring space pressure.

- Exhaust air hood assemblies containing backdraft dampers on each fan outlet, factory installed.

- All wiring and pressure tubing (except to space pressure pickup location) shall be factory supplied and installed.

- Return Fan/Building Pressure Control:

- Functions provided shall be:

- Airflow control for return duct path (dedicated to overcoming flow losses in return duct system).

- Modulate return airflow rate to track supply fan airflow rate and maintain a user set delta cfm between the supply and return airflow.

- Maintain building pressure by sensing building pressure and modulating fan speed.

- Option shall consist of following hardware:

- Plenum fan assembly, with welded steel airfoil blade fan.

- Spring isolation.

- Belt-drive fan system, fixed pitch for maximum belt life and reliability.

- Variable frequency drive (VFD) for return fan modulation control.

- Supply air cfm and return air cfm sensors to measure supply and return airflow.

- Exhaust damper with outlet hood.

- Building pressure transducer.

- Shall include a high static pressure safety switch installed into the return air plenum.

- Installation:

- Site installation shall require supply and installation of building pressure (BP) sensing pick-up and tube to connect to BP transducer in unit.

- All other wiring and pressure tubing shall be factory-supplied and factory installed.

- Barometric Relief Package:

- Package shall relieve excess internal pressure and consist of damper assemblies, hoods, damper screens, seal strips and required hardware.

- Damper assemblies shall close due to gravity upon unit shutoff.

- Pleated Filters:

Unit shall be factory equipped with MERV 7 pleated filters having the following characteristics:

- Efficiency of no less than 30% based on testing per ASHRAE Standard 52.

- Minimum average arrestance of 95%.

- High-Efficiency Pleated Filters (75 to 100 ton units only):

Unit shall be factory equipped with MERV 11 high-efficiency pleated filters having the following characteristics:

- Filters shall have a design dust spot efficiency with an average of 60 to 65% based on the ASHRAE Standard 52.1 test method.

- Filters shall have a minimum arrestance of 90%.

- Filters shall be classified as a Class 2 air filter according to UL Standard 900.

- Bag Filters with Prefilters (30 to 70 ton units only):

Unit shall be factory equipped with MERV 15 bag filters and 2-in. prefilters, and shall have an average efficiency of 90% based on testing per ASHRAE Standard 52.

- Cartridge Filters with Prefilters (30 to 70 ton units only):

Unit shall be factory equipped with cartridge filter mounting system with 2-in. prefilters.

- Supply Fan Variable Frequency Drive:

Variable air volume and staged air volume units shall be equipped with variable frequency drive (VFD) inverter. The VFD shall be factory-mounted, wired, and tested. The variable speed drive shall include the following features:

- Factory-supplied VFDs qualify, through ABB, for a 24-month warranty from date of commissioning or 30 months from date of sale, whichever occurs first.

- Full digital control with direct control from the unit ComfortLink controls.

- Insulated gate bi-polar transistors (IGBT) used to produce the output pulse width modulated (PWM) waveform, allowing for quiet motor operation.

- Inverters capable of operation at a frequency of 8 kHz so no acoustic noise shall be produced by the motor.

- VFDs shall include EMI/RFI (electromagnetic/ radio frequency interference) filters.

- Digital display keypad module, mounted on the VFD enclosure.

- Local/Remote and Manual/Auto function keys on the keypad.

- UL-listed electronic overload protection.

- Critical frequency avoidance.

- Self diagnostics.

- On-board storage of unit manufacturer's customer user settings, retrievable from the keypad.

- RS485 communications capability (accessory card source required).

- Internal thermal overload protection.

- 5% swinging (non-linear) chokes for harmonic reduction and improved power factor.

- All printed circuit boards shall be conformal coated.

- Supply Fan Static Pressure Control (VAV units):

Variable air volume units shall be equipped with a supply fan VFD. The VFD shall control motor speed to maintain set point static pressure control at the supply duct sensor tube location. The supply fan drive shall be field-adjustable to maintain supply duct static pressure set point from 0.0-in. wg to 5-in. wg, adjusted via scrolling marquee display or Navigator™ display. A pressure transducer shall be factory-mounted and wired. (Control tubing from sensor tube location to transducer shall be field-supplied and installed.) Transducer shall provide a 4 to 20 mA signal to the unit control module; unit control module shall provide a 4 to 20 mA signal to the VFD indicating desired VFD output level.

- Staged Air Volume (SAV™) units:

Staged air volume units shall be equipped with a supply fan VFD. The VFD shall control motor speed to user configurable speeds. High speed shall be a percentage of 60 Hz, and shall be user configurable. The range of adjustment for high speed shall be between 67 and 100% of 60 Hz. Low speed shall be a percentage of 60 Hz, and shall be user configurable. The range of adjustment for low cooling speed shall be between 33 and 67% of 60 Hz. The range of adjustment for low heating speed shall be between 75 and 100% of 60 Hz. The control shall allow user configurable fan speeds for cooling and heating modes.

- Discharge Plenum:

Discharge plenum design shall contain added length module for bottom supply air discharge, as shown in contract drawings. Discharge plenum design shall provide horizontal discharge arrangement supply fan which shall discharge into insulated plenum. Interior cabinet surfaces within discharge plenum section shall be lined with sheet metal on all surfaces, insulated on the side opposite the airstream. Electric heat is not available with discharge plenum models.

- Extended Chassis:

Extended chassis designs shall contain an added length module, after the evaporator section, as shown in the contract drawings. Module shall contain tracks to accept field-supplied/installed auxiliary heating coil.

- Non-Fused Disconnect:

A non-fused electrical disconnect for main unit power shall be factory installed. The disconnect shall be an interlocking through-the-door type.

- 115-Volt Convenience Outlet:

A duplex GFCI (ground fault circuit interrupt) receptacle shall be factory mounted in a weatherproof enclosure and wired for a 10-amp load. It will remain powered when all unit circuit breakers have been turned off. The outlet will be deenergized by the unit disconnect.

- Navigator™ Display Module:

The Navigator display module shall be a portable hand-held display module with a minimum of 4 lines and 20 characters per line, of clear English, Spanish, Portuguese or French language. Display menus shall provide clear language descriptions of all menu items, operating modes, configuration points and alarm diagnostics. Reference to factory codes shall not be accepted. An industrial grade coiled extension cord shall allow the display module to be moved around the chiller. Magnets shall hold the display module to any sheet metal panel to allow hands-free operation. Display module shall have NEMA 4x housing suitable for use in outdoor environments. Display shall have back light and contrast adjustment for easy viewing in bright sunlight or night conditions. The display module shall have raised surface buttons with positive tactile response.

- Controls Expansion Module (CEM):

Factory-installed package shall include all hardware for additional control of base unit operation and product integrated controls features. The functions supported are:

- Building pressurization, evacuation, and smoke purge control.

- Supply air reset from external 4 to 20 mA signal.

- Two-step demand limit inputs (when used with the CCN [Carrier Comfort Network®]).

- Indoor air quality (IAQ) switch monitoring.

- Outdoor airflow monitoring.

- Outdoor humidity monitoring.

- Space humidity monitoring (required for dehumidification control, reheat and humidifier control).

- Return air humidity monitoring.

- Demand limiting from an external 4 to 20 mA signal.

- Static pressure reset from an external 4 to 20 mA signal.

- Relative Humidity Sensors:

Package shall contain either duct-mounted or wall-mounted sensors to measure the relative humidity of the air within the occupied space (specify location) or return duct and/or outside air.

NOTE: For relative humidity sensor monitoring, the CEM must also be ordered (except for ZS sensors with RH sensing).

- Indoor Air Quality (CO2) Sensor:

- Shall have the ability to provide demand controlled ventilation indoor-air quality (IAQ) control through the economizer with an indoor air quality sensor.

- The IAQ sensor shall be available in duct mount, wall mount, and wall mount with LED display of CO2 in parts per million. The set point shall have adjustment capability.

- Return/Supply Air Smoke Detector:

The smoke detector shall send input to the controller to shut down the unit in case smoke is detected.

- Outdoor Airflow Sensor:

Outdoor airflow sensor package shall contain a airflow station with airflow sensor, a transducer and all hardware required to measure the quantity of outdoor air brought in through the economizer dampers. Optional economizer and CEM are required with this accessory. This airflow sensor shall control to the following airflow ranges:

Sizes 030-050: 2,500 to 12,500 CFM

Sizes 055-070: 3,000 to 17,000 CFM

Sizes 075-100: 5,000 to 21,000 CFM

- Differential Enthalpy Switch or Sensors (when equipped with both return air and outdoor air humidity sensors):

- For use with economizer only.

- Capable of comparing heat content (temperature and humidity) of outdoor and return air and controlling economizer cut-in point at the most economical level.

- Hot Gas Bypass:

Unit shall be factory equipped with hot gas bypass valve and tubing to maintain capacity control at minimal cooling loads.

- Condenser Coil Protective Coating — E-Coated Microchannel Coil:

E-coated aluminum microchannel coils shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat thickness of 0.8 to 1.2 mil with top coat having a uniform dry thickness from 1.0 to 2.0 mil on all external coil surface areas, including fin edges, shall be provided. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross-hatch adhesion of 4B-5B per ASTM D3359-02. E-coated coils shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2.

- Condenser Coil Hail Guard (sizes 040 to 060 only):

Canted face enclosure and welded wire grille complete with support retainers and fasteners shall be provided for protection of condenser coils. Field-assembled.

- BACnet Communication Option:

Shall provide factory-installed communication capability with a BACnet MS/TP network. Allows integration with i-Vu® Open Control System or a BACnet Building Automation System.

- MODBUS Protocol Translator:

A controller-based accessory module shall provide CCN access to MODBUS Remote Terminal Unit (RTU) protocol conversion.

- LonWorks Protocol Translator:

A controller-based accessory module shall provide CCN access to LON FT-10A ANSI/EIA-709.1 protocol conversion.

- Space Temperature Sensor (T-56):

The T-56 space temperature sensor (for CV applications) shall monitor space temperature. Device shall be suited for wall mounting in the occupied space. The T-56 sensor shall incorporate a front-panel located slider switch to effect a remote change in set point of ±5°F. The T-56 sensor shall also include a button used to initiate Unoccupied Override function.

- Space Temperature Sensor (T-56) with CO2 Sensor:

This device shall incorporate interior space temperature sensing and interior space CO2 level monitoring functions. Space temperature sensor shall sense the actual temperature in the conditioned space via 10,000-ohm thermistor. Temperature set point adjustment potentiometer via slide scale shall provide ±5°F adjustment. CO2 sensor shall provide CO2 measurement range of 0 to 2000 ppm. IAQ signal to unit base board terminals shall be 4 to 20 mA. Sensor shall be equipped with an override button for timed override. Sensor must be powered by a separate field-supplied 24-v transformer.

- Suction and Liquid Service Valves:

Shall be equipped with ball type service valves in the suction and liquid line for each circuit.

- Discharge Service Valve:

Shall be equipped with a ball type service valve in the discharge line of each circuit.

- Replaceable Core Filter Drier:

Shall be equipped with a replaceable core filter drier in each liquid line.

- Roof Curb:

Designed to comply with criteria established by NRCA Guideline B-1986.

- Size 030-060 Units:

Formed 14-gage galvanized steel with wood nailer. Supports full perimeter of unit.

- Size 070-100 Units:

Formed 14-gage galvanized steel with wood nailer strip as perimeter curb supporting the air-handling portion of unit, and rail for supporting the condenser portion of the unit.

- Roof Curb Condenser Section (accessory for size 070-100 units only):

Formed 14-gage galvanized steel with wood nailer strip for supporting condenser section of the unit to complete a full perimeter curb under entire unit.

- Silicon Controlled Rectifier (SCR) Controlled Electric Heat (30 to 70 ton units only):

- SCR electric heat option shall monitor unit supply-air temperature and control the unit heater section to provide the following sequences:

- Demand heating control, with modulation to maintain user-configured heating supply air temperature set point.

- Full output heating on heating control command.

- Tempering heat control, based on user-configured ventilation supply air temperature set point, to eliminate cold draft conditions with low mixed-air temperatures.

- SCR heat control option shall consist of:

- SCR controller capable of ensuring the proper heating rates.

- Supply air temperature thermistors with duct-mounting base.

- Limit switch temperature thermistors.

- Field installation shall be limited to installing three supply air temperature thermistors in the supply duct. All other hardware and wiring shall be factory-completed.

- Greenspeed Intelligence Control Option:

This factory-installed option shall regulate outdoor fan motor speeds in response to the saturated condensing temperature of the refrigeration circuits and local ambient conditions.

- The control shall be capable of operating the rooftop unit with outdoor temperature at –20°F.

- Fans shall be direct-driven shrouded-axial propeller type fans only, with 9-blade AeroAcoustic™ airfoil cross section (except size 35), reinforced polymer construction blades bolted to corrosion resistant steel supports for all size units.

- Fans discharge air vertically upward and are protected by PVC coated steel wire safety guards.

- Fans are statically and dynamically balanced.

- The condenser fan motors will be VFD driven.

- Compressor blankets will be applied to mitigate the level of outdoor sound on all refrigerant compressors. They shall be weather resistant and applied in both single and tandem arrangements.

- Unit efficiency is maximized by monitoring the refrigerant system and ambient conditions and controlling condenser fan performance.

- High Short Circuit Current Rating (SCCR):

An optional SCCR of 65kA shall be provided for 208/230 and 460 volt units. An optional of 25kA shall be provided for 575 volt units.

- Low Compressor Sound Blanket:

Low compressor sound blanket accessory shall be available for field installation.

- Phase Loss Monitor Option:

Phase loss monitor protection shall be available as a factory-installed option.

- ZS Communicating Sensors

The ZS room temperature sensor sensors shall be available in a variety of zone sensing combinations, including temperature, relative humidity, and indoor air quality, and shall be selected to meet the application requirements. The ZS room sensor shall be compatible with units with the factory installed BACnet communication option.

- Equipment Touch

Shall be a touchscreen interface with 4.3" color display and integral temperature and humidity sensing. The Equipment Touch shall be compatible with units with the factory installed BACnet communication option.

BACnet is a trademark of ASHRAE.

Modbus is a registered trademark of Schneider Electric.

LonWorks is a registered trademark of Echelon corporation.