Commercial Water Source Heat Pump Units with Puron® Refrigerant (R-410A)

HVAC Guide Specifications

Size Range:	HQP 72,000 to 242,000 Btuh Cooling Capacity
	VQP 72,000 to 360,000 Btuh Cooling Capacity

Carrier Model Number:	 50HQP,VQP

- General

- SYSTEM DESCRIPTION

- Units shall be designed to operate throughout the range of entering fluid temperature 50 to 100°F in the cooling mode and 50 to 80°F in the heating mode. Units shall have an operating range of 50 to 110°F in the cooling mode and 25 to 80°F in the heating mode when equipped with the optional extended range package.

- Units shall be individually packaged with wooden skid covered with protective corner posts and plastic stretch wrapping for maximum protection.

- QUALITY ASSURANCE

- Unit shall be certified (sizes 072-120) or rated in accordance with AHRI/ISO/ASHRAE (Air-Conditioning, Heating and Refrigeration Institute/International Organization for Standardization/American Society of Heating, Refrigerating, and Air-Conditioning Engineers) Standard 13256-1, latest edition.

- Units shall have insulation and adhesive which meet NFPA (National Fire Protection Association) 90A requirements for flame spread and smoke generation, and assembled units shall be UL (Underwriters Laboratories) listed, US and Canada, and meet UL-181 standards.

- Units shall undergo factory testing to verify operation of major components and safety devices prior to shipment.

- Product

- EQUIPMENT

- Heat Pump Assembly:

Factory-tested and assembled single-piece water source heat pump units shall be factory wired, charged with Puron refrigerant (R-410A), contain refrigerant-to-water heat exchanger, refrigerant-to-air heat exchanger, 4-way reversing valve, fan motor assembly, compressor, metering device, and all internal controls and safety devices.

- Unit Cabinet:

- All water source heat pumps shall be fabricated from heavy-gage sheet metal steel. All interior surfaces shall be lined with 1/2-in thick, multi-density acoustic insulation. Insulation within the air-handling section shall not have any exposed edges. All insulation must meet NFPA 90A and be certified to meet the GREENGUARD Indoor Air Quality Standard for Low Emitting Products. One blower access panel and two compressor compartment access panels shall be removable with supply and return air ductwork in place.

- Cabinets shall have separate holes and knockouts for entrance of line voltage and low voltage control wiring. Supply and return water connections shall be copper FPT fittings and shall be securely mounted flush to the cabinet allowing for connection to a flexible hose without the use of a back-up wrench. Water connections which protrude through the cabinet shall not be allowed.

- Units shall have the airflow arrangement as shown on the plans. If units with these arrangements are not used, the contractor supplying the water source heat pumps is responsible for any extra costs incurred by other trades and must submit detailed mechanical drawings showing ductwork requirements and changes or relocation of any other mechanical or electrical system. If other arrangements make servicing difficult the contractor must provide access panels and clear routes to ease service. The architect must approve all changes 10 days prior to bid.

- All units shall have a factory-installed two-sided filter rack capable of accepting 1-in. filters. Units shall have a 1 in. thick throwaway type fiberglass filter as standard. The filter rack shall incorporate a 1 in. duct flange.

- All units shall have stainless steel drain pans to comply with this project’s IAQ (indoor air quality) requirements. Painted steel or plastic materials shall not be permitted.

- Fan and Motor Assembly:

- The fan(s) shall be belt driven DWDI forward curved type with dynamically balanced wheel(s). The fan motor(s) shall be 1725 or 3450 rpm 56 frame sealed ball bearing type.

The motor(s) shall be permanently lubricated and have thermal overload protection.

- The fan and motor assembly must be capable of overcoming the external static pressures as shown on the schedule. External static pressure rating of the unit shall be based on a wet coil. Ratings based on a dry coil shall not be acceptable.

- Heat Exchangers:

- Finned tube refrigerant to air heat exchanger. Refrigerant-to-air heat exchangers shall utilize enhanced aluminum fins and rifled copper tube construction rated to withstand 600 psig refrigerant working pressure. All air coils shall have non-ferrous aluminum end plates.

- Coaxial (tube in tube) refrigerant-to-water heat exchanger:

Refrigerant-to-water heat exchangers shall be of copper inner water tube and steel outer refrigerant tube design rated to withstand 600 psig working refrigerant pressure and 400 psig working water pressure. Shell and tube style refrigerant to water heat exchangers shall be treated as pressure vessels and shall require refrigerant pressure relief valves piped to the exterior of the building. The contractor supplying the water source heat pumps with shell and tube heat exchangers shall be responsible for any additional insulation costs. Brazed plate water-to-refrigerant heat exchangers shall require additional centrifugal separators added to the supply water piping at each unit. Each separator shall have an automated clean out valve piped to a waste line. The contractor supplying water source heat pumps with brazed plate heat exchangers shall be responsible for any additional cost.

- Option for cupronickel water coil:

The refrigerant to water heat exchanger shall be cupronickel inner water tube.

- Refrigerant Components:

- Units shall use R-410A refrigerant. Units that use R-22 refrigerant shall not be allowed. All units shall have a factory sealed and fully charged refrigerant circuit with the following components.

- Thermostatic expansion valve shall be provided for refrigerant metering.

- Hermetic Compressor: Hermetic scroll compressors shall be specifically designed for R-410A refrigerant and shall be internally sprung (if reciprocating), externally isolated and with thermal overload protection. Unit compressors shall have rubber isolators to prevent transmission of vibration to the structure.

- Reversing Valve: Reversing valves shall be four-way solenoid activated refrigerant valves which shall fail to the heating operation should the solenoid fail to function. Reversing valves which fail to the cooling operation shall not be allowed.

- Controls and Safeties:

- Safety devices on all units shall include low-pressure sensor or loss-of-charge switch, high-pressure switch, low water temperature sensor, and condensate overflow switch.

- The standard unit control module shall provide control of major unit components and shall be compatible with heat pump thermostats or DDC controls. The standard control module shall have the following features:

- Anti-short cycle time delay on compressor operation; time delay shall be 5 minutes minimum

- Random start on power-up

- Low voltage protection

- High voltage protection

- Condensate overflow shutdown

- Condensate overflow protection: A condensate sensor shall activate the lockout circuit upon sensing a high level of condensate in the drain pan and immediately put the unit into a hard lockout.

- Unit shutdown on low or high refrigerant pressures.

- Unit shutdown on low water temperature with adjustable limit for standard and extended range applications.

- Option to reset unit at thermostat or 
disconnect.

- Automatic intelligent reset. Unit shall automatically reset after a safety shutdown and restart the unit after the anti-short cycle timer and random start timer expire. Should a fault reoccur within 60 minutes after reset, then a permanent lockout will occur. Reset attempts shall be selectable for either 2 or 4 tries. Condensate overflow shall put the unit into a hard lockout on the first fault.

- Ability to defeat time delays for servicing.

- Light-emitting diode (LED) to indicate high pressure, low pressure, improper voltage, water coil freeze protection, condensate overflow, and control status.

- Selectable 24-v or pilot duty dry contact alarm output.

- Freeze Protection. The freeze protection sensor shall be mounted close to the water coil to monitor refrigerant temperature between water coil and the thermal expansion valve or capillary tube. If the refrigerant temperature between the expansion device and water coil drops below or remains at 30°F for 30 seconds, the controller shall shut down the compressor and enter into a soft lockout condition. This trip point can be changed to 15°F by cutting the R17 and R77 resistors located above the DIP switch SW1 for applications that employ antifreeze. The freezestat may not provide protection in the case of loss of flow in the heating mode. A flow switch or pressure differential switch is recommended to prevent unit operation in case of loss of flow.

- Low pressure switch 120-second bypass timer.

- Alarm output selectable for constant output for general alarm notification, or pulse output for communication of the specific fault alarm.

- The optional Deluxe D control package shall have all the features of the Complete C control, with the following additional features:

- Boilerless control. Shall activate an electric heater and disable compressor should water temperature drop below set point. Includes a relay and splitting the power supply to the unit into a blower motor and control power supply and a compressor power supply. The relay (when energized) deactivates the compressor control circuit.

- Auxiliary pump/valve relay to enable a pump/valve operation when calling for compressor operation.

- Energy Management switch for remote enabling of the WSHP (water source heat pump).

- Phase monitor to protect the compressor from operating in reverse rotation on three phase units.

- WSHP Open Multiple Protocol Control:

- Units shall have all the features above (Complete C Board) and the state of the art WSHP Open multiple protocol interface board. All point objects will have the ability to be viewed in the Equipment Touch™, Sy-stem Touch™ or field assistant user interface. The following points must be available at a central or remote computer location:

- Space temperature

- Leaving water temperature

- Discharge air temperature

- Command of space temperature set point

- Cooling status

- Heating status

- Low temperature sensor alarm

- High pressure switch alarm

- Fan on/off position of space thermostat

- Unoccupied/occupied command

- Cooling demand

- Heating demand

- Fan “ON/AUTO” command

- Fault prevention with auto reset

- Itemized fault code viewed with Equipment Touch interface

- Additional WSHP Open multiple protocol control features shall include:

- Three-speed fan control. Controller shall automatically, based upon space temperature input, operate the fan at the lowest of 3 selectable speeds to achieve space temperature set point. A VFD (variable frequency drive) is required to operate 3-speed fan control.

- Two-position OA (outdoor air) damper

- Modulating OA damper with DCV (demand controlled ventilation)

- Hot gas reheat solenoid valve

- Two-position water economizer control

- Modulating water economizer control

- Single-stage electric auxiliary heat

- Power fail restart delay

- Two-stage compression control

- Multiple-protocol WSHP Open controller remote ZS sensors for DDC control options. Only Carrier ZS sensors can be used with the WSHP Open controller. Sensors are available as follows, and all sensors below offer monitoring of space temperature only, or space temperature and CO2, or space temperature and humidity, or space temperature and CO2 and humidity.

- ZS Standard sensor with a communication port.

- ZS Plus sensor with communication port, occupancy status indicator, local occupancy override and set point adjustment.

- ZS Pro sensor with communication port, occupancy status indicator, local occupancy override, set point adjustment, LCD display, alarm indicator and fan speed control.

- ZS Pro-F sensor with communication port, occupancy status indicator, local occupancy override, set point adjustment, LCD display, alarm indicator, fan speed control, cooling/heating/fan only mode control and F to C conversion.

- Electrical:

- A control box shall be located within the unit and shall contain a transformer, controls for the compressor, reversing valve and fan motor operation and shall have a terminal block for low voltage field wiring connections. The transformer shall be rated for a minimum 75 VA.

- Units shall be nameplated for use with time-delay fuses or HACR (heating, air-conditioning, and refrigeration) circuit breakers.

- Unit controls shall be 24-volt and provide heating or cooling as required by the remote thermostat.

- Units shall have a short circuit current rating (SCCR) of no less than 5 kA.

- Factory-Installed Options:

- Closed Cell Foam:

Closed cell foam (CCF) shall be installed on interior surfaces of water source heat pump and shall meet the density and compression requirements of ASTM D-1056, the water absorption requirements of ASTM D-1667 and the tensile and elongation requirements of ASTM D-412. Closed cell foam shall meet the flammability requirements of FMVSS302 and UL 94.

- Sound Attenuation Package (Mute Package):

Shall consist of a compressor blanket installed in the unit for additional attenuation.

- Extended Range:

Extended range units shall provide an insulated water circuit for the coaxial coil and refrigerant ci-rcuit to prevent condensation, and therefore potential dripping problems, in applications where the entering water temperature is beyond the normal operating range.

- Hot Gas Reheat:

Units as noted on the schedule shall be equipped with optional hot gas reheat (HGRH). On/Off HGRH shall be controlled by a humidistat connected to the unit H terminal and shall start the unit in reheat mode should the humidity be above set point once the thermostat control is satisfied. Cooling or heating requirements shall take precedent over HGRH.

- Hot Gas Bypass:

For units as noted on the schedule, supply each unit with a UL listed and MEA listed modulating hot gas bypass valve with factory-supplied and installed controls to prevent air coils from frost development by taking hot gas and bypassing the water coil and expansion device and reintroducing the hot gas into the refrigerant line prior to the air coil. The hot gas bypass valve shall maintain the minimum refrigerant suction pressure to allow for a light load cooling mode or a low entering air temperature cooling mode.

- Waterside Economizer:

Waterside economizer shall be completely installed at the factory, with condensate drain pan(s), motorized 3-way valve, aquastat, and all internal electric controls. Waterside economizer shall be rated at 400 psig and UL listed for application with the heat pump.

- Evaporator Coil Protection:

Evaporator coil protection shall be factory-installed with tin electro-plated copper tubing and high-tech polymer coated aluminum fins to protect the air coil from all forms of corrosive elements in the airstream.

- 1-Speed VFD:

Unit shall include a factory installed (50VQP) or field installed (50HQP) supply fan VFD with factory installed inverter duty motor. Two speed motors without VFDs or ECM motors are not acceptable.

- Staged Air Volume (SAV) – 2-Speed:

Unit shall include a factory-installed (50VQP) or field-installed (50HQP) supply fan VFD with factory-installed inverter duty motor. Unit and VFD shall be configured for stage air volume control in which the supply fan airflow can be varied based on load. Two speed motors without VFDs or ECM motors are not acceptable.

- 2 In. Filter Rack:

Unit shall include a factory installed 2 in., four sided filter rack with factory supplied 1 in. throwaway filters. Filter rack design shall not require the use of tools for filter changes. Hinges, thumb-screws, or screws for filter access are not acceptable.

- Accessories:

- Hose Kits and Valves:

All units shall be connected to main water supply and return headers with hoses. The hoses shall be 2 or 3 feet long, braided stainless steel rated to 400 psig at 265°F. Hoses may contain optional ball valves with P/T (pressure/temperature) ports, Y strainers with blow down valves and/or autoflow regulators as specified in the schedule.

- Ball Valves (Brass Body):

Valves shall be available for shutoff and balancing water flow. Available with memory, memory stop, and pressure temperature ports.

- Y Strainers (Bronze Body):

Strainers are “Y” type configuration with a brass cap. Maximum operating pressure rating of strainers is 450 psig. Strainer screen shall be made of stainless steel.

- Electric Duct Heaters:

- Duct heater shall be slip-in or flanged type and shall be UL approved for zero clearance to combustible surfaces. The heater shall bear a UL/CSA (Canadian Standards Association) label. Control panel and element housing shall be constructed of heavy gage galvanized steel. All heating elements shall be made of nickel/chromium resistance wire with ends terminated by means of staking and heliarc welding to machine screws. Heating element support structure shall consist of galvanized steel wire formed and constructed to support ceramic bushings through which the heating element passes. Control cabinet shall be constructed of heavy gage galvanized steel with multiple knockouts for field wiring. Control cabinet shall have a solid cover also of heavy gage galvanized steel and held in place with hinges and tool-release latches.

- Duct heater shall be supplied with primary over temperature protection by built in disc type automatic reset thermal cutouts and secondary over temperature protection by built in disc type manually resettable thermal cutouts. These devices must function independently of one another and are not acceptable if series connected in the control circuit wiring. A disconnecting magnetic control circuit is required. All duct heaters will require either a fan interlock circuit or an airflow switch.

- Over-current protection by means of factory-installed fusing within the control cabinet shall be provided for heaters rated at more than 48 amps. Heating elements shall be subdivided and fused accordingly.

- All wiring, component sizing, component spacing and protective devices within the control cabinet shall be factory installed and comply with NEC (National Electrical Code) and UL (Underwriters Laboratories) standardization. All heaters shall function properly with a 60 Hz power supply.

- A wiring diagram depicting layout and connections of electrical components within the control cabinet shall be affixed to the inside of the control cabinet cover.

- A rating plate label shall be affixed to the exterior of the control cabinet cover which states model number, serial number, volts, amps, phase, frequency, control volts, volt-amps and minimum airflow requirements.