Console Water Source Heat Pumps

HVAC Guide Specifications

Size Range: 3/4 to1-1/2 Nominal Tons

Carrier Model Number: 	50PEC

- General

- SYSTEM DESCRIPTION

- Install water source heat pumps, as indicated on the plans with capacities and characteristics as listed in the schedule and the specifications that follow. All equipment shall be rated and certified in accordance with ANSI/AHRI/ASHRAE/ISO (American National Standard Institute/Air-Conditioning, Heating and Refrigeration Institute/American Society of Heating, Refrigerating, and Air-Conditioning Engineers/International Organization for Standardization) 13256-1. All equipment shall be tested, investigated, and determined to comply with the requirements of the standards for Heating and Cooling Equipment UL-60335-2-40 for the United States and CSA C22.2 No. 60335-2-40 for Canada, by Intertek Testing Laboratories (ETL). The units shall have AHRI/ISO and ETL-US-C labels.

- Units shall be supplied completely factory built and capable of operation with an entering water temperature range from 20 to 110°F. Quality control system shall automatically perform via computer: triple leak check, pressure tests, evacuation and accurately charging of system, detailed heating and cooling mode tests, and quality cross checking all operational and test conditions to pass/fail criteria.

- Units shall be individually packaged with wooden skid covered with protective corner posts and plastic stretch wrapping for maximum protection.

- QUALITY ASSURANCE

- All equipment listed in this section must be rated in accordance with ANSI/AHRI/ASHRAE/ISO 13256-1 performance standard, latest edition. The applicable units shall have an AHRI/ISO label. Standard cabinet panel insulation shall meet NFPA (National Fire Protection Association) 90A requirements, air erosion and mold growth limits of UL-181, stringent fungal resistance test per ASTM-C1071 and ASTM G21 and shall meet zero level bacteria growth per ASTM (American Society for Testing and Materials) G22.

- Units shall be factory tested to verify operation of critical components and verify functionality of control and safety devices.

- Product

- EQUIPMENT

- General: Units shall be completely assembled, piped, internally wired, and fully charged at the factory.

- Unit Cabinet:

- Cabinet work shall include two separate integral assemblies: cabinet and sub-base. Cabinet shall be factory fabricated from heavy gauge galvanized steel, finished with powder coat paint. Cabinet dimensions are in accordance with drawings and are manufactured for left or right water discharge piping. Cabinet shall be single-piece construction. Removal of the cabinet shall give complete side and front access to unit for routine servicing. The cabinet is mounted onto the sub-base and secured with two screws for security. A wall mounting bracket secured to the sub-base shall be provided. Air flow is bottom intake-top discharge. Cabinets will be factory fabricated specifically for left hand or right hand connections as specified. Cabinet shall be slope top style, flat top cabinet is not acceptable.

- An access door shall be provided to access the unit mounted controller (units with unit mounted controller only).

- Factory mounted 3-3/8-in. sub-base is constructed of heavy gage painted steel. Cutouts are provided for floor connections and outside air. Includes integral filter mounts to support a bottom mount permanent, washable, aluminum mesh filter. Sub-base shall have integral wall bracket.

- Chassis:

The unit shall be chassis only, chassis on sub-base, or chassis with sub-base and cabinet. The chassis is of compact design and of the same dimensions for all model sizes. Dimensions must match details on drawings. Chassis mounts directly on support structures provided by the sub-base and shall be removable from the sub-base without dismantling the sub-base. Both the compressor and coil compartment shall be thermally and acoustically insulated, and have removable steel cover plates giving double acoustical protection between the two compartments. Compressor is mounted to the bottom of chassis with a 2-piece basepan to reduce noise transmission and vibration. The compressor access panel shall have a closed cell foam insulation for extra quiet operation. Fiberglass insulation is not acceptable on compressor access panel. The stainless steel condensate drain pan shall be IAQ with positive double slope and be removable without disturbing the evaporator assembly for cleaning as needed.

- Fan and Motor Assembly:

Unit blower has a high efficiency PSC motor with two speed settings. Motor is direct connected to two double width, double inlet forward curved oversized centrifugal blower wheels that are selected for quiet operation, and balanced to minimize vibration. Blower wheel access is through removable blower inlet rings. Motor and blower assembly shall be removable without removing the chassis.

- Outside Air Damper (optional):

Unit shall have a factory installed, motorized, 2-position, outdoor air damper.

- Refrigerant Components:

- Units shall have a sealed refrigerant circuit including a rotary compressor, a refrigerant metering device, a finned tube refrigerant-to-air heat exchanger, a reversing valve, a coaxial (tube-in-tube) refrigerant-to-water heat exchanger, and safety controls including a high-pressure sensor, a loss-of-charge sensor to protect against loss of refrigerant, and low water temperature (freeze-stat) sensor.

- Rotary compressors shall have thermal overload protection and shall be located in an insulated compartment to minimize sound transmission. Units shall have the compressor mounted on isolators to reduce noise and vibration transmission.

- Air Coils shall be coated using an electro coating process for protection against most airborne chemicals.

- Coaxial (tube in tube) refrigerant-to-water heat exchanger. Refrigerant-to-water heat exchangers shall be of copper inner water tube and steel outer refrigerant tube design rated to withstand 600 psig working refrigerant pressure and 450 psig working water pressure.

- [Optional] Cupronickel coaxial water-to-refrigerant heat exchangers shall be provided, with cupronickel inner water tube construction.

- Drain pan shall be constructed of stainless steel to resist corrosion.

- Reversing valve shall be four-way solenoid-activated refrigerant valves which shall fail to heating operation. If the unit fails to cooling a low-temperature thermostat must be provided to prevent over-cooling of the room.

- Piping:

- Copper tubes with a 5/8 in. OD dimension shall be provided on the supply and return water connections for the purpose of forming a sweat connection to field-supplied distribution piping.

- [Optional] Female Pipe threaded (FPT) connections: A 1/2 in. female pipe threaded fitting shall be factory mounted on the supply and return water connections.

- Controls and Safeties:

- Electrical:

- A control box shall be located within the unit and shall contain controls for compressor, reversing valve and fan motor operation.

- Units shall be provided with a factory mounted 2 x 4 junction box with removable cover on the same side as the water connections (left or right) for direct wire connection. This cover may be supplied with a non-fused power disconnect switch for servicing the unit. The unit shall operate with specified voltages 115 volt, 208/230 volt or 265 volt, single phase, 60 Hz supply current. Units with power cord and plug are not acceptable.

- All 50PEC console units are rated for 5kA SCCR.

- Controls and safety devices will be factory wired and mounted within the unit. Controls shall include fan relay, compressor contactor, 24-v transformer, reversing valve coil, and Unit Protection Module (UPM). The standard transformer shall be rated for a minimum 40 VA for all sizes, or 50 VA for 265-v units, or 75 VA for units with TruVu™ controller. All units shall be name plated for use with time-delay fuses or HACR circuit breakers. Unit controls shall be 24-v and provide heating or cooling as required by the remote thermostat/sensor.

- [Optional] A larger transformer rated for at least 75 VA shall be available for all unit sizes and have a push button reset circuit breaker on the secondary power.

- Unit shall include a wiring diagram permanently affixed to the inside of the cabinet.

- All units shall have a Unit Protection Module (UPM) printed circuit board which implements following equipment safeties:

- Anti-short cycle time delay (5-minute delay on break).

- Random start time delay on initial power.

- Brownout / surge / power interruption protection.

- 120 second low pressure switch bypass timer.

- High refrigerant pressure shutdown.

- Low refrigerant pressure shutdown.

- Water coil freeze protection shutdown.

- Air coil freeze protection shutdown.

- High condensate level shutdown.

- 24 vac alarm output for remote fault indication.

- Intelligent alarm reset.

- The UPM shall automatically reset after a safety shutdown. Restart the unit if the cause of the shutdown no longer exists (except for low temperature and high condensate level shutdowns). Should a fault re-occur within 60 minutes after reset, then a “hard” lockout will occur. A light-emitting diode (LED) shall annunciate the following alarms: brownout, high refrigerant pressure, low refrigerant pressure, low water temperature and a high level of condensate in the drain pan, refrigerant leak fault. The LED will display each fault condition as soon as the fault occurs. If a hard lockout occurs, then the fault LED will display the type of fault until the unit is reset.

The UPM shall feature the following field configurable adjustments:

- Lock out reset on thermostat interruption or power reset.

- Two or four restart attempts before a hard lockout.

- Test mode (reduces all time delays to 5 seconds for diagnostic work).

- Air/water coil freeze limit trip.

- [Optional] The optional unit mounted controller (UMC) shall provide a tactile touchpad for temperature, fan and mode adjustment and provide a digital display of temperature in either degrees Fahrenheit or Celsius. The unit mounted controller shall provide an LED display for indication of unit operating mode as well as fan speed and fault indication for high or low pressure lockout. Rotary dial electromechanical controls shall not be acceptable. Options and features shall include:

- adjustable temperature set point from 60°F through 80°F (15.5°C through 26.7°C)

- adjustable temperature differential between 1°F and 6°F (0.6°C and 3.3°C)

- manual or automatic changeover

- high and low fan speed control

- constant fan speed or fan speed cycling with compressor.

- a 5-minute anti-short cycling delay

- random start

- a 90-second low pressure bypass timer.

- intelligent reset to allow unit to automatically restart after 5 minutes if a fault is no longer active

- [Optional] Units shall have all the features above (UPM) and additionally TruVu™ DDC controller shall have an advanced controls logic and include following features:

- Two-speed fan control. Controller shall automatically, based upon space temperature input, operate the fan at the lowest of 2 selectable speeds to achieve space temperature set point.

- Two-position OA (outdoor air) damper.

- Modulating OA damper with DCV (demand controlled ventilation).

- Scheduling.

- Adaptive optimal start.

- Equipment performance monitoring.

- Alarm status.

TruVu™ controller must be capable of communicating over BACnet IP, supporting direct connection or daisy chain topologies using BACnet/IP for seamless integration into building automation systems, and shall have the ability to be viewed in the TruVu Equipment Touch (ET), or field assistant user interface.

- [Optional] Non-fused electrical disconnect shall be installed on the unit.

- [Optional] Energy management switch to enable remote operation of WSHP (water source heat pump).

- [Optional] Pump-valve relay to enable a pump/valve operation when calling for compressor operation.

- [Optional] Compressor status relay shall be provided to monitor a status of the compressor via normally open set of dry contact.

- [Optional] Outdoor air dampers shall be motorized with a spring return motor solenoid. The damper shall open when the damper switch is set to “ON” and a request for the compressor to run is provided by the system.

- Accessories:

- Hydronic accessories:

- Hose Kits

All units shall be connected to main water supply and return headers with hoses. The hoses shall be 2 or 3 feet long, braided stainless steel rated to 400 psig at 265°F. Hoses may contain optional ball valves with P/T ports, Y strainers with blow down valves and/or auto flow regulators as specified in the schedule.

- Two-position motorized isolation valve (2-way solenoid valve) with end switch is available for field installation. The two-way motorized solenoid valve is rated for a 125 psig working pressure. The valve shall be field wired to open with compressor operation.

- Ball Valves (Brass Body)

Valves shall be available for shutoff and balancing water flow. Available with memory, memory stop, and pressure temperature ports (600WOG at 325°F).

- Y Strainers (Bronze Body)

Strainers are “Y” type configuration with a brass cap. Strainer screen shall be made of stainless steel (600WOG at 325°F).

- Controls accessories:

- Carrier commercial thermostat controls are available as follows:

- Edge® Pro 7-day programmable thermostat offers 2-stage heat, 2-stage cool, remote contact input, remote sensor capability, pre-occupancy purge, soft start, manual/auto changeover, 4 settings per day, 24 vac, backlit LCD, keypad lockout, no batteries required, 5-minute compressor protection, never lost memory, 3 security levels, and temperature display in degrees F or C.

- Comfort Pro Programmable Thermostat, 2-stage Heat /2-stage Cool G/E, plus 1-stage auxiliary or emergency heat HP&WSHP, or 2-stage cool/heat only, Touch n Go™ prog. (OCC/UNOCC/ LIMIT), Passcode protection, remote sensor capability with override, random start, Manual/Auto-Changeover, Outdoor/supply/return temp, hospitality mode, option battery powered.

- Carrier Connect™ Wi-Fi 7-day programmable/non-prog; 4.3 in. touch screen, web enabled (portal), smartphone app, 1-2 stage heat/1-3 stage cool, G/E, HP (with 2-stage aux heat), remote sensor capability, manual/auto-changeover, humidify/dehumidify/Humidi-MiZer™

- Non-Branded Wi-Fi 7-day programmable/non-prog; 4.3 in. touch screen, web enabled (portal), smartphone app, 1-2 stage heat/1-3 stage cool, G/E, HP (with up to 2-stage aux heat), remote sensor capability, manual/auto-changeover, humidify/dehumidify/Humidi-MiZer™

- ComfortVu BACnet Thermostat, 24 VAC Thermostat, offers a large backlit LCD display and intuitive push-button controls for easy operation, BACnet MS/TP port, 2 universal inputs, 2 universal outputs, and 4 relay outputs, it allows control over up to 3 stages of heating and 2 stages of cooling, along with up to 3 fan speeds.

- ZS sensors for TruVu™ DDC (direct digital controls) control option. Sensors are available as follows, and all sensors below offer monitoring of space temperature only, or space temperature and CO2, or space temperature and humidity, or space temperature and CO2 and humidity.

- ZS Standard sensor with a communication port.

- ZS Plus sensor with communication port, occupancy status indicator, local occupancy override and set point adjustment.

- ZS Pro sensor with communication port, occupancy status indicator, local occupancy override, set point adjustment, LCD (liquid crystal diode) display, alarm indicator and fan speed control.

- ZS Pro-F sensor with communication port, occupancy status indicator, local occupancy override, set point adjustment, LCD display, alarm indicator, fan speed control, cooling/heating/fan only mode control and F to C conversion.

- TruVu™ Equipment Touch (ET) for unit start-up and commissioning shall be available in 7 and 10 in. touch screen sizes for panel or wall mounting. All point objects will have the ability to be viewed in the TruVu™ ET user interface.