Commercial Air-Cooled Condensing Units

HVAC Guide Specifications

Size Range:
	25 to 130 Nominal Tons at 60 Hz

88 to 457 Nominal kW at 60 Hz

21 to 108 Nominal Tons at 50 Hz

73 to 381 Nominal kW at 50 Hz

With Greenspeed® Intelligence:
	25 to 60 Nominal Tons at 60 Hz

88 to 211 Nominal kW at 60 Hz

21 to 50 Nominal Tons at 50 Hz

73 to 176 Nominal kW at 50 Hz

Carrier Model Number: 	38APD, 38APS

- General

- SYSTEM DESCRIPTION

Outdoor-mounted, air-cooled condensing unit with Puron® refrigerant (R-410A) suitable for on-the-ground or rooftop installation. The 38APS unit shall have one refrigeration circuit and shall consist of two or three rotary scroll compressors. The 38APD unit shall have two independent refrigeration circuits and shall consist of two, four, five or six rotary scroll compressors. Unit shall have air-cooled coils, propeller-type condenser fans, a control box, and shall discharge condenser air vertically upward as shown on certified drawings. Unit shall be used in refrigeration circuit with a central station air-handling unit or direct-expansion coils.

For units that incorporate Greenspeed intelligence, all fans are controlled with variable speed fan drive motors. Unit software shall be specifically developed to coordinate optimal fan speed for application conditions and provide refrigerant circuit optimization, resulting in higher part load efficiency and reduced acoustic levels.

- QUALITY ASSURANCE

- Unit performance shall be rated in accordance with AHRI (Air-Conditioning, Heating, and Refrigeration Institute) Standard 365, latest edition (U.S.A).

- Unit construction shall comply with latest edition of ASHRAE (American Society of Heating, Refrigerating, and Air-Conditioning Engineers) 15 Safety Code, UL 1995, and ASME (American Society of Mechanical Engineers) applicable codes (U.S.A. codes).

- The management system governing the manufacturer of the product is ISO (International Organization for Standardization) 9001: 2015 certified.

- Base unit shall be constructed in accordance with UL (Underwriters Laboratories) standards and CSA (Canadian Standards Association).

- Painted parts shall withstand 1000 hours in constant neutral salt spray under ASTM B117 conditions with a 1mm scribe per ASTM D1654. After test, painted parts shall show no signs of wrinkling or cracking, no loss of adhesion, no evidence of blistering, and the mean creepage shall not exceed 1/4 in. (Rating ≥ 4 per ASTM D1654) on either side of the scribe line.

- Design pressure shall be 650 psig (4482 kPa).

- Unit shall be functional checked at the factory.

- Lifting holes shall be provided to facilitate rigging.

- DELIVERY, STORAGE, AND HANDLING

Unit shall be shipped as single package and shall be stored and handled per the unit manufacturer's recommendations.

- WARRANTY (FOR INCLUSION BY SPECIFYING ENGINEER)

- Products

- EQUIPMENT

- General:

Factory assembled, single-piece, air-cooled condensing unit. Contained within the unit enclosure shall be all factory wiring, piping, controls, compressors, nitrogen holding charge, and special features required prior to field start-up.

- Unit Cabinet:

- Cabinet shall be galvanized steel casing with a baked enamel powder or pre-painted finish.

- Control box access panels shall be hinged for service access.

- Fans:

- Condenser fans shall be direct-drive propeller type, discharging air vertically upward.

- All condenser fan motors shall be totally enclosed 3-phase type with permanently lubricated ball bearings, class F insulation and internal, automatic-reset thermal overload protection or manual reset calibrated circuit breakers.

- Fans on units with Greenspeed intelligence shall be controlled by a variable-frequency drive, and the drive shall include a DC link reactor.

- Shafts shall have inherent corrosion resistance.

- Fan blades shall be statically and dynamically balanced.

- Condenser-fan openings shall be equipped with PVC-coated steel wire safety guards.

- Compressors:

- Compressors shall be rotary scroll.

- Operating oil charge and a crankcase heater control oil dilution.

- Compressors shall be mounted on two rails having rubber in shear vibration isolators.

- Staging of compressors shall provide unloading capability. Digital compressor unloading control shall be available as an option on one circuit (not available on size 065 unit).

- Compressor motors shall be cooled by refrigerant gas passing through motor windings and shall have either internal line break thermal and current overload protection or external current overload modules with compressor temperature sensors.

- Condenser Coils:

- Coil shall be air-cooled microchannel heat exchanger (MCHX) and shall have a series of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds. Microchannel coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for the fins, tubes and manifolds in combination with a corrosion-resistant coating on the tubes.

- Tubes shall be cleaned, dehydrated, and sealed.

- Assembled condenser coils shall be leak tested and pressure tested at 650 psig (4482 kPa).

- To plan the unit installation and for ease of maintenance/coil removal on unit sizes 38AP065-130, all refrigerant piping entering and leaving the condenser coils shall be located on only one side of the condensing unit so the coils can be removed (when needed) from the side free of piping. This is important to consider because removing the coils from the header side, although possible, involves extra labor due to extra bending and brazing of the coil headers.

- Refrigeration Components:

- Refrigeration circuit components shall include liquid line temperature relief device, pressure transducers, liquid line shutoff valve, suction shutoff valve, suction line accumulators, nitrogen holding charge, and compressor oil.

- Long line length check valves are required for liquid line installation on all linear line length applications of more than 100 ft (30.5 m) to prevent liquid migration during unit shutdown. For any 025-030 size dual circuit unit application where evaporator is located higher than the condensing unit, check valves are required for linear line length above 55 ft (16.8 m).

- Units shall include one factory-installed suction line accumulator for each refrigerant circuit.

- Controls and Safeties:

- Unit ComfortLink controls shall include:

- Scrolling marquee display module shall be used for accessing condensing unit information, reading sensor values, and testing the condensing unit. The scrolling marquee display is a 4-key, 4-character, 16-segment LED (light-emitting diode) display. Eleven mode LEDs shall be located on the display as well as an Alarm Status LED. The display shows all of the ComfortLink control codes (with 60-character expandable clear language), plus set points, time of day, temperatures, pressures, and superheat. Additional information can be displayed all at once with the accessory Navigator™ display.

- Carrier Comfort Network® (CCN) system capability.

- Unit control with standard pressure transducer, discharge pressure transducer and suction temperature thermistors.

- Current alarm list and alarm history list on display.

- Automatic compressor lead/lag control.

- Service run test capability.

- Compressor minimum run time (3 minutes) and minimum off time (3 minutes).

- Service diagnostic mode.

- Self-contained low voltage control circuit.

- Cycle condenser fans to maintain proper head pressure control.

- Capacity control with staging compressors.

- Optional digital scrolls to stage compressors and cycle digital compressor for maintaining desired leaving air temperature set point.

- Alarm relay output to indicate when unit is in alarm condition.

- Minimum unit safety devices shall include:

Solid-state compressor lockout to provide optional reset capability at the space thermostat if any of the following safety devices trip and shut off compressor.

- Compressor lockout protection for internal or external overload.

- Low pressure protection.

- High pressure protection (high pressure switch or internal).

- Compressor reverse rotation protection.

- Loss of charge protection.

- Low suction superheat protection.

- Short cycle protection.

- Suction and discharge pressure transducers.

- Circuit breakers or fuses for short circuit protection of compressors.

- Operating Characteristics:

- The capacity of the condensing unit shall meet or exceed ____ Btuh (____kW) at a suction temperature of ____°F (____°C). The power consumption at full load shall not exceed ____Btuh (____kW).

- The combination of the condensing unit and the evaporator or air-handling unit shall have a total net cooling capacity of ____ Btuh (____kW) or greater at conditions of ____ cfm (____L/s) entering-air temperature at the evaporator at ____°F (____°C) wet bulb and ____°F (____°C) dry bulb, and air entering the condensing unit at ____°F (____°C).

- The system shall have an Energy Efficiency Ratio (EER) of ____Btuh/watt or greater at standard AHRI conditions.

- Electrical Requirements:

All unit power wiring shall enter unit cabinet at a single location (115 and 130 size units available with dual point power with terminal block).

- Special Features:

- High-efficiency variable condenser fans:

All fans on the unit shall have variable speed fan motors to provide higher part load efficiency and reduced acoustic levels. Each fan circuit shall have a factory-installed, independent variable speed drive with display. Variable speed drives are rated IP-55 enclosures and UL Listed. The use of this option, with the addition of wind baffles, shall allow running with outdoor ambient temperatures down to –20°F (–28.9°C). This option is available on unit sizes 025-060.

- Optional Condenser Coil Materials:

- E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum microchannel coils shall be capable of withstanding 8,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) B-117 Standard.

- Aluminum fin/copper tube coils:

Coil shall be constructed of seamless copper tubes mechanically bonded to aluminum fins. Fins shall have wavy enhancements. These condenser coils are recommended with remote cooler applications. These coils are not recommended for corrosive environments.

- Pre-coated aluminum-fin coils:

Coil shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments. Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube. Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.

- E-coated aluminum-fin coils:

Coil shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss; 60° of 65 to 90% per ASTM ID523-89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). E-coated aluminum-fin coils shall be capable of withstanding an 8000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) (U.S.A.) B-117 Standard. Coil construction shall be aluminum fins mechanically bonded to copper tubes.

- Sound Reduction:

- Low sound fan for sound reduction is available as a factory-installed option or field-installed accessory for all units.

- Low sound compressor blankets for additional sound reduction are available as a factory-installed option on all units having low sound fans or as a field-installed accessory.

- Digital Compressor Option:

Modification shall include digital compressor to provide incremental steps for tighter temperature control. The digital compressor shall be available as a factory-installed option for all units except size 065.

- Non-Fused Disconnect:

A non-fused disconnect is available as a factory-installed option for all units having single point power connection units.

- Long Line Length Check Valves:

Long line length check valves are available as options shipped with the unit or accessories shipped separately. In either case, field installation is required.

- High Short Circuit Current Rating (SCCR):

The optional high SCCR interrupt capability shall allow the unit to tolerate a 65 kA (208/230v, 380v and 460-v units) or 25 kA (575-v units) short circuit current for a brief period of time while protecting downstream components. The high SCCR option shall provide a higher level of protection than the standard unit (option for 60 Hz only). High interrupt shall be available as a factory-installed option strictly in conjunction with a non-fused disconnect and only with single-point power connection.

- Navigator™ Hand Held Display:

- Portable hand held display module with a minimum of 4 lines and 20 characters per line, of clear English, French, Spanish, or Portuguese language.

- Display menus shall provide clear language descriptions of all menu items, operating modes, configuration points and alarm diagnostics. Reference to factory codes shall not be accepted.

- RJ-14 connection plug shall allow display module to be connected to factory-installed receptacle.

- Industrial grade coiled extension cord shall allow the display module to be moved around the unit.

- Magnets shall hold the display module to any sheet metal panel to allow hands-free operation.

- Display module shall have NEMA (National Electrical Manufacturers Association, U.S.A.) 4x housing suitable for use in outdoor environments.

- Display shall have back light and contrast adjustment for easy viewing in bright sunlight or night conditions.

- Navigator module shall have raised surface buttons with positive tactile response.

- Navigator module shall be available as field-installed accessory for all units.

- BACnet Communication Option:

The BACnet Communication option shall provide factory-installed communication capability with a BACnet MS/TP network. Allows integration with i-Vu® Open control system or a BACnet building automation system.

- BACnet Translator Control:

BACnet control shall be available as a field-installed accessory for all units to provide interface between unit and a BACnet Local Area Network (LAN, i.e., MS/TP EIA-485).

- LON Translator Control:

Unit shall be supplied with field-installed interface between the chiller and a Local Operating Network (LON, i.e., LonWorks FT-10A ANSI/EIA-709.1). LON shall be available as a field-installed accessory for all units.

- Touch Pilot™ Display:

Touch Pilot remote mount touch screen display for network attachment to unit shall be available as a field-installed accessory for all units.

- Energy Management Module (EMM):

The EMM shall provide remote set point, demand limit control, and percent capacity input. The EMM is not needed with use of BACnet or LON accessory kit.

- Security Grilles/Hail Guards:

Units shall be supplied with factory-installed or field-installed louvered, sheet metal panels which securely fasten to the unit to provide condenser coil protection against hail and physical damage.

- Vibration Isolation Pads:

Neoprene vibration isolation pads (24 in. x 3 in. x 1/4 in.) shall be available for field installation to reduce vibration transmission from the compressor through the floor and into the conditioned space.

- Wind Baffle Kit:

Wind baffles facilitate operation down to –20°F (–29°C) when used in conjunction with high-efficiency variable condenser fans. The combination of wind baffles and high-efficiency variable condenser fans is available on unit sizes 025-060.

- Seismic Certification:

A seismic unit modification is available which will result in a unit SDS (seismic design acceleration parameter) level of 2.5 for 38AP025-065 units and 2.1 for 38AP070-130 units.