39M Indoor Air Handler Units

HVAC Guide Specifications

Size Range: 1,500 to 60,500 Nominal Cfm

Carrier Model Number: 39MN — Indoor Unit

- General

- QUALITY ASSURANCE

- Manufacturer Qualifications:

Company specializing in manufacturing the products specified in this section with minimum of five years documented experience.

- The management system governing the manufacture of this product is ISO (International Organization for Standardization) 9001:2015 certified.

- Air-handling unit assembly shall have UL (Underwriters Laboratories) 1995 certification for safety, including use with electric heat.

- Products requiring electric connection shall be listed and classified by ETL and CSA (Canadian Standards Association) as suitable for the purpose specified and indicated.

- All coils shall be rated in accordance with AHRI Standard 410, latest edition. Chilled water, hot water, and steam coils shall be certified, in accordance with AHRI Standard 410.

- Direct expansion coils shall be designed and tested in accordance with ANSI/ASHRAE (American National Standard Institute/American Society of Heating, Refrigerating and Air-Conditioning Engineers) 15 Safety Code for Mechanical Refrigeration.

- Unit performance shall be rated in accordance with AHRI Standard 430 for Central Station Air Handling Unit Supply Fans and subject to verification of rating accuracy by AHRI-sponsored, third party testing.

- Units shall meet NFPA (National Fire Protection Association) 90A requirements.

- DELIVERY, STORAGE AND PROTECTION

- All indoor units, painted or unpainted, shall be completely shrink-wrapped from the factory for protection during shipment. Tarping of bare units is unacceptable.

- Inspect for transportation damage and store in clean dry place and protect from weather and construction traffic. Handle carefully to avoid damage to components, enclosures, and finish.

- START-UP REQUIREMENTS

Do not operate units until ductwork is clean, filters are in place, bearings lubricated, condensate properly trapped, piping connections verified and leak tested, belts aligned and tensioned, all shipping braces have been removed, and fan has been test run under observation.

- Products

- GENERAL DESCRIPTION

- Units shall ship in the number of sections necessary to meet project requirements and shall ship in as many splits as specified in selection software. Split options as follows:

- Shipped in sections — shipping split.

- Shipped assembled — base rail break (ship attached).

- Shipped assembled — solid base rail.

- Unit shall be factory-supplied, central station air handler. The air-handling unit may consist of a fan with the following factory-installed components as indicated on the equipment schedule.

- Mixing Box Section:

- No filter tracks.

- With flat filter tracks.

- With angle filter tracks.

- With bag cartridge filter tracks.

- With exhaust air dampers.

- Air Mixing Section.

- Exhaust Box Section.

- Integral Face and Bypass Section:

- With hot water coil.

- With steam coil.

- Internal Face and Bypass Damper Section.

- External Face and Bypass Damper Section.

- Plenum Section:

- With drain pan.

- No drain pan.

- Humidifier Section.

- Blow-Thru Discharge Plenum.

- With no openings

- With custom discharge openings

- Filter Section:

- 2-in. flat filters.

- 4-in. flat filters.

- 4-in. flat filters with 2-in. pre-filters.

- 2-in. angle filters.

- 4-in. angle filters.

- Side loading 12-in. bag/cartridge filters with 2-in. pre-filters.

- Side loading 30-in. bag/cartridge filters with 2-in. pre-filters.

- Face loading bag/cartridge filters without pre-filters. Maximum bag/cartridge filter length is limited to access/plenum sections placed after this section.

- Face loading HEPA (high-efficiency particulate air) bag/cartridge filters without pre-filters.

- Gas Heating Section.

- Coil Section:

- Chilled water coil.

- Direct expansion coil.

- Hot water coil.

- Steam coil.

- Electric coil.

- Multi-Zone Cooling/Heating Coil Section:

- With dampers.

- No dampers (for dual duct).

- Energy Recovery Wheel Section.

- Fan Section:

- Horizontal draw-thru (supply, return, and exhaust).

- Horizontal blow-thru (with integral diffuser on supply fan only).

- Plenum fan:

- With custom discharge openings on draw thru supply fans

- With optional exhaust air damper on return fans

- Vertical draw-thru.

- CASING

- Construction:

- Unit shall be constructed of a complete frame with easily removable panels. Removal of any panel shall not affect the structural integrity of the unit.

- All units shall be supplied with 14-gage or heavier, G-90 galvanized steel base rails. Bolt-on legs are NOT acceptable. Perimeter lifting lugs for overhead lifting shall be provided on each shipping section. Slinging units in place of lifting lugs shall not be acceptable.

- Unit shall be thermally broken to minimize the conduction path from the inside of the casing to the outside.

- Casing panels (top, sides, and bottom) shall be constructed of galvanized steel (18 gauge optional), and shall have one of the following exterior finishes as specified:

- Pre-painted with a baked enamel finish passing 500-hour salt spray test (ASTM [American Society of Mechanical Engineers] B-117) for pre-painted steel and 125-hour marine level 1 prohesion test (ASTM G-85.A5) for pre-painted steel.

- Unpainted G-90 galvanized steel.

- Casing panels (top, sides, and bottom) shall be constructed of galvanized steel (18 gauge optional) or stainless steel, and shall have one of the following interior finishes as specified:

- G-90 pre-coated galvanized steel with a silver zeolite antimicrobial material registered by the US EPA (Environmental Protection Agency) for use in HVAC applications.

- Unpainted G-90 galvanized steel.

- Unpainted 304 stainless steel.

- Option for aluminum diamond treadplate floors.

- Casing panels (top, sides, and bottom) shall be one piece, double-wall construction with foam insulation sealed between the inner and outer panels. Panel assemblies shall not carry an R-value of less than 13.

- Casing deflection shall not exceed a L/240 ratio when subject to an internal pressure of ± 8-in. wg and shall exhibit no permanent deformation at ± 9-in. wg. L is defined as the longest linear panel or cabinet length (measured to AHRI 1350 Cd level 2).

- Casing leakage rate shall be less than 1% at 8 in. wg of nominal unit airflow or 50 cfm, whichever is greater. Leakage rate shall be tested and documented on a routine basis on random production units. Optionally, factory witness leak testing and/or test reports shall be available.

- Side panels shall be easily removable for access to unit and shall seal against a full perimeter automotive style gasket to ensure a tight seal.

- The panel retention system shall comply with UL 1995 which states all moving parts (for example, fan blades, blower wheels, pulleys, and belts) that, if accidentally contacted, could cause bodily injury, shall be guarded against accidental contact by an enclosure requiring tools for removal.

- Accessibility options shall be as follows:

- Hinged, lockable double-wall access door on either side with removable access panel(s) on the other side.

- Hinged, lockable double-wall access doors on both sides.

- Removable double-wall access panels on both sides.

- Depending on the options selected and the remaining available space inside each section, the following options may be available:

- Reinforced glass viewports shall be factory-installed on the access panel(s) or door(s) of the section.

- Marine lights shall be factory installed with or without GFCI (ground fault circuit interrupter) convenience outlets.

- Fan supports, structural members, panels, or flooring shall not be welded, unless aluminum, stainless steel, or other corrosion-resistant material is used. Painted welds on unit exterior steel or galvanized steel are not acceptable.

- All coil sections shall be doublewall construction with foam insulation sealed between the inner and outer panels. Panel assemblies shall not carry an R-value of less than 13. Single height coil sections shall have removable frame sections to facilitate vertical coil extraction.

- Blow-thru sections shall have a diffuser plate as an integral part of the fan section.

- Access Doors:

Access doors shall be one piece, hinged, lockable double-wall construction with foam insulation sealed between the inner and outer panels. Panel assemblies shall not carry an R-value of less than 13.

- Drain Pans:

Drain pans shall be foam insulated double-wall galvanized or stainless steel construction (18 gauge optional). The pan shall be sloped toward the drain connection. Drain pan shall have 11/2-in. MPT connection exiting through the hand side or opposite side of the casing as specified. One drain outlet shall be supplied for each cooling coil section. Drain pan shall allow no standing water and comply with ASHRAE (American Society of Heating, Refrigeration and Air-Conditioning Engineers). Standard 62.1-2010. Where 2 or more coils are stacked in a coil bank, intermediate drain pans shall be provided and the condensate shall be piped to the bottom drain pan. The bottom coil shall not serve as a drain path for the upper coil.

- FANS

- General:

- Forward-curved fan sections shall have one double-width double-inlet (DWDI) fan wheel and scroll. They shall be constructed of galvanized steel with baked enamel. They shall be designed for continuous operation at the maximum rated fan speed and motor horsepower. Fans shall have an AMCA class rating corresponding to the static pressure at which the fan is designed to operate (Class I or II). Completed fan assembly shall be dynamically balanced in accordance with AHRI Guideline G and ANSI S2.19 at design operating speed using contract drive and motor if ordered.

- Airfoil fan sections shall have one DWDI airfoil fan wheel and scroll. Airfoil blades shall be double thickness design constructed of heavy gage, high strength steel or aluminum continuously welded to the backplate and the spun inlet flange. Entire fan assembly shall be cleaned, primed and painted with alkyd enamel, except for an aluminum fan wheel when supplied. Fans shall have an AMCA class rating corresponding to the static pressure at which the fan is designed to operate (Class I or II). Completed fan assembly shall be dynamically balanced to minimum grade of G 6.3 per ANSI/AMCA 204 at design operating speed using contract drive and motor if ordered.

- Belt drive plenum fan sections shall have one single-width single-inlet (SWSI) airfoil fan wheel. Airfoil blades shall be double thickness design constructed of heavy gage, high strength steel or aluminum continuously welded to the backplate and the spun inlet flange. Entire fan assembly shall be cleaned, primed and painted with alkyd enamel, except for an aluminum fan wheel when supplied. They shall be designed for continuous operation at the maximum rated fan speed and motor horsepower. Fans shall have an AMCA class rating corresponding to the static pressure at which the fan is designed to operate (Class I or II). Completed fan assembly shall be dynamically balanced to minimum grade of G 6.3 per ANSI/AMCA 204 at design operating speed using contract drive and motor if ordered.

- Direct drive plenum fan sections:

- with a NEMA “T” frame motor shall have the option of one, two, four, or six single width single inlet (SWSI) airfoil fan wheel(s). Airfoil blades shall be double thickness design continuously welded to the back plate and the front plate. Fan wheel shall be constructed of aluminum. Airfoil blades shall be aluminum extrusions and shall be top welded to the back plate and front plate of the wheel. Fan wheel shall be dynamically balanced per ISO standard 1940 quality grade G6.3.

- with an EC motor shall have the option of single or multiple SWSI backward curved fans. Fan wheel shall be constructed of aluminum. Blades shall be welded to both front and back plates of the wheel. Fan assembly shall be dynamically balanced per ISO standard 1940 quality grade 6.3.

- Isolated fan assembly vibration shall not exceed 0.248 in. per second when mounted on active isolators. Vibration shall be measured in both vertical and horizontal directions at the specified fan operating speed using specified motor. For testing purposes, accelerometers shall be mounted on the motor near the bearing locations an removed before shipment.

- All fan sled components shall provide corrosion protection to pass 100-hour salt spray test per ASTM B-117.

- Fan wheels for all AF, FC, belt drive PF, and direct drive PF with NEMA “T” frame motors shall be keyed to the shaft. Fan wheels for direct drive PF with EC motors shall be mounted directly to the rotor of the EC motor. All shall be designed for continuous operation at maximum rated fan speed and motor horsepower. Fan wheels and shafts shall be selected with a maximum operating speed 25% below the first critical.

- Belt drive fan motor shall be mounted within the fan section casing on slide rails equipped with adjusting screws. Belt drive and direct drive with NEMA “T” frame motors shall be premium efficiency, open drip-proof or totally enclosed fan cooled NEMA (National Electrical Manufacturers Association) Design A or B with size and electrical characteristics as shown on the equipment schedule. Motor shall be mounted on a horizontal flat surface and shall not be supported by the fan or its structural members. All three-phase motors shall have a ± 10% voltage utilization range and a 1.15 minimum service factor. Motor shall be compliant with the Energy Independence and Security Act (EISA) of 2007 where applicable. Single-phase motors shall be available up to and including 5 hp.

- Direct drive with EC motors shall exceed the minimum efficiency requirements of the ErP Directive for Fans, efficiency class IE4, and specify motor protection according to EN 60529. Motors shall also provide the following: locked rotor protection, phase failure detection, soft start, mains under-voltage detection, over-temperature protection of electronics/motor, and short circuit protection.

- Performance Ratings:

Supply fan performance shall be rated and certified in accordance with AHRI Standard 430, latest edition.

- Sound Ratings:

Manufacturer shall submit first through eighth octave sound power for fan discharge and casing radiated sound. Sound ratings shall be tested in accordance with AHRI 260.

- Mounting:

- AF, FC, Belt-drive PF, Direct-drive PF with NEMA motor: Fan scroll, wheel, shaft, bearings, drives, and motor shall be mounted on a common base assembly. The base assembly is isolated from the outer casing with factory-installed isolators and rubber vibration absorbent fan discharge seal. A canvas style duct connection between fan discharge and cabinet is not acceptable. Units shall use 2-in. deflection spring isolators.

- Direct drive PF with EC motor: Fan wheel, inlet plate, inlet ring, and motor and motor supports shall be a common assembly. The assembly is mounted directly to panels on an internal bulkhead wall.

- Fan Accessories:

- Forward-curved fans:

- Variable frequency drives with or without bypass.

- Magnetic motor starters.

- Motor disconnects.

- Airflow measuring piezo ring.

- Piezo ring transducer.

- Motor shaft grounding ring.

- Belt guards.

- Inlet screen.

- Airfoil Fans:

- Variable frequency drives with or without bypass.

- Magnetic motor starters.

- Motor disconnects.

- Airflow measuring piezo ring.

- Piezo ring transducer.

- Motor shaft grounding ring.

- Belt guards.

- Inlet screen.

- Belt Drive Plenum Fans with NEMA “T” frame motors:

- Variable frequency drives with or without bypass.

- Magnetic motor starters.

- Motor disconnects.

- Airflow measuring piezo ring.

- Piezo ring transducer.

- Motor shaft grounding ring.

- Inlet screen and wheel cage.

- Direct Drive Plenum Fans with NEMA “T” frame motors:

- Variable frequency drives.

- Motor protection box for motor current protection with a single VFD driving multiple motors.

- Airflow measuring piezo ring.

- Piezo ring transducer.

- Motor shaft grounding ring.

- Inlet guard.

- Blank off plate.

- Backdraft dampers.

Optional backdraft damper blades shall be 6063-T5 extruded aluminum channel with galvanized steel braces and extruded vinyl blade seals. Blades shall be mechanically fastened to axle rod rods rotating in corrosion-resistant, synthetic bearings. Blades open at 0.12 in. wg and are fully open at 0.2 in. wg.

- Flexible Connection:

The base assembly is isolated from the outer casing with factory-installed isolators and rubber vibration absorbent fan discharge seal. A canvas style duct connection between fan discharge and cabinet is not acceptable.

- Direct Drive Plenum Fans and EC Motors

- Corrosion protection

- Inlet guard

- Blankoff plate

- Backdraft dampers

- Control options

- 0-10 VDC

- 4-20 mA

- Modbus

- BACnet

- BEARINGS AND DRIVES

- Bearings:

Self-aligning, grease lubricated, anti-friction with lubrication fittings extended to drive side of fan section. Optional grease fittings extended to the exterior of the casing are available. All bearing life calculations shall be done in accordance with ABMA 9 for ball bearings and ABMA 11 for roller bearings.

- Size 03 to 110 forward-curved fans: Cartridge type bearings for Class I fans. Heavy-duty pillow block type, self-aligning, regreasable ball or roller type bearings selected for a minimum average life (L50) of 200,000 hours or optionally for an (L50) of 500,000 hours.

- Size 03 to 110 airfoil fans: Heavy-duty pillow block type, self-aligning, regreasable ball or roller type bearings selected for a minimum average life (L50) of 200,000 hours or optionally for an (L50) of 500,000 hours.

- Size 06 to 110 belt-drive plenum fans: Heavy-duty pillow block type, self-aligning, regreasable roller type bearings selected for a minimum average life (L50) of 200,000 hours or optionally for an (L50) of 500,000 hours.

- Shafts:

Fan shafts shall be solid steel, turned, ground, polished and coated with a rust inhibitor.

- V-Belt Drive:

Drive shall be designed for a minimum 1.2 service factor as standard with a 1.5 service factor option and/or a factory-supplied extra set of belts. Drives shall be fixed pitch with optional variable pitch for motors 15 hp and less. All drives shall be factory mounted, with sheaves aligned and belts properly tensioned.

- COILS

- All water, steam and direct expansion (DX) refrigerant coils shall be provided to meet the scheduled performance. All coil performance shall be certified in accordance with AHRI Standard 410. All water and direct expansion coils shall be tested at 450 psig air pressure. Direct expansion coils shall be designed and tested in accordance with ANSI/ASHRAE 15 Safety Code for Mechanical Refrigeration (latest edition). Factory-supplied 1/2-in. OD coils shall be covered under the standard product one-year limited warranty. All steam coils, integral face and bypass coils and 5/8-in. OD coils shall be warranted for a period not in excess of 12 months from their shipment from the manufacturer. Coil epoxy coating shall be covered under a 5-year limited warranty from the date of shipment from the manufacturer.

- General Fabrication:

- All water and refrigerant coils shall have minimum 1/2-in. OD copper tubes mechanically expanded into fins to ensure high thermal performance with lower total flow and pumping requirements. Minimum tube wall thickness shall be 0.016 inches. Optional tube wall thickness of 0.025 in. shall be supplied, if specified.

- Optionally, water coils shall have minimum 5/8-in. OD copper tubes mechanically expanded into fins to ensure high thermal performance with lower total flow and pumping requirements. Minimum tube wall thickness shall be 0.020 inches. Optional tube wall thickness of 0.035 in. shall be supplied, if specified.

- Aluminum plate fin type with belled collars. Optional copper plate fins shall be supplied, if specified. Fin type shall be sine wave construction.

- Aluminum-finned coils shall be supplied with die-formed casing and tube sheets of mill galvanized steel or stainless steel as specified. Copper-finned coils shall be supplied with stainless steel casing and tube sheets.

- Hydronic Heating and Cooling Coils:

- Headers shall be constructed of steel with steel MPT connections. Headers shall have drain and vent connections accessible from the exterior of the unit. Optional non-ferrous headers and red brass MPT connections shall be supplied if specified.

- Configuration: Coils shall be drainable, with non-trapping circuits. Coils will be suitable for a design working pressure of 300 psig at 200°F.

- Steam Distribution (Non-Freeze Type) Heating Coils:

- Headers shall be steel with MPT connections.

- Inner steam distributing tubes shall be 5/8-in. OD, 0.020 in. wall thickness, located within 1 in. OD, 0.030 in. wall outer condensing tubes. Working pressure shall be 175 psig at 400°F.

- Integral Face and Bypass Coils:

- Sizes 03-14 shall have horizontal steam or hot water coils with a tubewall thickness of not less than 0.020 inches. Tubes shall be mechanically expanded into die formed collars formed in aluminum plate type fins.

- Sizes 17-110 shall have vertical steam or hot water coils with a tubewall thickness of not less than 0.035 inches. Fins shall be spiral edge-wound copper. Tubes shall be free-floating for thermal expansion and contraction without the use of offset bends or floating headers.

- Refrigerant Coils:

- Headers shall be constructed of copper with brazed joints.

- Brass refrigerant distributors and seamless copper distribution tubes shall be factory supplied to ensure uniform flow.

- Thermal expansion valves (TXV) and nozzles shall be factory installed and piped to the exterior of the casing. Equalizer lines shall be piped internal to the coil header.

- Suction and liquid line pairs shall be located next to each other for easy circuit identification. A custom label showing TXV size, nozzle size and condensing unit circuit pairing shall be located on the side of the coil section.

- Standard circuiting selections include:

- Single distributor arrangement for sizes 03-17.

- Row split intertwined multiple distributor arrangement for sizes 03-110.

- Face split multiple distributor arrangement for sizes 03-110.

- Submittals must include a DX coil and condensing unit cross plot to show that the coil and condensing unit capacity match at the rated design conditions.

- Electric Heating Section:

- The electric heater casing is constructed of galvanized steel. Heater control box access door shall be mounted on the designated hand side of the unit. Element construction as follows:

- Open-wire type, 80% nickel, 20% chromium resistance coils, insulated by Steatite bushings and supported in a galvanized steel frame. Bushings shall be recessed into embossed openings and stacked into supporting brackets, spaced no more than 4-in. centers. Thermal cutouts for overtemperature protection shall be provided to meet UL and NEC requirements. Maximum element heating density shall be 55 watts/sq inch.

- Contactor control - electric heaters up through 60 kW shall have 3 stages of control, beyond 60 kW shall have 6 stages of control.

- SCR control - electric heaters up through a maximum of 90 amps are available with full SCR control. The entire heater is modulated to achieve the proportional control based on a 0 to 10 volt DC or 4 to 20 mA control signal.

- Vernier control - the heater has full modulating control of the first circuit of heat, all of which is rated at equal kW increments. There is a minimum of 3 circuits for this type of control. These stage increments are turned on and off by a step controller. As each stage fulfills the demand for heat, the SCR increment is used as a fully modulating filler between stages. This end output is a fully proportional control of the electric heater based on a 0 to 10 volt DC or 4 to 20 mA control signal.

- Sheathed type, 80% nickel, 20% chromium resistance coils, suspended in a magnesium oxide insulator fill within a tubular steel sheath/brazed fin assembly. Silicone rubber end seals shall prevent contamination of the interior, and the exterior shall be protected from corrosion by a high temperature aluminum coating. Thermal cutouts for overtemperature protection shall be provided to meet UL and NEC requirements. Maximum element heating density shall be 55 watts/sq inch.

- Contactor control - electric heaters up through 60 kW shall have 3 stages of control, beyond 60 kW shall have 6 stages of control.

- The manufacturer shall furnish an integral control box containing thermal cutouts, primary control, subcircuit fusing, airflow switch, and fused control transformer.

- Electric heaters shall be UL listed for zero clearance and shall meet all applicable National Electric Code requirements.

- Units with electric heat sections shall be listed under UL 1995 Standard for Safety.

- GAS HEATING SECTION

- Indirect fired gas furnace section(s) shall have a minimum thermal efficiency of 80% and incorporate agency listed gas-fired duct furnace(s) per UL, CSA, or ETL for operation on natural or propane gas to the current edition of ANSI Z83.8 or Canadian CSA 2.6 Standard for Gas-Fired Duct Furnaces. Duct furnaces shall be installed on the positive pressure side of the supply fan only.

- The duct furnace module(s) shall have:

- 20 gage galvanized steel heat exchanger cabinet.

- 1 in. thick, minimum 11/2 lb per cu ft density thermal insulation for the heat exchanger cabinet.

- Each furnace shall have an induced-draft fan for the removal of flue gases and to keep the heat exchanger at a negative pressure.

- Air pressure switches to prove air supply for combustion before operation of gas valve.

- Patented inshot gas burners with integral carryovers.

- Direct-spark ignition of the gas burners with remote flame sensor to prove carryover across all burners.

- A listed 24-vac redundant combination gas valve including two electric shutoff valves, gas pressure regulator, and a manual shutoff valve per furnace.

- An automatic reset type high limit switch to limit maximum outlet air temperature to less than 250°F.

- Manual reset flame rollout switches.

- Minimum of one 40 va, 24 vac control transformer.

- 1/8-in. NPT tapped test gage connection in the gas manifold for measuring gas pressure.

- Union fitting downstream of gas control to facilitate installation and service.

- Provision for attachment of a vent system to exhaust flue gases to the outdoors.

- Gas-fired duct furnace(s) provided shall have an 18 gage tubular heat exchanger assembly suitable to withstand 3.0 in. wg total external static pressure without burner flame disturbance and constructed of either:

- Type 409 stainless steel (0.044 minimum wall thickness) produced to ASTM A268.

- Type 304L stainless tubes (0.047 minimum wall thickness) produced to ASTM A249.

- Gas heating section modules shall be listed for application downstream of refrigeration and cooling systems and shall provide means for removal of condensate that occurs in the tubes during cooling operation. Heat exchanger tubes shall have (integral formed dimpled restrictors; formed tubulators) to provide for an unobstructed drainage path and tubes shall be formed to provide a positive pitch to promote condensate drainage. Drainage shall be configured so that burners and burner surfaces are not exposed to condensate.

- Gas heating section shall incorporate a direct spark ignition control module listed by one of the following: US, CSA, or ETL.

- Controls shall provide:

- 100% safety shutoff.

- A 15-second minimum pre-purge period prior to trial for ignition.

- High-energy direct spark ignition of main burners.

- Electronic flame supervision incorporating a 0.8-second flame failure response time.

- Up to 2 additional ignition retrials preceded by an inter-purge period.

- A minimum 30-second post-purge.

- Automatic reset after one hour to initiate additional ignition trials if lockout occurs during heat call.

- An LED indicator light to provide a flash code to identify the operating condition of the control.

- Gas heating section shall be equipped for operation with 115 vac, single-phase, 60 Hz power supply.

- All electrical components shall be listed or recognized by UL, CSA, or ETL.

- Gas Furnace Control:

- Single furnace — Operates from 10 to 100% of input from a single analog input of 0 to 10 vdc.

- Two furnaces in series — Lead unit operates from 20 to 100% of input and secondary unit operates in two-stage operation to achieve overall system input of 10 to 100% from a single analog input of 0 to 10 vdc.

- Furnace rack systems — Multiple furnaces operate from a single analog input of 0 to 10 vdc with a lead modulating furnace and multiple secondary two-stage furnaces to achieve overall system input of 10 to 100%. (10:1 turndown minimum; most rack systems provide greater than 10:1 turndown.)

- Electronic modulation — Operates from 10 to 100% of input from a single analog input of 0 to 10 vdc. Heat enable contact (supplied by others) initiates and ends heating cycles. Heating unit incorporates two-speed operation of combustion air blower and two-stage gas valve, signal amplifier and timer relay control.

- Gas supply pressure to the gas valve inlet shall be 5.0 to 13.5 in. wg for natural gas or 11.0 to 13.5 in. wg for propane gas.

- Units are orificed for operation up to 2000 ft above sea level unless specified for high altitude operation.

- Duct furnaces shall be test-fired prior to shipment to verify proper ignition, operation and shutdown and satisfactory operation of all components.

- Furnaces shall be provided with printed installation and maintenance instructions, burner operating and maintenance instructions, piping and wiring diagrams and installation start-up data sheet.

- ENERGY RECOVERY WHEEL

- Construction:

- Wheel sections shall incorporate a rotary wheel in an insulated cassette frame complete with seals, drive motor and drive belt.

- The wheel shall be coated with silica gel desiccant, permanently bonded without the use of binders or adhesives.

- The substrate shall be made of a light weight polymer and shall not degrade nor require additional coatings for application in coastal environments.

- Coated wheel segments shall be washable with detergent or alkaline coil cleaner and water.

- The silica gel desiccant shall not dissolve nor deliquesce in the presence of water or high humidity.

- The wheel polymer layers shall be wound continuously with one flat and one structured layer in an ideal parallel plate geometry providing laminar flow and minimum pressure drop.

- The wheel shall incorporate the channel matrix design and an optional adjustable mechanical purge.

- The polymer layers shall be captured in a stainless steel wheel frame or aluminum and stainless steel segment frames that provide a rigid and self-supporting matrix.

- Energy recovery wheels greater than 25 inches in diameter shall be provided with removable wheel segments.

- Wheel frame shall be a welded hub, spoke and rim assembly of stainless, plated and/or coated steel and shall be self-supporting without the wheel segments in place.

- Wheel segments shall be removable without tools to facilitate maintenance and cleaning.

- Wheel bearings shall provide an L-10 life in excess of 400,000 hours.

- Wheel rim shall be continuous rolled stainless steel and the wheel shall be connected to the shaft by means of taper locks.

- All diameter and perimeter seals shall be provided as part of the cassette assembly and shall be factory set.

- Drive belts of stretch urethane shall be provided for wheel rim drive without the need for external tensioners or adjustment.

- The energy recovery section shall be a UL recognized component for electrical and fire safety. The wheel drive motor shall be UL recognized and mounted in the cassette frame and supplied with a service connector or junction box.

- Thermal performance shall be AHRI Standard 1060 certified and bear the AHRI Certified Product Seal. Cassettes shall be listed in the AHRI Certified Products Directory and bear the AHRI Certified Product Seal.

- Wheel shall carry a 5-year parts warranty. This warranty is for all wheel cassette components except the drive motor, which carries the motor manufacturer’s warranty.

- HUMIDIFIERS

- The humidifiers shall be of the direct discharge type, using steam from existing steam lines or boilers to be injected into the air plenums for humidification.

- Each humidifier shall consist of multiple, vertical steam discharge pipes, supported on horizontal header manifolds, spaced to provide the optimum of steam to air contact while minimizing pressure drop. Each humidifier shall be sized to nominally match the air plenum width and height for maximum contact of the discharging steam to the air passing around the vertical steam discharge pipes.

- The vertical steam discharge pipes shall be constructed of 316 stainless steel. Each pipe shall have a full-length, inverted slot on each side for steam discharge at 100% air to steam contact. Nozzles and holes have less than 15% air to steam contact and are, therefore, unacceptable.

- A full-length stainless steel fishbone shaped baffle shall be used inside the vertical discharge pipe to wick condensate away from the discharge slots and back to the center of the pipe for re-evaporation.

- The feeder manifolds shall be constructed of 316 stainless steel, sized to move the steam in a specific mass-flow speed range, for maximum condensate separation. Final condensate separation shall occur inside the feeder manifolds, after the control valve, with the dried steam then injected directly into the vertical discharge pipes.

- Insulated uprights provide a cushion of air that reduces both heat gain and condensate formation. Insulated models have nozzles inserted in the uprights to ensure that only dry steam is delivered into the air.

- The steam humidifier shall be designed with slip fittings for easy assembly. The steam humidifier shall be designed without plastic nozzles, collars, o-rings or gaskets for zero maintenance.

- FILTER SECTIONS

- Flat filter sections shall accept either 2-in. or 4-in. filters. Sections shall include side access slide rails. Optional 6-in. filter racks shall be capable of accepting 4-in. final filters. Optional 2 in. pre-filter shall be available.

- Angle filter sections shall accept either 2-in. or 4-in. filters of standard sizes, arranged in a horizontal V formation.

- Draw-thru bag/cartridge filter sections shall be capable of accepting headered standard size 6-in. to 12-in. deep rigid media or bag filters and a 2-in. pre-filter.

- Draw-thru bag/cartridge filter sections shall be capable of accepting headered standard size 12-in. to 30-in. deep rigid media or bag filters and a 2-in. pre-filter.

- Blow-thru bag/cartridge filter sections shall contain a face loading filter frame and be capable of accepting standard size 12-in. deep rigid media (headered or box) or bag filters.

- Blow-thru HEPA filter sections shall contain a face loading filter frame and be capable of accepting standard size 12-in. deep HEPA box filters.

- Differential Pressure Gages:

- Housing shall be constructed of a glass filled nylon case and acrylic lens. Exterior finish shall be coated black.

- Accuracy shall be ±5% of full scale throughout range at 70°F.

- Pressure limits shall be 30 psig continuous to either pressure connection.

- Temperature limits shall be 20 to 120°F.

- Diameter of dial face shall be 2.33 in.

- Process connections shall be barbed, 3/16-in. for ID tubing.

- DAMPERS

- Factory-supplied dampers shall be warranted to be free from defects in material and workmanship for a period of 12 months after being installed or placed in service, but in no instance shall the period of warranty be longer than 18 months from the date of the original shipment by the manufacturer.

- Mixing boxes, filter-mixing boxes, and exhaust boxes shall have parallel or opposed blades and interconnecting outside-air and return-air dampers. Bottom damper locations shall be optionally available with a tool screen to prevent most objects from falling through a bottom damper opening.

- Standard Dampers:

Damper blades shall be constructed of galvanized steel, with blade seals and stainless steel jamb seals. Blades shall be mechanically fastened to axle rods rotating in self-lubricating synthetic bearings. Maximum leakage rate shall be 4 cfm/ft2 at 1 in. wg differential pressure.

- Premium Dampers:

Damper blades shall be constructed of galvanized steel with a double-skin airfoil design, with blade seals and stainless steel jamb seals. Blades shall be mechanically fastened to axle rods rotating in self-lubricating synthetic bearings. Maximum leakage rate shall be 2 cfm/ft2 at 1 in. wg differential pressure.

- Outside Air Measurement Dampers:

- Damper frame shall be nominal 4 in. x 1 in. x minimum 0.081 in. and constructed of 6063-T5 extruded aluminum.

- Airflow measuring blades shall be airfoil-shaped, heavy gage anodized 6063-T5 extruded aluminum and fixed in 10 in. x minimum 16 gage galvanized steel frame.

- Jamb seals shall be flexible metal compression type along control damper sides.

- Blade seals shall be neoprene along control damper blade edges.

- Bearings shall be molded synthetic.

- Linkage shall be galvanized steel, concealed in frame.

- Axles shall be minimum 1/2-in. diameter plated steel, hex-shaped, mechanically attached to blade.

- Operating temperature shall be –22 to 140°F.

- Air straightener section shall be aluminum alloy honeycomb contained in 5 in. long, 16 gage galvanized steel sleeve attached to monitoring blade frame.

- Airflow range shall be 400 to 5,000 ft per minute face velocity.

- Maximum leakage rate shall be 2 cfm/ft2 at 1 in. wg differential pressure.

- Integral Face and Bypass Dampers:

- Integral face and bypass (IFB) coils shall be capable of maintaining a constant air volume, within 5%, shall be capable of maintaining a constant leaving air temperature as entering air conditions vary, and shall be capable of producing mixed leaving air temperatures within 3 ft downstream with a maximum variance in air temperature of 5°F, regardless of damper position.

- When no heating is required, dampers shall divert air to bypass around heating surface with minimal temperature override.

- Coil casing, dampers and baffles shall be fabricated from galvanized steel with an option for stainless steel. Coils shall be tested at 300 psig.

- Integral face and bypass coils shall be provided with a connection point for field-mounted actuator(s), electrical or pneumatic, or can be provided from the factory at an additional cost.

- Actuator connection point shall be mechanically attached to dampers via linkage mechanisms. Dampers shall be interconnected for operation simultaneously across each face of coil.

- Face and Bypass Dampers:

- Internal Face and Bypass Dampers:

Internal face and bypass dampers shall be factory mounted in galvanized steel frame. Damper blades shall be constructed of galvanized steel, with high temperature blade and edge seals. Blades shall be mechanically fastened to axle rods rotating in self-lubricating synthetic bearings. To eliminate blade warping, face dampers shall be sectionalized to limit blade length to 60 in. maximum. Face damper blades shall be opposed and arranged to match coil face with top bypass, and internal linkage.

- External Face and Bypass Dampers:

Face damper shall be factory mounted in galvanized steel frame. Damper blades shall be constructed of galvanized steel, with high temperature blade and edge seals. Blades shall be mechanically fastened to axle rods rotating in self-lubricating synthetic bearings. Bypass damper shall be constructed of galvanized steel, with blade seals and stainless steel jamb seals. Blades shall be mechanically fastened to axle rod rotating in self-lubricating synthetic bearings. Face damper blades shall be opposed with top bypass, and internally mounted linkage.

- Multi-Zone Dampers:

Multi-zone dampers shall be factory mounted in galvanized steel frame. Damper blades shall be constructed of galvanized steel with a double-skin airfoil design, with blade seals and stainless steel jamb seals. Blades shall be mechanically fastened to axle rods rotating in self-lubricating synthetic bearings. Maximum leakage rate shall be 11 cfm/ft2 at 1 in. wg differential pressure. Maximum pressure drop due to dampers shall be no more than 0.40 in. wg. Number of zones shall vary by size of section.

- AIR MIXING SECTION

- KEES Air Mixxer

Air mixer of 0.081-in. aluminum construction of size, performance and maximum pressure drop indicated. The air mixer shall mix two or more airstreams of differing temperature to within ±6°F of theoretical mixed-air temperature and provide a more uniform air velocity contour entering a downstream filter or coil bank.

- Blender Products Series IV Air Blender

Static mixing devices of a minimum 0.080 in. aluminum welded and mechanical fastened construction shall be installed where shown to enhance the mixing of outside air with return air to a desired mixing effectiveness and provide even airflow across filters, coils and control sensors. When combined with a typical mixing box the mixing section shall provide a Mixing Effectiveness of 65% with a minimum outdoor air percentage of 30%. Air mixer models shall be geometrically scaled to ensure proper performance across full range of applications. Mixers that are not geometrically scaled are not acceptable.

- UV-C GERMICIDAL LAMPS

- Emitters and fixtures for UV-C lamps shall be designed for use inside an HVAC system and shall be covered by a 1 year warranty. Individual lamp output shall be measured in an ASME nozzled test apparatus using a 45°F airstream moving at not less than 400 fpm. Lamp output at 253.7 nm shall not be less than 10 mW/cm2 per inch of arc length measured at a distance of one meter.

- Power supplies for UV-C lamps shall be a high-efficiency electronic type which are matched to the emitters and are capable of producing the specified output intensity with an input power no more than 80 watts.

- Fixtures for UV-C lamps shall be factory installed and wired to a SPDT disconnect switch and door interlock switches in each door. Fixtures are wired for 120 v/single ph requiring a minimum circuit ampacity of 15 amps. Lamps shall ship separately for field installation to minimize the chance for bulb damage.

- Emitters and fixtures shall be installed in sufficient quantity and arranged so as to provide an equal distribution of UV-C energy on the coil and drain pan.

- The minimum UV-C energy striking the leading edge of the coil pan shall be not less than 820 mW/cm2 at the closest point and through placement, not less than 60% of that value at the farthest point. Equal amounts are to strike the drain pan, either directly or indirectly through reflection.

- Emitters and fixtures shall be installed such that UV-C energy strikes all surfaces of the coil, drain pan, and the available line of sight airstream.

- ELECTRICAL ACCESSORIES:

- ECM Power Distribution Panel

- Power distribution panel shall be enclosed in a NEMA 4 electrical box and shall be included with every fan section which has an ECM fan array.

- A single line of sight disconnect for the entire fan array shall be located on the outside of the electrical box.

- Individual circuit breakers for each fan shall be mounted on the power distribution panel to isolate each fan for service. Fans shall be factory wired back to the power distribution panel.

- Control wiring from all fans in the array shall terminate at one point inside the power distribution panel to control the entire array. Control signal shall be wired as 0-10 volt and shall include a field installed resistor if 4-20 mA control is required.

- BACnet or Modbus shall be available as an option. When selected, all motors shall be factory addressed.

- Single Point Power:

The single point power (SPP) box shall have an externally mounted, complete unit line of site disconnect. Internally, the single point power box shall have individual circuit breakers for each circuit, allowing individual circuit protection and a means of disconnect while not completely disabling the unit. SPP box locations shall be offered as:

- Single Point Power Right Side Mount

- Single Point Power Left Side Mount

- Single point Power End Mount

- Single Point Power Enclosure:

- Enclosure supplied shall have appropriately sized circuit breakers, fusing, wiring, labeling and penetrations based on the unit configuration.

- Enclosure shall be equipped with a lockable door and a NEMA extended rotary handle mechanism on the enclosure door to provide a means for external disconnect operation to the main circuit breaker switch within the SPP enclosure.

- Enclosure to be SCE “Enviroline” NEMA 4 steel or equivalent.

- Enclosure to be suitable for both indoor and outdoor applications and shall operate within temperature limits of –20°F to +140°F.

- All SPP assemblies shall comply with UL 508 and be labeled as compliant.

- Wiring penetrations shall be pre-punched in the back of the enclosure and enter the inside of the air handling unit through strain reliefs. Enclosure shall be gasketed and sealed to the panel it is mounted to.

- A single 120 volt GFCI outlet shall be mounted on the enclosure when at least one marine light, convenience outlet, UV-C section or controls section is selected.

- Internal components (i.e., Fuse blocks, circuit breakers) shall be labeled with the appropriate circuit identification.

- Enclosure assemblies supplied with fuses shall have a label affixed that provides replacement fuse identification.

- All enclosures shall have the following labels adhered to the inside of the enclosure door: UL 508 labeling, amperage and voltage rating, maximum overcurrent protection rating.

- Transformer:

- Single phase resin filled.

- Low voltage transformer to be Square D or equivalent.

- NEMA 3R enclosure rating.

- Stepdown shall be one of the following:

- 240/480 volt primary to 120/240 volt secondary 60 Hz

- 600 volt primary to 120/240 volt secondary 60 Hz

- 190/200/208/220 or 380/400/416/440 volt primary to 110/220 volt secondary 50/60 Hz.

- Wiring and Harnesses:

- Wiring harnesses shall be specifically designed for the unit configuration. Generic wiring harnesses are not acceptable.

- Wire assemblies shall be thermoplastic heat resistant nylon coated (THHN) stranded copper (90°C) or AWM wire. All wires used shall be moisture resistant. Conductors shall be bundled and sleeved with heat-shrink material over connector end and sleeve. All colored electrical tape for wire marking shall be “3M Super 35 electrical tape”. For readability, laser print to be black on white background, smudge and wear resistant for life of wire assembly. The crimping of contactors to wires and the assembly of connectors to contactors shall follow manufacturer’s instructions.

- Wiring harnesses shall have polarized plugs that can only be assembled one way. Plugs shall have the ground lug identified by a green connector, while all of the powered lugs shall be black.

- If a shipping split is inserted in the unit configuration, a label shall instruct the assembler to connect the single point wiring harness before the two unit sections are mated. Each wiring harness shall extend at least 12 in. from each shipping split to allow the harnesses to be mated.

- Marine Lights and Convenience Outlets:

- Cast, non-ferrous metal, weatherproof, fixture.

- Cast, non-ferrous metal, weatherproof, electrical junction box.

- Gasketed, heat and shock resistant glass globe protects against moisture and debris.

- Cast, non-ferrous metal lamp guard to protect glass globe.

- UL and CSA listed.

- 100 watt type ‘A’ lamp maximum capacity.

- Each fixture is equipped with a 9.5 watt, 120 volt 800 lumen LED lamp with an average rated life of 25,000 hours, factory installed.

- Metallic, single gang, electrical junction box, UL listed.

- With convenience outlet: Factory supplied and wired, SPST, toggle switch and 15 amp, 120 vac/60 Hz, NEMA 5-15 type, ground fault circuit interrupt (GFCI) receptacle, UL listed.

- Without convenience outlet: Factory supplied and wired, SPST, UL listed toggle switch.

- Each fixture is factory wired to an externally mounted switch box. (Field power connections are made to the switch box mounted externally on the unit.)

- All factory wiring penetrating through the panel is protected in ‘RIGID’ type metal conduit.

- Disconnects:

Factory-supplied disconnects shall be covered under a 1 year limited warranty from the manufacturer from the date of shipment.

- 115-230 volt/single-phase non-fused disconnects shall have the following characteristics:

- Plated current carrying components for superior corrosion protection.

- Factory-installed equipment grounding terminals with slot/square drive screws.

- Rated for motor disconnect applications (10 Hp maximum).

- NEMA type 3R non-metallic enclosure.

- Up to 10,000 rms symmetrical amperes SCCR, when protected by a fuse or circuit breaker rated 60 amperes or less.

- Cover padlock hasp.

- Pull-out cartridge type.

- UL listed.

- 115-230 volt/single-phase fused disconnects shall have the following characteristics:

- Visible blades.

- Quick-make, quick-break operating mechanism.

- Cover padlock hasp and handle lock “OFF.”

- 240 vac maximum.

- Factory supplied and installed class ‘T Series’ fuses (fused disconnects only).

- Up to 10,000 rms symmetrical amperes SCCR, utilizing appropriately rated factory-supplied fuses.

- Horsepower rated for motor applications.

- Tangential combination knockouts for field wiring.

- Spring reinforced plated copper fuse clips.

- NEMA type 1 enclosures.

- Insulated, bondable solid neutral assemblies.

- UL listed, File E2875.

- Meet or exceed NEMA KS1-1990.

- 200-230 volt/3-phase fused and non-fused disconnects shall have the following characteristics:

- Visible blades.

- Quick-make, quick-break operating mechanism.

- Cover padlock hasp and handle lock “OFF.”

- 240 vac maximum.

- Factory supplied and installed class RK5 fuses (fused disconnects only).

- Up to 100,000 rms symmetrical amperes SCCR, utilizing appropriately rated, factory-supplied Class R fuses.

- Horsepower rated for motor applications.

- Tangential combination knockouts for field wiring.

- Spring reinforced plated copper fuse clips.

- NEMA type 1 enclosures.

- Insulated, bondable solid neutral assemblies.

- UL listed, File E2875.

- Meet or exceed NEMA KS1-1990.

- 380-575 volt/3-phase fused and non-fused disconnects shall have the following characteristics:

- Visible switch blades with for positive “OFF” indication.

- Quick-make, quick-break operating mechanism.

- Dual cover interlock.

- Color coded “ON” — “OFF” indicator handle.

- Cover padlock hasp and handle lock “OFF” provision for multiple padlocks.

- 600 vac maximum.

- Factory supplied and installed class RK5 fuses (fused disconnects only).

- Up to 200,000 rms symmetrical amperes SCCR, utilizing appropriately rated, factory-supplied Class R fuses.

- Horsepower rated for motor applications.

- Spring reinforced plated copper fuse clips.

- Tangential combination knockouts.

- NEMA type 1 enclosures.

- Insulated, bondable solid neutral assemblies.

- Wire terminations suitable for aluminum or copper conductors.

- UL listed.

- Meet or exceed NEMA KS1-1999.

- Starters:

Factory-supplied disconnects shall be covered under a 1 year limited warranty from the manufacturer from the date of shipment.

- Starter without disconnect:

- Adjustable motor overload with trip indication.

- Manual overload reset button (accessible without opening enclosure).

- 115-v fused secondary control transformer (fuse included — fused primary and secondary over 50 amps).

- Hand/Off/Auto selector switch (accessible without opening enclosure).

- Separate 4-position terminal strip for remote H-O-A wiring.

- C series contactors.

- Horsepower rated for motor applications.

- NEMA 4 or higher enclosures.

- Lug connections for field wiring.

- Factory mounted, wired, and run tested with factory-supplied motor.

- UL listed.

- Combination Starter/Disconnect:

- Non-fused UL 508 disconnect switch with lockable handle (locks not provided).

- Cover interlock.

- Adjustable motor overload with trip indication.

- Manual overload reset button (accessible without opening enclosure).

- 115-v fused secondary control transformer (fuse included — fused primary and secondary over 50 amps).

- Hand/Off/Auto selector switch (accessible without opening enclosure).

- Separate 4-position terminal strip for remote H-O-A wiring.

- C series contactors.

- Horsepower rated for motor applications.

- NEMA 4 or higher enclosures.

- Lug connections for field power wiring.

- Factory mounted, wired, and run tested with factory-supplied motor.

- UL listed.

- External Bypass for Variable Frequency Drives:

Factory-supplied bypasses shall be covered under a 1 year limited warranty from the manufacturer from the date of shipment.

- 200-230 v/3 Ph/60 Hz (1 to 7.5 Hp), 460-575 v/3 Ph/60 Hz (1 to 20 Hp), 380 v/3 Ph/50 Hz (1 to 15 Hp):

- 4-position panel-mounted disconnect style switch with lockable handle (locks not provided), meets OSHA 1910.

- Switch position indication (LINE/OFF/ DRIVE/TEST).

- Adjustable motor overload with trip indication (LINE position).

- Manual overload reset button.

- Horsepower rated for motor applications.

- Direct control (no contactors, relays, or holding coils).

- Complete isolation of inverter in LINE position.

- NEMA 12 type metal enclosures.

- Terminal strip provided for field power supply wiring.

- Lug connection for field ground wire.

- Gold flashed, auxiliary switch contact set (for switch position monitoring).

- Factory mounted, wired to VFD and motor, and run tested (motor and VFD must be factory supplied and installed).

- UL; UL, Canada; CE listed.

- 200-230 v/3 Ph/60 Hz (10 to 75 Hp), 460-575 v/3 Ph/60 Hz (25 to 150 Hp), 380 v/3 Ph/50 Hz (20 to 75 Hp):

- 4-position panel-mounted disconnect style switch with lockable handle (locks not provided), meets OSHA 1910.

- Switch position indication (LINE/OFF/ DRIVE/TEST).

- Adjustable motor overload with trip indication (in LINE position).

- Manual overload reset button.

- Horsepower rated for motor applications.

- 115-v control transformer with fused secondary (fused primary on units over 50 amps).

- Contactor for Line Start/Stop.

- Door-mounted Line Start and Line Stop pushbuttons.

- Complete isolation of inverter in LINE position.

- NEMA 12 type metal enclosures.

- Terminal strip provided for field power supply wiring.

- Lug connection for field ground wire.

- Gold flashed, auxiliary switch contact set (for switch position monitoring).

- Factory mounted, wired to VFD and motor, and run tested (motor and VFD must be factory supplied and installed).

- UL; UL, Canada; CE listed.

- Variable Frequency Drives:

- Referenced Standards and Guidelines:

- Institute of Electrical and Electronic Engineers (IEEE)

- IEEE 519-1992, Guide for Harmonic Content and Control.

- Underwriters Laboratories (as appropriate)

- UL508

- UL508A

- UL508C

- National Electrical Manufacturer’s Association (NEMA)

- ICS 7.0, AC Adjustable Speed Drives

- International Electrotechnical Commission (IEC)

- EN/IEC 61800-3

- National Electric Code (NEC)

- NEC 430.120, Adjustable-Speed Drive Systems

- International Building Code (IBC)

- IBC 2006, 2009, 2012, and 2015 Seismic – referencing ASC 7-05 and ICC AC-156

- Qualifications:

- VFDs and options shall be UL508 listed as a complete assembly. The base VFD shall be UL listed for 100 kA SCCR without the need for external input fuses.

- CE Mark – The base VFD shall conform to the European Union Electromagnetic Compatibility directive, a requirement for CE marking. The VFD shall meet product standard EN 61800-3 for the First Environment restricted level (Category C2). Base drives that only meet the Second Environment (Category C3, C4) shall be supplied with filters to bring the drive in compliance with the First Environment levels.

- The entire VFD assembly, including the bypass (if specified), shall be seismically certified and labeled as such in accordance with the 2006, 2009, 2012, and 2015 International Building Code (IBC):

- VFD manufacturer shall provide Seismic Certification and Installation requirements at time of submittal.

- Seismic importance factor of 1.5 rating is required, and shall be based upon actual shake test data as defined by ICC AC-156.

- Seismic ratings based upon calculations alone are not acceptable. Certification of Seismic rating must be based on testing done in all three axis of motion.

- Special seismic certification of equipment and components shall be provided by OSHPD preapproval.

- Factory-mounted variable frequency drives (VFDs) shall be wired to factory-supplied motors.

- Factory-supplied VFDs are programmed and started up from the factory and qualify the VFD, through ABB, for a 36-month warranty from date of commissioning or 40 months from date of sale, whichever occurs first.

- The VFD parameters are programmed into the controller and removable keypad. In the event that the VFD fails and needs replacement, the program can then be uploaded to the replacement VFD via the original keypad.

- The VFD package as specified herein and defined on the VFD schedule shall be enclosed in a UL Type enclosure (enclosures with only NEMA ratings are not acceptable), completely assembled and tested by the manufacturer in a facility where the management system governing the manufacture of this product is ISO 9001:2015 certified.

- The VFD shall provide full rated output from a line of ±10% of nominal voltage. The VFD shall continue to operate without faulting from a line of +30% to –35% of nominal voltage.

- VFDs shall be capable of continuous full load operation under the following environmental operating conditions:

- –15 to 40°C (5 to 104°F) ambient temperature. Operation to 50°C shall be allowed with a 10% reduction from VFD full load current.

- Altitude 0 to 3300 feet above sea level. Operation to 6600 ft shall be allowed with a 10% reduction from VFD full load current.

- Humidity less than 95%, non-condensing.

- All VFDs shall have the following standard features:

- All circuit boards shall be coated to protect against corrosion.

- All VFDs shall have the same customer interface, including digital display, and keypad, regardless of horsepower rating. The keypad shall be removable, capable of remote mounting and allow for uploading and downloading of parameter settings as an aid for start-up of multiple VFDs.

- The keypad shall include Hand-Off-Auto selections and manual speed control. The drive shall incorporate “bumpless transfer” of speed reference when switching between “Hand” and “Auto” modes. There shall be fault reset and “Help” buttons on the keypad. The Help button shall include “on-line” assistance for programming and troubleshooting.

- There shall be a built-in time clock in the VFD keypad. The clock shall have a battery backup with 10 years minimum life span. The clock shall be used to date and time stamp faults and record operating parameters at the time of fault. VFD programming shall be held in non-volatile memory and is not dependent on battery power.

- The VFDs shall utilize pre-programmed application macros specifically designed to facilitate start-up. The Application Macros shall provide one command to reprogram all parameters and customer interfaces for a particular application to reduce programming time. The VFD shall have two user macros to allow the end-user to create and save custom settings.

- The VFD shall be capable of starting into a coasting load (forward or reverse) up to full speed and accelerate or decelerate to set point without tripping or component damage (flying start).

- The VFD shall have the ability to automatically restart after an over-current, over-voltage, under-voltage, or loss of input signal protective trip. The number of restart attempts, trial time, and time between attempts shall be programmable.

- The overload rating of the drive shall be 110% of its normal duty current rating for 1 minute every 10 minutes, 130% overload for 2 seconds every minute. The minimum FLA rating shall meet or exceed the values in the NEC/UL table 430.250 for 4-pole motors.

- VFDs through 200 HP shall have internal swinging (non-linear) chokes providing impedance equivalent to 5% to reduce the harmonics to the power line. Swinging choke shall be required resulting in superior partial load harmonic reduction. Linear chokes are not acceptable. 5% impedance may be from dual (positive and negative DC bus) chokes, or 5% swinging AC line chokes. VFDs with only one DC choke shall add an AC line choke.

- The input current rating of the VFD shall not be greater than the output current rating. VFDs with higher input current ratings require the upstream wiring, protection devices, and source transformers to be oversized per NEC 430.122. Input and output current ratings must be shown on the VFD nameplate.

- The VFD shall include a coordinated AC transient surge protection system consisting of 4 MOVs (phase to phase and phase to ground), a capacitor clamp, 1600 PIV Diode Bridge and internal chokes. The MOV’s shall have a minimum 125 joule rating per phase across the diode bridge. VFDs that do not include coordinated AC transient surge protection shall include an external TVSS (Transient Voltage Surge Suppressor).

- The VFD shall provide a programmable loss-of-load (broken belt/broken coupling) Form-C relay output. The drive shall be programmable to signal the loss-of-load condition via a keypad warning, Form-C relay output, and/or over the serial communications bus. The loss-of-load condition sensing algorithm shall include a programmable time delay that will allow for motor acceleration from zero speed without signaling a false loss-of-load condition.

- The VFD shall include multiple “two zone” PID algorithms that allow the VFD to maintain PID control from two separate feedback signals (4 to 20mA, 0 to10V, and/or serial communications). The two zone control PID algorithm will control motor speed based on a minimum, maximum, or average of the two feedback signals. All of the VFD PID controllers shall include the ability for “two zone” control.

- If the input reference is lost, the VFD shall give the user the option of either (1) stopping and displaying a fault, (2) running at a programmable preset speed, (3) hold the VFD speed based on the last good reference received, or (4) cause a warning to be issued, as selected by the user. The drive shall be programmable to signal this condition via a keypad warning, Form-C relay output and/or over the serial communication bus.

- The VFD shall have programmable “Sleep” and “Wake up” functions to allow the drive to be started and stopped from the level of a process feedback signal.

- All VFDs to have the following adjustments:

- Three (3) programmable critical frequency lockout ranges to prevent the VFD from operating the load continuously at an unstable speed. The lockout range must be fully adjustable, from 0 to full speed.

- Two (2) PID Set point controllers shall be standard in the drive, allowing pressure or flow signals to be connected to the VFD, using the microprocessor in the VFD for the closed-loop control. The VFD shall have 250 mA of 24 VDC auxiliary power and be capable of loop powering a transmitter supplied by others. The PID set point shall be adjustable from the VFD keypad, analog inputs, or over the communications bus. There shall be two independent parameter sets for the PID controller and the capability to switch between the parameter sets via a digital input, serial communications or from the keypad. The independent parameter sets are typically used for night setback, switching between summer and winter set points, etc.

- There shall be an independent, second PID loop that can utilize the second analog input and modulate one of the analog outputs to maintain the set point of an independent process (i.e. valves, dampers, etc.). All set points, process variables, etc. to be accessible from the serial communication network.

- Two (2) programmable analog inputs shall accept current or voltage signals.

- Two (2) programmable analog outputs (0 to 20 mA or 4 to 20 mA). The outputs may be programmed to output proportional to Frequency, Motor Speed, Output Voltage, Output Current, Motor Torque, Motor Power (kW), DC Bus voltage, Active Reference, Active Feedback, and other data.

- Six (6) programmable digital inputs for maximum flexibility in interfacing with external devices. All digital inputs shall be programmable to initiate upon an application or removal of 24VDC.

- Three (3) programmable, digital Form-C relay outputs. The relay outputs shall include programmable on and off delay times and adjustable hysteresis. The relays shall be rated for maximum switching current 8 amps at 24 VDC and 0.4 A at 250 VAC; Maximum voltage 300 VDC and 250 VAC; continuous current rating of 2 amps RMS. Outputs shall be true Form-C type contacts; open collector outputs are not acceptable. Drives that have only two (2) relay outputs must provide an option card that provides additional relay outputs.

- Run permissive circuit - There shall be a run permissive circuit for damper or valve control. Regardless of the source of a run command (keypad, input contact closure, time-clock control, or serial communications), the VFD shall provide a dry contact closure that will signal the damper to open (VFD motor does not operate). When the damper is fully open, a normally open dry contact (end-switch) shall close. The closed end-switch is wired to a VFD digital input and allows VFD motor operation. Two separate safety interlock inputs shall be provided. When either safety is opened, the motor shall be commanded to coast to stop and the damper shall be commanded to close. The keypad shall display “start enable 1 (or 2) missing.” The safety input status shall also be transmitted over the serial communications bus.

- The VFD control shall include a programmable time delay for VFD start and a keypad indication that this time delay is active. A Form C relay output provides a contact closure to signal the VAV boxes open. This will allow VAV boxes to be driven open before the motor operates. The time delay shall be field programmable from 0 to 120 seconds. Start delay shall be active regardless of the start command source (keypad command, input contact closure, time-clock control, or serial communications), and when switching from drive to bypass.

- Seven (7) programmable preset speeds.

- Two independently adjustable accel and decel ramps with 1 to 1800 seconds adjustable time ramps.

- The VFD shall include a motor flux optimization circuit that will automatically reduce applied motor voltage to the motor to optimize energy consumption and reduce audible motor noise. The VFD shall have selectable software for optimization of motor noise, energy consumption, and motor speed control.

- The VFD shall include a carrier frequency control circuit that reduces the carrier frequency based on actual VFD temperature that allows higher carrier frequency settings without derating the VFD.

- The VFD shall include password protection against parameter changes.

- The keypad shall include a backlit LCD display. The display shall be in complete English words for programming and fault diagnostics (alpha-numeric codes are not acceptable). All VFD faults shall be displayed in English words. The keypad shall include a minimum of 14 assistants including:

- Start-up assistant

- Parameter assistants

- PID assistant

- Reference assistant

- I/O assistant

- Serial communications assistant

- Option module assistant

- Panel display assistant

- Low noise set-up assistant

- Maintenance assistant

- Troubleshooting assistant

- Drive optimizer assistants

- All applicable operating values shall be capable of being displayed in engineering (user) units. A minimum of three operating values from the list below shall be capable of being displayed at all times. The display shall be in complete English words (alpha-numeric codes are not acceptable):

- Output Frequency

- Motor Speed (RPM,%, or Engineering units)

- Motor Current

- Motor Torque

- Motor Power (kW)

- DC Bus Voltage

- Output Voltage

- The VFD shall include a fireman’s override input. Upon receipt of a contact closure from the fire / smoke control station, the VFD shall operate in one of two modes: 1) Operate at a programmed predetermined fixed speed ranging from -500Hz (reverse) to 500Hz (forward). 2) Operate in a specific fireman’s override PID algorithm that automatically adjusts motor speed based on override set point and feedback. The mode shall override all other inputs (analog/digital, serial communication, and all keypad commands), except customer defined safety run interlocks, and force the motor to run in one of the two modes above. “Override Mode” shall be displayed on the keypad. Upon removal of the override signal, the VFD shall resume normal operation, without the need to cycle the normal digital input run command.

- Serial Communications

- The VFD shall have an EIA-485 port as standard. The standard protocols shall be Modbus, Johnson Controls N2, Siemens Building Technologies FLN, and BACnet. [Optional protocols for LonWorks, Profibus, EtherNet, BACnet IP, and DeviceNet shall be available.] Each individual drive shall have the protocol in the base VFD. The use of third party gateways and multiplexers is not acceptable. All protocols shall be “certified” by the governing authority (i.e. BTL Listing for BACnet). Use of non-certified protocols is not allowed.

- The BACnet connection shall be an EIA-485, MS/TP interface operating at 9.6, 19.2, 38.4, or 76.8 Kbps. The connection shall be tested by the BACnet Testing Labs (BTL) and be BTL Listed. The BACnet interface shall conform to the BACnet standard device type of an Applications Specific Controller (B-ASC). The interface shall support all BIBBs defined by the BACnet standard profile for a B-ASC including, but not limited to:

- Data Sharing – Read Property – B.

- Data Sharing – Write Property – B.

- Device Management – Dynamic Device Binding (Who-Is; I-Am).

- Device Management – Dynamic Object Binding (Who-Has; I-Have).

- Device Management – Communication Control – B.

- Serial communication capabilities shall include, but not be limited to; run-stop controls, speed set adjustment, and lock and unlock the keypad. The drive shall have the capability of allowing the BAS to monitor feedback such as process variable feedback, output speed / frequency, current (in amps), % torque, power (kW), kilowatt hours (resettable), operating hours (resettable), and drive temperature. The BAS shall also be capable of monitoring the VFD relay output status, digital input status, and all analog input and analog output values. All diagnostic warning and fault information shall be transmitted over the serial communications bus. Remote VFD fault reset shall be possible.

- Serial communication in bypass (if bypass is specified) shall include, but not be limited to; bypass run-stop control, the ability to force the unit to bypass, and the ability to lock and unlock the keypad. The bypass shall have the capability of allowing the BAS to monitor feedback such as, current (in amps), kilowatt hours (resettable), operating hours (resettable), and bypass logic board temperature. The BAS shall also be capable of monitoring the bypass relay output status, and all digital input status. All bypass diagnostic warning and fault information shall be transmitted over the serial communications bus. Remote bypass fault reset shall be possible.

- The VFD / bypass shall allow the BAS to control the drive and bypass digital and analog outputs via the serial interface. This control shall be independent of any VFD function. The analog outputs may be used for modulating chilled water valves or cooling tower bypass valves. The drive and bypass’ digital (Form-C relay) outputs may be used to actuate a damper, open a valve or control any other device that requires a maintained contact for operation. In addition, all of the drive and bypass’ digital inputs shall be capable of being monitored by the BAS system. This allows for remote monitoring of which (of up to 4) safeties are open.

- The VFD shall include an independent PID loop for customer use. The independent PID loop may be used for cooling tower bypass value control, chilled water value / hot water valve control, etc. Both the VFD PID control loop and the independent PID control loop shall continue functioning even if the serial communications connection is lost. As default, the VFD shall keep the last good set point command and last good DO and AO commands in memory in the event the serial communications connection is lost and continue controlling the process.

- EMI/RFI filters. All VFDs shall include EMI/RFI filters. The onboard filters shall allow the VFD assembly to be CE Marked and the VFD shall meet product standard EN 61800-3 for the First Environment restricted level (Category C2) with up to 100 feet of motor cable. Second environment (Category C3, C4) is not acceptable. No Exceptions. Certified test reports shall be provided with submittals confirming compliance to EN 61800-3, First Environment (C2).

- Drive options shall be furnished and mounted by the drive manufacturer as defined on the VFD schedule. All optional features shall be UL Listed by the drive manufacturer as a complete assembly and carry a UL508 label.

- Eclipse Bypass (Optional) – Bypasses shall be furnished and mounted by the drive manufacturer as defined on the VFD schedule. All VFD with bypass configurations shall be UL Listed by the drive manufacturer as a complete assembly and carry a UL508 label.

- A complete factory wired and tested bypass system consisting of a door interlocked, padlockable circuit breaker, output contactor, bypass contactor, and fast acting VFD input fuses. UL Listed motor overload protection shall be provided in both drive and bypass modes.

- The bypass enclosure door and VFD enclosure must be mechanically interlocked such that the disconnecting device must be in the “Off” position before either enclosure may be accessed.

- The VFD and bypass package shall have a UL listed short circuit current rating (SCCR) of 100,000 Amps and this rating shall be indicated on the UL data label.

- The drive and bypass package shall be seismic certified and labeled to the 2006, 2009, 2012 and 2015 IBC:

- Seismic importance factor of 1.5 rating is required, and shall be based upon actual shake table test data as defined by ICC AC-156.

- Special seismic certification of equipment and components shall be provided by OSHPD preapproval.

- Drive Isolation Fuses - To ensure maximum availability of bypass operation, fast acting fuses, exclusive to the VFD, shall be provided to allow the VFD to disconnect from the line prior to clearing upstream branch circuit protection. This maintains bypass operation capability in the event of a VFD failure. Bypass designs which have no such fuses, or that incorporate fuses common to both the VFD and the bypass, will not be accepted. Third contactor “isolation contactors” are not an acceptable alternative to fuses, as contactors could weld closed and are not an NEC recognized disconnecting device.

- The bypass shall maintain positive contactor control through the voltage tolerance window of nominal voltage +30%, –35%. This feature is designed to avoid contactor coil failure during brown out/low line conditions and allow for input single phase operation when in the VFD mode. Designs that will not allow input single phase operation in the VFD mode are not acceptable.

- Motor protection from single phase power conditions - the bypass system must be able to detect a single phase input power condition while running in bypass, disengage the motor in a controlled fashion, and give a single phase input power indication. Bypass systems not incorporating single phase protection in bypass mode are not acceptable.

- The bypass system shall be designed for stand-alone operation and shall be completely functional in both Hand and Automatic modes even if the VFD has been removed from the system for repair/ replacement. Serial communications shall remain functional even with the VFD removed. Bypass systems that do not maintain full functionality with the drive removed are not acceptable.

- Serial communications – the bypass shall be capable of being monitored and/or controlled via serial communications. On-board communications protocols shall include ModBus RTU; Johnson Controls N2; Siemens Building Technologies FLN (P1); and BACnet MS/TP.

- Serial communication capabilities shall include, but not be limited to: bypass run-stop control, the ability to force the unit to bypass, and the ability to lock and unlock the keypad. The bypass shall have the capability of allowing the BAS to monitor feedback such as, current (Amps), kilowatt hours (resettable), operating hours (resettable), and bypass logic board temperature. The BAS shall also be capable of monitoring the bypass relay output status, and all digital input status. All bypass diagnostic warning and fault information shall be transmitted over the serial communications bus. Remote bypass fault reset shall be possible. The following additional status indications and settings shall be transmitted over the serial communications bus and/or via a Form-C relay output – keypad “Hand” or “Auto” selected, bypass selected, and broken belt indication. The BAS system shall also be able to monitor if the motor is running in the VFD mode or bypass mode over serial communications. A minimum of 50 field serial communications points shall be capable of being monitored in the bypass mode.

- The bypass serial communications shall allow control of the drive/bypass (system) digital outputs via the serial interface. This control shall be independent of any bypass function or operating state. The system digital (relay) outputs may be used to actuate a damper, open a valve or control any other device that requires a maintained contact for operation. All system analog and digital I/O shall be capable of being monitored by the BAS system.

- There shall be an adjustable motor current sensing circuit for the bypass and VFD modes to provide proof of flow (broken belt) indication. The condition shall be indicated on the keypad display, transmitted over the BAS and/or via a Form-C relay output contact closure. The broken belt indication shall be programmable to be a system (drive and bypass) indication. The broken belt condition sensing algorithm shall be programmable to cause a warning or system shutdown.

- The digital inputs for the system shall accept 24VDC. The bypass shall incorporate an internally sourced power supply and not require an external control power source. The bypass power board shall supply 250 mA of 24 VDC for use by others to power external devices.

- There shall be a coordinated run permissive circuit for damper or valve control. Regardless of the source of a run command (keypad command, time-clock control, digital input, or serial communications) the bypass shall provide a dry contact closure that will signal the damper to open before the motor can run. When the damper is fully open, a normally open dry contact (end-switch) shall close. The closed end-switch is wired to a bypass system input and allows motor operation. Up to four separate safety interlock inputs shall be provided. When any safety is opened, the motor shall be commanded to coast to stop, and the damper shall be commanded to close. This feature will also operate in Fireman’s override/smoke control mode.

- The bypass control shall monitor the status of the VFD and bypass contactors and indicate when there is a welded contactor contact or open contactor coil. This failed contactor condition shall be indicated on the bypass LCD display, programmed to activate a Form-C relay output, and/or over the serial communications protocol.

- The bypass control shall include a programmable time delay bypass start including keypad indication of the time delay. A Form C relay output commands the VAV boxes open. This will allow VAV boxes to be driven open before the motor operates at full speed in the bypass mode. The time delay shall be field programmable from 0 to 120 seconds.

- There shall be a keypad adjustment to select manual or automatic transfer to bypass. The user shall be able to select via keypad programming which drive faults will result in an automatic transfer to bypass mode and which faults require a manual transfer to bypass. The user may select whether the system shall automatically transfer from drive to bypass mode on the following drive fault conditions:

- Over current

- Over voltage

- Under voltage

- Loss of analog input

- The following operators shall be provided:

- Bypass Hand-Off-Auto

- Drive mode selector

- Bypass mode selector

- Bypass fault reset

- The bypass shall include the ability to select the operating mode of the system (VFD/Bypass) from either the bypass keypad or digital input.

- The bypass shall include a two line, 20 character LCD display. The display shall allow the user to access and view:

- Energy savings – in US dollars

- Bypass motor amps

- Bypass input voltage-average and individual phase voltage

- Bypass power (kW)

- Bypass faults and fault logs

- Bypass warnings

- Bypass operating time (resettable)

- Bypass energy (kilowatt hours – resettable)

- I/O status

- Parameter settings/programming

- Printed circuit board temperature

- The following indicating lights (LED type) or keypad display indications shall be provided. A test mode or push to test feature shall be provided.

- Power-on (Ready)

- Run enable

- Drive mode selected

- Bypass mode selected

- Drive running

- Bypass running

- Drive fault

- Bypass fault

- Bypass H-O-A mode

- Automatic transfer to bypass selected

- Safety open

- Damper opening

- Damper end-switch made

- The Bypass controller shall have six programmable digital inputs, and five programmable Form-C relay outputs. This I/O allows for a total System (VFD and Bypass) I/O count of 24 points as standard. The bypass I/O shall be available to the BAS system even with the VFD removed.

- The on-board Form-C relay outputs in the bypass shall programmable for any of the following indications.

- System started

- System running

- Bypass override enabled

- Drive fault

- Bypass fault

- Bypass H-O-A position

- Motor proof-of-flow (broken belt)

- Overload

- Bypass selected

- Bypass run

- System started (damper opening)

- Bypass alarm

- Over temperature

- The bypass shall provide a separate terminal strip for connection of freeze, fire, smoke contacts, and external start command. All external safety interlocks shall remain fully functional whether the system is in VFD or Bypass mode. The remote start/stop contact shall operate in VFD and bypass modes. The terminal strip shall allow for independent connection of up to four (4) unique safety inputs.

- The bypass shall include a supervisory control mode. In this bypass mode, the bypass shall monitor the value of the VFDs analog input (feedback). This feedback value is used to control the bypass contactor on and off state. The supervisory mode shall allow the user to maintain hysteresis control over applications such as cooling towers and booster pumps.

- The user shall be able to select the text to be displayed on the keypad when an external safety opens. Example text display indica-tions include “FireStat,” “FreezStat,” “Over pressure” and “Low suction.” The user shall also be able to determine which of the four (4) safety contacts is open over the serial communications connection.

- Smoke Control Override Mode (Override 1) – The bypass shall include a dedicated digital input that will transfer the motor from VFD mode to Bypass mode upon receipt of a dry contact closure from the Fire/Smoke Control System. The Smoke Control Override Mode action is not programmable and will always function as described in the bypass User’s Manual documentation. In this mode, the system will ignore low priority safeties and acknowledge high priority safeties. All keypad control, serial communications control, and normal customer start/stop control inputs will be disregarded. This Smoke Control Mode shall be designed to meet the intent of UL864/UUKL.

- Fireman’s Override Mode (Override 2) – the bypass shall include a second, programmable override input which will allow the user to configure the unit to acknowledge some digital inputs, all digital inputs, ignore digital inputs or any combination of the above. This programmability allows the user to program the bypass unit to react in whatever manner the local Authority Having Jurisdiction (AHJ) requires. The Override 2 action may be programmed for “Run-to-Destruction.” The user may also force the unit into Override 2 via the serial communications link.

- VFD with Integral Disconnect:

- UL listed by the drive manufacturer as a complete assembly.

- UL 508 labeled.

- Capable of being locked by three padlocks.

Air Mixxer is a registered trademark of KEES Incorporated.

Air Bender is a registered trademark of Blender Products, Inc.

Modbus is a registered trademark of Schneider Electric.

BACnet is a trademark of ASHRAE.

LonWorks is a registered trademark of Echelon Corporation.