Commercial Air-Cooled Condensers 
50/60 Hz

HVAC Guide Specifications

Size Range: 20 to 60 Nominal Tons

(70 to 211 Nominal kW)

Carrier Model Number: 	09RCM, 09RCS

- General

- SYSTEM DESCRIPTION

Outdoor-mounted, air-cooled condenser on the ground or rooftop installation. The 09RCS unit shall have one refrigeration circuit and

the 09RCM unit shall have two independent refrigeration circuits capable of field conversion to single circuit. Unit shall have air-cooled coils, aeroacoustic condenser fans, a control box, and shall discharge condenser air vertically upward as shown on certified drawings. Unit shall be used in refrigeration circuit with 30MPA or 30HXA air-cooled condenserless chillers.

- QUALITY ASSURANCE

- Unit construction shall comply with latest edition of ASHRAE 15 Safety Code, UL 60335-2-40, and ASME applicable codes (U.S.A. codes).

- Unit shall be manufactured in a facility registered to ISO 9001: 2015 Manufacturing Quality Standard.

- Base unit shall be constructed in accordance with UL standards and CSA.

- Painted parts shall withstand 1000 hours in constant neutral salt spray under ASTM B117 conditions with a 1mm scribe per ASTM D1654. After test, painted parts shall show no signs of wrinkling or crackling, no loss of adhesion, no evidence of blistering, and the main creepage shall not exceed 1/4 in. (rating ³ 4 per ASTM D1654) on either side of the scribe line.

- Design pressure shall be 650 psig (4482 kPa).

- Unit shall be functional checked at the factory.

- Unit shall be rated using refrigerants R-32, R-454B, R-515B, R-513A, R-1234ze, R-410A, and R-134a.

- DELIVERY, STORAGE, AND HANDLING

Unit shall be shipped as single package and shall be stored and handled per unit manufacturer's recommendations.

- WARRANTY (FOR INCLUSION BY SPECIFYING ENGINEER)

- Products

- EQUIPMENT

- General:

Factory assembled, single-piece, air-cooled remote condenser. Contained within the unit enclosure shall be all factory wiring, piping, controls, nitrogen holding charge, and special features required prior to field start-up.

- Unit Cabinet:

- Cabinet shall be galvanized steel casing with a baked enamel powder or pre-painted finish.

- Painted parts shall withstand 1000 hours in constant neutral salt spray under ASTM B117 conditions with a 1 mm scribe per ASTM D1654. After test, painted parts shall show no signs of wrinkling or crackling, no loss of adhesion, no evidence of blistering, and the main creepage shall not exceed 1/4-in. (rating ³ 4 per ASTM D1654) on either side of the scribe line.

- Control box access panels shall be removable for service access.

- Lifting holes shall be provided to facilitate rigging.

- Fans:

- Condenser fans shall be direct-drive aeroacoustic, discharging air vertically upward.

- All condenser fan motors shall be totally enclosed 3-phase type with permanently lubricated ball bearings, class F insulation, and internal, automatic-reset thermal overload protection.

- Shafts shall have inherent corrosion resistance.

- Fan blades shall be statically and dynamically balanced.

- Condenser Coils:

- Coil shall be air-cooled microchannel heat exchanger (MCHX) and shall have a series of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds. Microchannel coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for the fins, tubes and manifolds in combination with a corrosion-resistant coating on the tubes.

- Tubes shall be cleaned, dehydrated, and sealed.

- Assembled condenser coils shall be leak tested and pressure tested at 650 psig (4482 kPa).

- Refrigeration Components:

Refrigeration circuit components shall include liquid line temperature relief device and nitrogen holding charge.

- Controls and Safeties:

Unit controls shall include:

- Unit shall have a temperature fusible plug for safety on each refrigerant circuit.

- Self-contained low voltage control circuit.

- Cycle condenser fans to maintain proper head pressure control.

- Operating Characteristics:

- Unit shall be capable of rejecting the required heat at the required cfm and be capable of operating down to moderate ambient temperatures with standard factory supplied fan cycling.

- Head pressure fan cycling control utilizes pressure switches for all units.

- Electrical Requirements:

- A dual power supply of the correct voltage shall be required for each series unit. A 3-phase power circuit voltage and a 24 volt single-phase control circuit shall be required.

- The number of control circuits shall depend on the unit application, whether it is matched with one unit or two units.

- Power supplies for all units shall enter the control box through factory-punched entrance holes in the control box shelf.

- Terminal blocks shall be supplied for field wiring connections.

- Units shall utilize electromechanical fan cycling head pressure controls to control proper head pressure.

- Special Features:

- Optional Condenser Coil Materials:

- E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum micro-channel coils shall be capable of withstanding 10,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) B-117 Standard.

- Aluminum fin/copper tube coils:

Coil shall be constructed of seamless copper tubes mechanically bonded to aluminum fins. Fins shall have wavy enhancements. These condenser coils are recommended with remote cooler applications. These coils are not recommended for corrosive environments.

- E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum microchannel coils shall be capable of withstanding 10,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) B-117 Standard.

- Non-Fused Disconnect:

Units shall be factory-installed with non-fused disconnect capability for power and control located at the unit.

- High Short Circuit Current Rating (SCCR):

The optional high SCCR interrupt capability shall allow the unit to tolerate a 65 kA (208/230v, 380v and 460-v units) or 25 kA (575-v units) short circuit current for a brief period of time while protecting downstream components. The high SCCR option shall provide a higher level of protection than the standard unit (option for 60 Hz only). High interrupt shall be available as factory-installed option on all units.

- Full Hail Guard:

Unit shall be equipped with factory-installed louvered panels on the sides and ends of the unit which firmly fasten to the condenser frame. These panels shall cover the unit from top to bottom. The full hail guard also provides the functionality of a wind baffle.

- Vibration Isolation Pads:

Neoprene vibration isolation pads (24 in. x 3 in. x 1/4 in.) shall be available for field installation to reduce vibration transmission from the compressor through the floor and into the conditioned space.

- Low Ambient Head Pressure Control:

Unit shall be provided with factory or field-installed low ambient head pressure control to permit operation to –20°F (–29°C) outdoor ambient temperature when field-installed wind baffles or factory-installed hail guards are provided.

- Variable Speed Condenser Fans:

All fans on the unit shall have factory installed variable speed fan motors to provide higher part load efficiency and reduced acoustic levels. Each fan circuit shall have a factory-installed, independent variable speed drive. Variable speed drives are rated IP-55 enclosures and UL Listed. The use of this option or accessory, with the addition of wind baffles or hail guards and antifreeze in the evaporator circuit, shall allow Carrier chillers to run with outdoor ambient temperatures down to –20°F (–28.9°C).

- Wind Baffles:

Wind baffles shall be field installed to facilitate operation down to –20°F (–29°C) when used in conjunction with high-efficiency variable condenser fans.

- Export Packaging:

Unit shall be provided with a skid underneath the condenser as well as a bag covering the complete package.