Indoor Self-Contained Air-Cooled Unit
Constant Volume Application

HVAC Guide Specifications

Size Range: 5 to 20 Tons

Carrier Model Number: 50XCA

- General

- SYSTEM DESCRIPTION

- Indoor packaged vertical air-cooled cooling unit using hermetic scroll compressors and built-in condenser fan for cooling duty. Unit shall discharge supply air vertically or horizontally and condenser air horizontally as shown on contract drawings.

- QUALITY ASSURANCE

- Units shall be rated in accordance with AHRI (Air-Conditioning, Heating, and Refrigeration Unit) Standard 340/360, latest edition, as appropriate.

- Unit shall be designed to conform to ANSI/ASHRAE (American National Standards Institute/American Society of Heating, Refrigerating, and Air-Conditioning Engineers) 15, latest revision safety code, and UL (Underwriters Laboratories) Standard 1995, and shall be UL listed under both American and Canadian Standards.

- The management system governing the manufacture of this product is ISO 9001:2015 certified.

- Insulation, adhesive, and liner system shall meet NFPA (National Fire Protection Association) 90A requirements for flame spread and smoke generation.

- DELIVERY, STORAGE, AND HANDLING

- Units shall be stored and handled according to manufacturer’s recommendations.

- Products

- EQUIPMENT

- General:
Factory-assembled, single-piece, air-cooled cooling unit. Unit shall consist of scroll refrigerant compressor(s), indoor fan section with belt drive centrifugal fans and motor, evaporator coil section with direct expansion coil and drain pan, air-cooled condenser fan section with belt drive centrifugal fans and motor, factory wiring, piping and controls, and a system charge of refrigerant (R-410A). Unit may be used with or without return ductwork.

- Unit Cabinet:

- Cabinet shall be constructed of minimum 18 gauge zinc surface alloyed steel with a baked enamel finish. Unit shall be capable of withstanding ASTM (American Society for Testing and Materials) B117 500-hour salt spray test.

- Cabinet shall be fully insulated.

- Configurations include vertical or horizontal discharge with a ducted or louvered return.

- Unit drain pan shall have positive double slope to the drain to prevent standing water in pan.

- Panels for servicing shall be easily removable.

- Evaporator Fan Section:

- Fans shall be double inlet, centrifugal wheel with forward curved blades designed for continuous operation. Fan wheel shall be constructed of steel with corrosion resistant finish, and statically and dynamically balanced.

- Motor shall be 3-phase high-efficiency NEMA (National Electrical Manufacturers Association) frame ODP (open drip proof) of the same voltage as the compressor(s). Motor shall have permanently lubricated ball bearings.

- Compressor:
Hermetic scroll compressors shall be internally protected with high pressure relief. Compressors shall be factory mounted with vibration isolators. Compressors shall be two-stage (size 06-08) or single circuit tandem (size 12-24) for two-stage cooling operation.

- Coils:

- Evaporator and condenser coils shall have aluminum plate fins mechanically bonded to seamless copper tubes with all joints brazed. Tube sheet openings shall be swaged to prevent tube wear. Coils shall be full face.

- Direct expansion coil shall be designed and tested in accordance with ANSI/ASHRAE 15, latest revision safety code.

- Coil and drain pan shall be accessible through service access panels for cleaning.

- Filter:
Filter frame shall be installed upstream of the cooling coil, designed to take a 1 in. or 2 in. thick cleanable or disposable type commercially available filter. Filters shall be accessible from either side of the unit and filter rack shall be usable with ducted or free return. Disposable filters will be supplied with the unit. Four-in. filter racks are available.

- Condenser:

- Fans shall be double inlet, centrifugal wheel with forward curved blades designed for continuous operation. Fan wheel and scroll shall be constructed of steel with corrosion resistant finish, and statically and dynamically balanced.

- Fan shall be belt drive with an adjustable pitch motor pulley and fixed pitch fan pulley, with permanently lubricated, ball-bearing type bearings.

- Motor shall be 3-phase high-efficiency NEMA frame ODP (open drip proof) of the same voltage as the compressor(s). Motor shall have permanently lubricated ball bearings.

- Operating Characteristics:

- Unit shall be capable of providing a constant volume of conditioned air at a specified static pressure within the unit’s normal operating range. Unit shall have dual-stage cooling capacity control on all unit sizes. All units have a single, common refrigeration circuit. Unit shall be capable of starting and operating at up to 115°F outdoor ambient. Sizes 06 and 08 have a single compressor, with two stages. Sizes 12-24 have two compressors in tandem.

- Units shall be able to operate down to 0°F when equipped with low ambient option.

- Controls and Safeties:

- Units shall be furnished with a control terminal block for connection of low voltage controls and thermostats.

- Unit shall require a room-mounted thermostat mounted in the conditioned space. Thermostat shall be digital type. Thermostat shall control fan operation and be capable of turning unit on and off.

- Units shall have the following factory-installed safeties:

- High and low-pressure switches.

- Motor and compressor overtemperature.

- Current lockout.

- Inherent automatic fan motor overload.

- Electrical Requirements:

Units shall have a short circuit current rating (SCCR) of no less than 5 kA. All electrical power wiring shall enter the unit cabinet at a single location. Control circuit is 24-v, suitable for a field-supplied 24-v thermostat.

- Refrigerant Components:

Refrigerant circuit components include thermal expansion valves, distributor with nozzle, filter driers, and charging service valves on each circuit. Suction line shall have a refrigerant loop to prevent refrigerant drain back to the compressor. Suction piping shall be insulated with closed cell piping insulation.

- Special Features:

- Evaporator and Condenser Coil Coating:
The coating shall be continuous and cover the whole fin surface, tubing, manifolds, and feeder lines if applicable. For evaporator coils with thermostatic expansion valve assemblies, valve body, head, and bulb shall be masked. A minimum of 2 in. shall be masked on all coil connection points. Expansion valve inlet piping less than 6 in. in total length, expansion valve distributor, and external equalizer line are not required to be coated.

- Airside Economizer:

A field-installed airside economizer shall have a low leak damper assembly with Honeywell W7220 economizer controller for fault detection and diagnostics (FDD).

- Winter Start Option:

Shall provide a bypass of low-pressure switch on start-up for initial 90 seconds.

- SAV™ (Two-Speed Fan):

Fan speed shall operate at 67% of full speed for first stage cooling operation and 100% of full speed for second stage cooling operation or heating operation.

- High-Static Motor Upgrade:

- May be required for higher external static pressure (ESP) needed for factory or field-installed accessories (dampers, heating coils, etc.) to achieve the required performance.

- Units shall be designed with a fixed pulley on the blower and an adjustable sheave on the motor. The sheave turns open or the components themselves may need to be changed to provide the desired performance.

- Non-Fused Disconnect:

Shall be located by the unit control panel to disconnect all unit power. The lockable switch shall be accessible without opening any control panels.