Indoor Self-Contained Water-Cooled Unit
Constant Volume Application

HVAC Guide Specifications

Size Range: 5 to 20 Tons

Carrier Model Number: 50XCW

- General

- SYSTEM DESCRIPTION

Indoor packaged vertical water-cooled cooling unit using hermetic scroll compressors and brazed plate heat exchange. Unit shall discharge supply air vertically or horizontally (units 10 tons and above).

- QUALITY ASSURANCE

- Units shall be rated in accordance with AHRI (Air-Conditioning, Heating, and Refrigeration Institute) Standard 340/360, latest edition.

- Unit shall be designed to conform to ANSI/ASHRAE (American National Standards Institute/American Society of Heating Refrigerating, and Air-Conditioning Engineers) 15, latest revision safety code, and UL Standard 1995, and shall be UL listed under both American and Canadian Standards.

- The management system governing the manufacture of this product is ISO 9001:2015 certified.

- Insulation, adhesive, and liner system shall meet NFPA (National Fire Protection Association) 90A requirements for flame spread and smoke generation.

- DELIVERY, STORAGE, AND HANDLING

Units shall be stored and handled according to manufacturer’s recommendations.

- Products

- EQUIPMENT

- General:

Factory-assembled, single-piece, water-cooled cooling unit. Unit shall consist of scroll refrigerant compressor(s), indoor fan section with belt drive centrifugal fans and motor, evaporator coil section with direct expansion coil and drain pan, brazed plate condenser, factory wiring, piping and controls, and a system charge of refrigerant (R-410A). Unit may be used with or without return ductwork.

- Unit Cabinet:

- Cabinet shall be constructed of minimum 18 gauge zinc surface alloyed steel with a baked enamel finish. Unit shall be capable of withstanding ASTM (American Society for Testing and Materials) B117 500-hour salt spray test.

- Cabinet shall be fully insulated.

- Configurations include vertical or horizontal discharge with a ducted or louvered return.

- Unit drain pan shall have positive double slope to the drain to prevent standing water in pan.

- Panels for servicing shall be easily removable.

- Evaporator Fan Section:

- Fans shall be double inlet, centrifugal wheel with forward curved blades designed for continuous operation. Fan wheel shall be constructed of steel with corrosion resistant finish, and statically and dynamically balanced.

- Fan shall be belt drive with an adjustable pitch motor pulley and fixed pitch fan pulley, with permanently lubricated ball-bearing type bearings.

- Motor shall be 3-phase high-efficiency NEMA (National Electrical Manufactures Association) frame ODP (open drip proof), of the same voltage as the compressor(s). Motor shall have permanently lubricated ball bearings.

- Units with Staged Air Volume (SAV™) shall be equipped with a variable frequency drive to operate at 67% of full speed for first stage cooling and 100% of full speed for second stage cooling.

- Compressor:

Hermetic scroll compressors shall be internally protected with high pressure relief. Compressors shall be factory-mounted with vibration isolators. Compressors shall be two-stage (size 06-08) or single circuit tandem (size 12-24) for two-stage cooling operation.

- Coils:

- Evaporator coil shall have aluminum plate fins mechanically bonded to seamless copper tubes with all joints brazed. Tube sheet openings shall be swaged to prevent tube wear. Coils shall be full face for all sizes.

- Direct expansion coil shall be designed and tested in accordance with ANSI/ASHRAE 15, latest revision safety code.

- Coil and drain pan shall be accessible through service access panels for cleaning.

- Filter:

Filter frame shall be installed upstream of the cooling coil, designed to take a 1 in. or 2 in. thick cleanable or disposable type commercially available filter. Filters shall be accessible from either side of the unit and filter rack shall be usable with ducted or free return. Disposable filters will be supplied with the unit. 4 in. filter racks are available.

- Condenser:

Condenser shall be single pass, water-cooled, ANSI type 316, stainless steel brazed plate construction and shall provide positive subcooling of liquid refrigerant. Condenser shall have a maximum working water side pressure of 400 psig. An independent condenser shall be provided for each refrigerant circuit.

- Operating Characteristics:

Unit shall be capable of providing a constant volume of conditioned air at a specified static pressure within the unit’s normal operating range. Unit shall have dual-stage cooling capacity control on all units sizes. Sizes 6 and 8 have a single compressor, with two speed capability; sizes 12 thru 24 shall have two compressors in tandem on a single circuit.

- Controls and Safeties:

- Units shall be furnished with a control terminal block for connection of low voltage controls and thermostats.

- Unit shall require a room-mounted thermostat mounted in the conditioned space. Thermostat shall be digital type.

- Thermostat shall control fan operation and be capable of turning unit on and off.

- Units shall have the following factory-installed safeties: high and low-pressure switches, motor and compressor overtemperature, current lockout, and inherent automatic fan motor overload.

- Electrical Requirements:

Units shall have a short circuit current rating (SCCR) of no less than 5 kA. All electrical power wiring shall enter the unit cabinet at a single location. Control circuit is 24-v, suitable for a field-supplied 24-v thermostat.

- Refrigerant Components:

Refrigerant circuit components include thermal expansion valves, distributor with nozzle, filter driers, and charging service valves on each circuit. Suction line shall have a refrigerant loop to prevent refrigerant drain back to the compressor. Suction piping shall be insulated with closed cell piping insulation.

- Special Features:

- Heating Coil:

Field-installed hot water coil shall be two rows with copper tube aluminum fins and a powder coated steel casing. Fins shall be bonded to tubes by mechanical expansion. Coil to be leak tested at 400 psig air pressure submerged in water and charged with dry air.

- Thermostats:

A complete line of thermostats shall be available to meet any application control requirements.

- Steam Coil:

Field-installed steam heating coil shall be of a steam distributing tube type. Aluminum fin coil to be mounted external to the unit.

- Evaporator Coil Coating:

The coating shall be continuous and cover the whole fin surface, tubing, manifolds, and feeder lines if applicable. For evaporator coils with thermostatic expansion valve assemblies, valve body, head, and bulb shall be masked. A minimum of 2 in. shall be masked on all coil connection points. Expansion valve inlet piping if less than 6 in. in total length, expansion valve distributor, and external equalizer line are not required to be coated.

- Waterside Economizer:

Waterside economizer is available as a factory-installed option. Valve and controls are to be factory-installed.

- Head Pressure Control:

Pressure activated water regulating valve shall slow water flow to allow mechanical cooling during low entering water temperature conditions.

- SAV™ (Two-Speed Fan):

Fan speed shall operate at 67% of full speed for first stage cooling operation and 100% of full speed for second stage cooling operation or heating operation.

- Non-Fused Disconnect:

Shall be located by the unit control panel to disconnect all unit power. The lockable switch shall be accessible without opening any control panels.