
Split System Heat Pump Indoor Unit 
(Air-Handling Unit) with Puron® Refrigerant

HVAC Guide Specifications — Section 15859

Size Range: 2,400 to 8,000 Cfm, Nominal Airflow

6 to 20 Tons, Nominal Cooling

Carrier Model Numbers: 40RUQ*07-25

· General

· System Description

· Indoor, packaged air-handling unit for use in commercial heat pump split systems. Unit shall have a multi-position design and shall be capable of horizontal or vertical installation on a floor or in a ceiling, with or without ductwork. (Only vertical units are to be applied without ductwork.) Unit shall function as the indoor component of an air-to-air electric heat pump system. 

· Unit must be designed with a Puron® (R-410A) refrigerant circuit with a matching air-cooled condensing unit 38AUQ, for matched systems approved by the manufacturer.

· Quality Assurance

· All coils shall be designed and tested in accordance with ASHRAE 15 Safety Code for Mechanical Refrigeration, latest edition.

· Unit shall be constructed in accordance with ETL and ETL, Canada, standards and shall carry the ETL and ETL, Canada, labels.

· Unit insulation and adhesive shall comply with NFPA-90A requirements for flame spread and smoke generation. Insulation shall be treated with an immobilized antimicrobial agent to inhibit the growth of bacteria and fungi on the insulation as proven by tests in accordance with ASTM standards G21 and 22 (U.S.A.).

· Unit shall be manufactured in a facility registered to the ISO 9001 manufacturing quality standard.

· Direct-expansion coils shall be leak tested at 150 psig and pressure tested at 650 psig and qualified to UL burst test at 1980 psig.

· Delivery and Storage

· Units shall be stored and handled per manufacturer’s recommendation.

· Products

· Equipment

· Base Unit:

1. Cabinet shall be constructed of mill-galvanized steel.

2. Cabinet panels shall be fully insulated with 1/2 in. fire-retardant material. Insulation shall be treated with an immobilized antimicrobial agent to inhibit the growth of bacteria and fungi on the insulation as proven by tests in accordance with ASTM standards G21 and 22 (U.S.A.).

3. Unit shall contain corrosion-free condensate drain pans for both vertical and horizontal applications. Drain pans shall have connections on right and left sides of unit to facilitate field connection. Drain pans shall have the ability to be sloped toward the right or left side of the unit to prevent standing water from accumulating in pans.

4. Unit shall have factory-supplied 2 in. throw-away-type filters installed upstream from the cooling coil. Filter access shall be from either the right or left side of the unit.

· Coils:

1. Coils shall consist of 3 rows (40RUQ*07) or 4 rows (40RUQ*08-25) of copper tubes with sine-wave aluminum fins bonded to the tubes by mechanical expansion. Coil tubing shall be internally rifled to maximize heat transfer. Refrigerant line connections shall be made on the same side of the coil.

2. Coils shall feature factory-installed thermostatic expansion valves (TXVs) for refrigerant control. The TXVs shall be capable of external adjustment.

3. Coils shall have a factory-installed bypass line and check valve assembly around the TXVs to allow liquid flow from the coil to the outdoor unit during heating mode.

· Operating Characteristics:

1. When combined with the matching 38AUQ condensing unit the system shall be capable of starting and running up to 125°F (52°C) and down to 35°F (2°C) ambient outdoor temperature.

2. Unit shall operate at +/-10% from rated voltage.

· Motor:

1. Fan motor of the size and electrical characteristics specified on the equipment schedule shall be factory-supplied and factory-installed.

2. Indoor-fan motor shall have permanently lubricated, sealed bearings and inherent automatic-reset thermal overload protection (motors smaller than 5 hp) or manual reset calibrated circuit breakers (motors equal or larger than 5 hp). Indoor motors are designed specifically for Carrier and do not have conventional horsepower (hp) ratings listed on the motor nameplate. Motors are designed and qualified in the “air-over” location downstream of the cooling coil and carry a maximum continuous bhp rating that is the maximum application bhp rating for the motors; no “safety factors” above that rating may be applied.

3. All indoor fan motors 5 hp and larger shall meet the minimum efficiency requirements as established by the Energy Policy Act of 1992 (EPACT), effective October 24, 1997.

4. High efficient motors listed shall meet section 313 of the Energy Independence and Security Act of 2007 (EISA 2007).

· Special Features:

1. Alternate Motor and Drive:

An alternate motor and medium or high-static drive shall be available to meet the airflow and external static pressure requirements specified on the equipment schedule.

2. External Paint Cabinet:

Where conditions require, units shall be painted with an American Sterling Gray finish.

3. Hot Water Coil:

Coil shall be 2-row, U-bend coil with copper tubes and aluminum plate fins bonded to the tubes by mechanical expansion. Coil shall be mounted in a galvanized steel housing that shall be fastened to the unit’s fan deck for blow-thru heating operation. Coil shall have maximum working pressure of 150 psig.

4. Steam Distributing Coil:

Coil shall consist of one row of copper tubes with aluminum plate fins, and shall have inner steam distributing tubes. Coil shall be mounted in a galvanized steel housing and shall be fastened to the unit’s fan deck for blow-thru heating operation. Coil shall have maximum working pressure of 20 psig at 260°F.

5. Electric Heaters:

Heaters for nominal 240v, 480v, or 575v, 3-phase, 60 Hz power supply shall be factory-supplied for field installation as shown on the equipment drawings. Electric heat assembly shall be ETL and ETL, Canada; agency approved, and shall have single-point power wiring. Heater assembly shall include contactors with 24v coils, power wiring, 24v control wiring terminal blocks, and a hinged access panel.

6. Air Discharge Plenum:

Plenum shall be factory-supplied to provide free-blow air distribution for vertical floor-mounted units. A grille with moveable vanes for horizontal or vertical airflow adjustment shall be included. Plenum housing shall be field-installed on the unit’s fan deck for blow-thru air distribution.

7. Return Air Grille:

Grille shall be factory-supplied for field installation on the unit’s return air opening.

8. Unit Subbase:

Subbase assembly shall be factory-supplied for field installation. Subbase shall elevate floor-mounted vertical units to provide access for correct condensate drain connection.

9. Economizers:

a. Accessory Ultra Low Leak EconoMi$er X. (Field installed)

Economizer for ventilation or “free” cooling shall be factory provided for field installation on either return air opening of air handler.

1) Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.

2) Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

3) Shall include all hardware, actuator and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.

4) Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

5) Ultra LOW LEAK design meets California Title 24 section 140.4 and ASHRAE90.1 requirements for 4 cfm per sq. ft. on the outside air dampers and 10 cfm per sq. ft. on the return dampers.

6) Economizer controller on EconoMi$er X models shall be the Honeywell W7220 that provides:

a) 2-line LCD interface screen for setup, configuration and troubleshooting

b) On-board Fault Detection and Diagnostics (FDD) that senses and alerts when the economizer is not operating properly, per California Title 24

c) Sensor failure loss of communication identification

d) Automatic sensor detection

e) Capabilities for use with multiple-speed indoor fan systems

f) Utilizing digital sensors: 
Dry bulb and Enthalpy. Accessory comes standard with dry bulb sensing.

g) Field installing enthalpy sensor required.

b. Accessory Standard Leak EconoMi$er IV (Field-installed)

Economizer for ventilation or “free” cooling shall be factory provided for field installation on either return air opening of air handler.

1) Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.

2) Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

3) Shall include all hardware, actuator and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.

4) Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

5) Standard leak rate shall be equipped with dampers not to exceed 2% leakage at 1 in. wg pressure differential.

6) Economizer controller on EconoMi$er IV models shall be Honeywell W7212 that provides:

a) Combined minimum and DCV maxi-mum damper position potentiometers with compressor staging relay.

b) Functions with solid state analog enthalpy or dry bulb changeover control sensing.

c) Contains LED indicates for:
when free cooling is available, when module is in DCV mode, when exhaust fan is closed.

10. Overhead Suspension Package:

Package shall include necessary brackets to sup-port units in a horizontal ceiling installation.

11. CO2 Sensor:

Sensor shall provide the ability to signal the economizer to open when the space CO2 level exceeds the predetermined set point. Sensor shall have the capability of being connected to Comfort System relay pack or to economizer using field-sup-plied and field-installed Honeywell dc adapter no. Q769C1004.

12. Condensate Drain Trap:

Trap shall have transparent, serviceable design for easy cleaning. Kit shall also include overflow shutoff switch and wiring harness for connection to alarm if desired.

13. Staged Air Volume System (SAV) for 2-stage cooling models only:

a. Evaporator fan motor:

1) Shall have permanently lubricated bearings.

2) Shall have a maximum continuous bhp rating for continuous duty operation; no safety factors above that rating.

3) Shall be Variable Frequency duty and 2-speed control.

4) Shall contain motor shaft grounding ring to prevent electrical bearing fluting damage by safely diverting harmful shaft voltages and bearing currents to ground.

14. Variable Frequency Drive (VFD). Only available on 2-speed indoor fan motor option Staged Air Volume System (SAV™):

a. Shall be installed inside the unit cabinet, mounted, wired and tested.

b. Shall contain Electromagnetic Interference (EMI) frequency protection.

c. Insulated Gate Bi-Polar Transistors (IGBT) used to produce the output pulse width modulated (PWM) waveform, allowing for quiet motor operation.

d. Self diagnostics with fault and power code LED indicator. Field accessory Display kit available for further diagnostics and special setup applications.

e. RS485 capability standard

f. Electronic thermal overload protection

g. 5% swinging chokes for harmonic reduction and improved power factor.

h. All printed circuit boards shall be conformal coated.

15. Display Kit for Variable Frequency Drive:

a. Kit allows the ability to access the VFD con-troller programs to provide special setup capabilities and diagnostics.

b. Kit contains display module and communications cable.

c. Display Kit can be permanently installed in the unit or used on any SAV system VFD controller as needed.

1


1

