## G38MBRC-02SB
Outdoor Unit Single Zone Heat Pump Ductless System
38MBRC Submittal Selection
Job Data: |  |  | Location: |  |  |  | Carrier #:
Tag #: | [6 empty] | Date:
[5 empty] | Outdoor Model # | Size |  | STANDARD FEATURES • Variable Speed (Inverter) • Factory installed Base Pan Heater • Factory installed Crankcase Heater • Low Voltage Controls • Auto-Restart function • Condenser High Temp Protection • Quiet operation • Anti-corrosive fin coating LIMITED WARRANTY* • 10 year limited to original purchaser on compressor and parts upon timely registration, otherwise 5 years *For residential applications. See warranty for full details.
[5 empty] | 38MBRCQ36AA3 | 36K
[5 empty] | 38MBRCQ48AA3 | 48K
[5 empty] | 38MBRCQ58AA3 | 58K
Combination Selection
[5 empty] | Outdoor Unit | 58K
[5 empty] | Indoor Category | ALL
NOTE: Images for illustration purposes only. Actual models may be slightly different.
Specifications
Outdoor - Heat Pump
System | Outdoor Size |  | 36K | 48K | 58K
Electrical | Voltage, Phase, Cycle | V/Ph/Hz | 208/230-1-60 | 208/230-1-60 | 208/230-1-60
| MCA | A. | 30 | 39 | 42
| Recommended Fuse Size | A. | 35 | 40 | 45
| MOCP - Fuse Rating | A. | 45 | 50 | 60
| Short Circuit Current Rating (SCCR) | kA | 2.4 | 2.4 | 2.4
Operating Range | Cooling Outdoor DB Min - Max | °F(°C) | 5~122(-15~50) | 5~122(-15~50) | 5~122(-15~50)
| Heating Outdoor DB Min - Max | °F(°C) | -13~75(-25~24) | -13~75(-25~24) | -13~75(-25~24)
Piping | Total Piping Length | ft (m) | 213 (65) | 213 (65) | 213 (65)
| Piping Lift* | ft (m) | 98 (30) | 98 (30) | 98 (30)
| Pipe Connection Size - Liquid | in (mm) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52)
| Pipe Connection Size - Suction | in (mm) | 5/8 (16) | 5/8 (16) | 7/8 (22)
Refrigerant | Type |  | R410A | R410A | R410A
| Charge | lbs (kg) | 6.72 (3.05) | 9.26 (4.2) | 10.58 (4.8)
| Additional Refrigerant Charge (between Std & Max Piping Lengths) | Oz/ft (g/m) | 0.32 (30) | 0.32 (30) | 0.32 (30)
| Metering Device |  | EXV | EXV | EXV + Capillary
Outdoor Coil | Face Area | Sq. Ft. | 8.02 | 13.64 | 26.72
| No. Rows |  | 2 | 2 | 3
| Fins per inch |  | 18 | 18 | 18
| Circuits |  | 4 | 8 | 14
Compressor | Type |  | Rotary Inverter | Rotary Inverter | Rotary Inverter
| Model |  | ATF310D43UMT | ATQ420D1UMU | KTQ420D1UMU
| Oil Type |  | VG74 | VG74 | VG74
| Oil Charge | Fl. Oz. | 28.22 | 39.51 | 47.35
| Rated Current | RLA | 22 | 23.5 | 25
Airflow & Sound | Airflow | CFM | 2130 | 4500 | 4500
| Sound Pressure | dB(A) | 63 | 62.5 | 61.2
* Condensing unit above or below indoor unit
Performance
| Outdoor Size |  | 36K | 48K | 58K
Cassette | Indoor Model |  | 36K | 48K
| Energy Star |  | NO | NO
| NEEP |  | NO | NO
| MASSCEC |  | NO | NO
| CCHP |  | NO | NO
| ASHP |  | NO | NO
| ASHP COLD CLIMATE |  | NO | NO
| Cooling System Tons |  | 3 | 4
| Cooling Rated Capacity | Btu/h | 36000 | 48000
| Cooling Cap. Range Min - Max | Btu/h | 12,400~36,000 | 16,600~48,000
| SEER |  | 18.2 | 17.8
| EER |  | 9 | 9.5
| Heating Rated Capacity (47°F) | Btu/h | 38000 | 50000
| Heating Rated Capacity (17°F) | Btu/h | 23000 | 28000
| Heating Maximum Capacity (17°F) | Btu/h
| Heating Maximum Capacity (17°F) | Btu/h | 25300 | 37900
| Heating Maximum Capacity (5°F) | Btu/h | 22300 | 30200
| Heating Cap. Range Min - Max | Btu/h | 11,200~38,000 | 11,850~52,000
| HSPF |  | 10.6 | 11.5
| COP (47°F) | W/W | 3.01 | 3.1
| COP (17°F) | W/W | 1.9 | 1.8
| COP (5°F) | W/W | 2.02 | 1.92
Copyright 2024 CAC/BDP ● Atlanta, GA. 30339 | [8 empty] | Catalog No.: G38MBRC-03SB
SUBJECT TO CHANGE WITHOUT NOTICE | [8 empty] | Replaces: G38MBRC-02SB
| Outdoor Size |  | 36K | 48K | 58K
Ducted | Indoor Model |  | 36K | 48K | 58K
| Energy Star |  | NO | NO | NO
| NEEP |  | NO | NO | NO
| MASSCEC |  | NO | NO | NO
| CCHP |  | NO | NO | NO
| ASHP |  | NO | NO | NO
| ASHP COLD CLIMATE |  | NO | NO | NO
| Cooling System Tons |  | 3 | 4 | 4.75
| Cooling Rated Capacity | Btu/h | 36000 | 48000 | 57000
| Cooling Cap. Range Min - Max | Btu/h | 5,900~36,000 | 12,000~48,000 | 13,000~59,000
| SEER |  | 16.7 | 17.4 | 18
| EER |  | 9 | 9.2 | 10
| Heating Rated Capacity (47°F) | Btu/h | 40000 | 50000 | 60000
| Heating Rated Capacity (17°F) | Btu/h | 27000 | 29000 | 35400
| Heating Maximum Capacity (17°F) | Btu/h | 25000 | 29000 | 35400
| Heating Maximum Capacity (5°F) | Btu/h | 22000 | 32000 | 35000
| Heating Cap. Range Min - Max | Btu/h | 12,700~40,000 | 11,600~50,000 | 12,000-61,000
| HSPF |  | 11.5 | 10.3 | 10
| COP (47°F) | W/W | 3.37 | 3 | 3.5
| COP (17°F) | W/W | 2.63 | 2.57 | 2.5
| COP (5°F) | W/W | 1.9 | 1.95 | 2.01
Console | Indoor Model |  | 36K | 48K | 58K
| Energy Star |  | NO | NO | NO
| NEEP |  | NO | NO
| MASSCEC |  | NO | NO
| CCHP |  | NO | NO
| ASHP |  | NO | NO
| ASHP COLD CLIMATE |  | NO | NO
| Cooling System Tons |  | 3 | 4 | 4.5
| Cooling Rated Capacity | Btu/h | 36000 | 48000 | 54000
| Cooling Cap. Range Min - Max | Btu/h | 11,400~36,000 | 15,800~48,000 | 15,000~54,000
| SEER |  | 17 | 18 | 18
| EER |  | 8 | 9.3 | 9.8
| Heating Rated Capacity (47°F) | Btu/h | 38000 | 50000 | 60000
| Heating Rated Capacity (17°F) | Btu/h | 23000 | 29000 | 35000
| Heating Maximum Capacity (17°F) | Btu/h | 23000 | 29000 | 35000
| Heating Maximum Capacity (5°F) | Btu/h | 22000 | 28000 | 30000
| Heating Cap. Range Min - Max | Btu/h | 11,400~38,000 | 12,000~50,000 | 17,000~62,000
| HSPF |  | 10 | 11 | 10
| COP (47°F) | W/W | 2.8 | 2.5 | 3
| COP (17°F) | W/W | 2.34 | 2.52 | 2.49
| COP (5°F) | W/W | 1.8 | 1.95 | 1.9
Air Handler | Indoor Model |  | 36K | 48K | 60K
| Energy Star |  | NO | NO | NO
| NEEP |  | YES | YES
| MASSCEC |  | NO | NO
| CCHP |  | NO | NO
| ASHP |  | NO | NO
| ASHP COLD CLIMATE |  | NO | NO
| Cooling System Tons |  | 3 | 4 | 4.75
| Cooling Rated Capacity | Btu/h | 36000 | 48000 | 57000
| Cooling Cap. Range Min - Max | Btu/h | 11,600-41,000 | 11,800~51,900 | 11,000~60,000
| SEER |  | 17 | 16.2 | 17
| EER |  | 8.8 | 8.6 | 10
| Heating Rated Capacity (47°F) | Btu/h | 38000 | 55000 | 60000
| Heating Rated Capacity (17°F) | Btu/h | 25600 | 37500 | 34000
| Heating Maximum Capacity (17°F) | Btu/h | 27000 | 37500 | 34600
| Heating Maximum Capacity (5°F) | Btu/h | 22000 | 31000 | 33000
| Heating Cap. Range Min - Max | Btu/h | 9,200-43,000 | 11,900~58,000 | 12,000~60,400
| HSPF |  | 11.3 | 10.8 | 10.4
| COP (47°F) | W/W | 3.35 | 3.03 | 3.2
| COP (17°F) | W/W | 2.61 | 2.46 | 2.52
| COP (5°F) | W/W | 1.9 | 1.75 | 1.81
FB4C Fan Coil | Indoor Model |  |  | FB4CNP060L | FB4CNP061L
| Indoor Model 2 |  |  | FB4CNP061L
| Energy Star |  |  | NO | NO
| Cooling System Tons |  |  | 4.0833 | 4.8333
| Cooling Rated Capacity | Btu/h |  | 49000 | 58000
| Cooling Cap. Range Min - Max | Btu/h |  | 12500~51000 | 12000~60000
| SEER2 |  |  | 15.5 | 16.5
| EER2 |  |  | 9.5 | 10
| Heating Rated Capacity (47°F) | Btu/h |  | 41500 | 54000
| Heating Rated Capacity (17°F) | Btu/h |  | 28400 | 36600
| Heating Maximum Capacity (5°F) | Btu/h |  | 26700 | 29300
| Heating Cap. Range Min - Max | Btu/h |  | 12000~55000 | 12500~57000
| HSPF2 |  |  | 8 | 8.5
| COP (47°F) | W/W |  | 3.1 | 3.2
| COP (17°F) | W/W |  | 2.44 | 2.58
| COP (5°F) | W/W |  | 1.8 | 1.9
PF4M Fan Coil | Indoor Model |  |  | PF4MN(B,F)049L | PF4MN(B,F)061L
| Energy Star |  |  | NO | NO
| Cooling System Tons |  |  | 4.25 | 4.8333
| Cooling Rated Capacity | Btu/h |  | 51000 | 58000
| Cooling Cap. Range Min - Max | Btu/h |  | 12600~51500 | 12300~60200
| SEER2 |  |  | 16.5 | 16.5
| EER2 |  |  | 9.5 | 10
| Heating Rated Capacity (47°F) | Btu/h |  | 41500 | 54000
| Heating Rated Capacity (17°F) | Btu/h |  | 28000 | 36600
| Heating Maximum Capacity (5°F) | Btu/h |  | 26400 | 34500
| Heating Cap. Range Min - Max | Btu/h |  | 11900~53000 | 12300~56500
| HSPF2 |  |  | 8 | 8.5
| COP (47°F) | W/W |  | 3.4 | 3.2
| COP (17°F) | W/W |  | 2.6 | 2.58
| COP (5°F) | W/W |  | 1.9 | 1.9
Copyright 2024 CAC/BDP ● Atlanta, GA. 30339 | [8 empty] | Catalog No.: G38MBRC-03SB
SUBJECT TO CHANGE WITHOUT NOTICE | [8 empty] | Replaces: G38MBRC-02SB
| Outdoor Size |  | 36K | 48K | 58K
FV4C Fan Coil | Indoor Model |  |  | FV4CNF005L | FV4CNF006L
| Energy Star |  |  | NO | NO
| Cooling System Tons |  |  | 4.125 | 4.9583
| Cooling Rated Capacity | Btu/h |  | 49500 | 59500
| Cooling Cap. Range Min - Max | Btu/h |  | 12400~51000 | 12100~59600
| SEER2 |  |  | 14.45 | 14.75
| EER2 |  |  | 9.35 | 9.95
| Heating Rated Capacity (47°F) | Btu/h |  | 44000 | 56500
| Heating Rated Capacity (17°F) | Btu/h |  | 29400 | 38000
| Heating Maximum Capacity (5°F) | Btu/h |  | 18900 | 20600
| Heating Cap. Range Min - Max | Btu/h |  | 12100~53200 | 12500~59000
| HSPF2 |  |  | 7.95 | 8.35
| COP (47°F) | W/W |  | 3.2 | 3.25
| COP (17°F) | W/W |  | 2.5 | 2.55
| COP (5°F) | W/W |  | 1.75 | 1.55
Dimensions
*Drawing for reference only; 48K & 58K models have dual fans.
| Size |  | 36K | 48K | 58K
| Width (W) | in (mm) | 37.24 (946) | 37.48 (952) | 37.48 (952)
| Height (H) | in (mm) | 31.89 (810) | 52.48 (1333) | 52.48 (1333)
| Depth (D) | in (mm) | 16.14 (410) | 16.34 (415) | 16.34 (415)
| L1 | in (mm) | 26.50 (673) | 24.96 (634) | 24.96 (634)
| L2 | in (mm) | 15.85 (403) | 15.58 (396) | 15.58 (396)
| Operating Weight | lbs (kg) | 148.59 (67.4) | 219.14 (99.4) | 217.15 (98.5)
| Shipping Width | in (mm) | 42.91 (1090) | 43.11 (1095) | 43.11 (1095)
| Shipping Height | in (mm) | 34.45 (875) | 58.27 (1480) | 58.27 (1480)
| Shipping Depth | in (mm) | 19.68 (500) | 19.49 (495) | 19.49 (495)
| Shipping Weight | lbs (kg) | 160.94 (73) | 249.12 (113) | 248.24 (112.6)
Copyright 2024 CAC/BDP ● Atlanta, GA. 30339 | [8 empty] | Catalog No.: G38MBRC-03SB
SUBJECT TO CHANGE WITHOUT NOTICE | [8 empty] | Replaces: G38MBRC-01SB
36K
48K-58K