## 38MARB BRY
Outdoor Unit Single Zone Heat Pump Ductless System
38MARB Submittal Selection
Job Data: |  |  | Location: |  |  |  | Carrier #:
Tag #: | [6 empty] | Date:
[5 empty] | Outdoor Model # |  | Size |  | STANDARD FEATURES • Variable Speed (Inverter) • Factory installed Base Pan Heater • Factory installed Crankcase Heater • Low Voltage Controls • Auto-Restart function • Condenser High Temp Protection • Quiet operation • Anti-corrosive fin coating LIMITED WARRANTY* • 10 year limited to original purchaser on compressor and parts upon timely registration, otherwise 5 years *For residential applications. See warranty for full details.
[5 empty] | 38MARBQ12AA1 |  | 12K - 115V
[5 empty] | 38MARBQ06AA3 | 38MARBQ06AA3 | 6K
[5 empty] | 38MARBQ09AA3 | 38MARBQ09AA3 | 9K
[5 empty] | 38MARBQ12AA3 | 38MARBQ12AA3 | 12K - 208/230V
[5 empty] | 38MARBQ18AA3 | 38MARBQ18AA3 | 18K
[5 empty] | 38MARBQ24AA3 | 38MARBQ24AA3 | 24K
[5 empty] | 38MARBQ30AA3 | 38MARBQ30AA3 | 30K
[5 empty] | 38MARBQ36AA3 | 38MARBQ36AA3 | 36K
[5 empty] | 38MARBQ36AB3 | 38MARBQ36AB3 | 36K - AHU Only
Combination Selection
[5 empty] | Outdoor Unit | 24K
[5 empty] | Indoor Category | ALL
NOTE: Images for illustration purposes only. Actual models may be slightly different.
Specifications
Outdoor - Heat Pump
System | Outdoor Size |  | 12K - 115V | 6K | 9K | 12K - 208/230V | 18K | 24K | 30K | 36K | 36K - AHU Only
Electrical | Voltage, Phase, Cycle | V/Ph/Hz | 115-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60
| MCA | A. | 19 | 13 | 15 | 15 | 16 | 25 | 23 | 28 | 30
| Recommended Fuse Size | A. | 20 | 15 | 15 | 15 | 20 | 30 | 25 | 30 | 35
| MOCP - Fuse Rating | A. | 25 | 15 | 15 | 15 | 25 | 35 | 30 | 35 | 45
| Short Circuit Current Rating (SCCR) | kA | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Operating Range | Cooling Outdoor DB Min - Max | °F(°C) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50) | -22~122 (-30~50)
| Heating Outdoor DB Min - Max | °F(°C) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30)
Piping | Total Piping Length | ft (m) | 82 (25) | 82 (25) | 82 (25) | 82 (25) | 98 (30) | 164 (50) | 164 (50) | 213 (65) | 213 (65)
| Piping Lift* | ft (m) | 32 (10) | 32 (10) | 32 (10) | 32 (10) | 65 (20) | 82 (25) | 82 (25) | 98 (30) | 98 (30)
| Pipe Connection Size - Liquid | in (mm) | 1/4 (6.35) | 1/4 (6.35) | 1/4 (6.35) | 1/4 (6.35) | 1/4 (6.35) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52)
| Pipe Connection Size - Suction | in (mm) | 1/2 (12.7) | 3/8 (9.52) | 3/8 (9.52) | 1/2 (12.7) | 1/2 (12.7) | 5/8 (16) | 5/8 (16) | 5/8 (16) | 5/8 (16)
Refrigerant | Refrigerant Type |  | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A
| Charge | lbs (kg) | 2.47 (1.12) | 2.38 (1.08) | 2.6 (1.18) | 2.6 (1.18) | 4.08 (1.85) | 5.73 (2.6) | 6.06 (2.75) | 7.50 (3.40) | 7.05 (3.2)
| Add'l Refrigerant (between Std & Max Piping Lngths) | Oz/ft (g/m) | 0.161 (15) | 0.161 (15) | 0.161 (15) | 0.161 (15) | 0.161 (15) | 0.322 (30) | 0.322 (30) | 0.322 (30) | 0.322 (30)
| Metering Device |  | EEV | EEV | EEV | EEV | EEV | EEV | EEV | EEV | EEV
Outdoor Coil | Face Area | Sq. Ft. | 4.04 | 4.04 | 4.67 | 4.67 | 5.9 | 8.16 | 8.14 | 8.14 | 8.16
| No. Rows |  | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 2
| Fins per inch |  | 21 | 21 | 20 | 20 | 20 | 20 | 18 | 18 | 20
| Circuits |  | 4 | 4 | 4 | 4 | 6 | 4 | 6 | 6 | 4
Compressor | Type |  | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter
| Model |  | KSK103D33UEZ3 | KSK103D33UEZ3 | KTN110D42UFZ | KTN110D42UFZ | KTM240D43UKT | KTM240D43UKT | KTF250D22UMT | KTF250D22UMT | KTF310D43UMT
| Oil Type |  | VG74 | VG74 | VG74 | VG74 | VG74 | VG74 | VG74 | VG74 | VG74
| Oil Charge | Fl. Oz. | 10.48 | 10.48 | 11.84 | 11.84 | 20.97 | 20.97 | 22.66 | 22.66 | 33.8
| Rated Current | RLA | 11.5 | 6.4 | 6 | 8.5 | 14.25 | 14.8 | 15 | 18 | 20
Airflow & Sound | Airflow | CFM | 794.12 | 1324 | 1323.53 | 1323.53 | 1764.71 | 2235.29 | 2235.29 | 2235.29 | 3000
| Sound Pressure | dB(A) | 54 | 54.5 | 54.5 | 56 | 59 | 62 | 63 | 61.5 | 64
* Condensing unit above or below indoor unit
Performance
| Outdoor Size |  | 12K - 115V | 6K | 9K | 12K - 208/230V | 18K | 24K | 30K | 36K | 36K - AHU Only
High Wall | Indoor Model |  | 12K (115V) | 6K | 9K | 12K (208/230V) | 18K | 24K | 30K | 36K
| Energy Star |  | YES | YES | YES | YES | YES | YES | NO | NO
| Cooling Rated Capacity | Btu/h | 12000 | 6000 | 9000 | 12000 | 18000 | 24000 | 30000 | 36000
| Cooling Cap. Range Min - Max | Btu/h | 3,500~13,200 | 2,500~11,000 | 3,300~13,400 | 3,300~14,300 | 8,870~19,400 | 6,850~27,000 | 9,070~30,700 | 9,300~38,800
| SEER |  | 23 | 26.5 | 28.1 | 25.5 | 21.5 | 21.5 | 20 | 17.5
| EER |  | 13 | 15.8 | 16.2 | 14 | 12.5 | 13 | 11.5 | 8.5
| Heating Rated Capacity (47°F) | Btu/h | 12100 | 7400 | 11800 | 12000 | 18000 | 29000 | 30000 | 36000
| Heating Rated Capacity (17°F) | Btu/h | 7400 | 4900 | 7500 | 7500 | 10800 | 19800 | 19000 | 22400
| Heating Maximum Capacity (17°F) | Btu/h | 12200 | 9000 | 12000 | 12000 | 14000 | 24480 | 20670 | 23600
| Heating Maximum Capacity (5°F) | Btu/h | 7100 | 7500 | 10500 | 11650 | 18000 | 25400 | 17200 | 20400
| Heating Cap. Range Min - Max | Btu/h | 5,000~12,200 | 3,500~11,600 | 5,000~15,200 | 5,000~15,300 | 8,400~19,500 | 8,600~31,000 | 8,600~34,800 | 11,570~37,000
| HSPF |  | 11.5 | 14 | 13 | 13 | 13 | 12 | 9.6 | 9
| COP (47°F) | W/W | 3.7 | 3.9 | 3.81 | 3.81 | 3.1 | 3.4 | 2.6 | 2.51
| COP (17°F) | W/W | 2.67 | 3.05 | 3 | 3 | 2.8 | 3.05 | 2.25 | 2.18
| COP (5°F) | W/W | 2.18 | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.75 | 1.75
Copyright 2022 CAC/BDP • Atlanta, GA, 30339 | [10 empty] | Catalog No.: B38MARB-02SB
SUBJECT TO CHANGE WITHOUT NOTICE | [10 empty] | Replaces: B38MARB-01SB
| Outdoor Size |  | 12K - 115V | 6K | 9K | 12K - 208/230V | 18K | 24K | 30K | 36K | 36K - AHU Only
Cassette | Indoor Model |  |  |  | 9K | 12K (208/230V) | 18K | 24K
| Energy Star |  |  |  | YES | YES | YES | NO
| Cooling System Tons |  |  |  | 0.75 | 1 | 1.3333 | 2
| Cooling Rated Capacity | Btu/h |  |  | 9000 | 12000 | 16000 | 24000
| Cooling Cap. Range Min - Max | Btu/h |  |  | 2,850~11,100 | 3,000~13,700 | 5,600~17,000 | 8,000~25,000
| SEER |  |  |  | 20.5 | 21.5 | 20 | 20
| EER |  |  |  | 13 | 12.7 | 12.5 | 11
| Heating Rated Capacity (47°F) | Btu/h |  |  | 10000 | 12000 | 18000 | 24000
| Heating Rated Capacity (17°F) | Btu/h |  |  | 6100 | 7900 | 11000 | 14500
| Heating Maximum Capacity (17°F) | Btu/h |  |  | 11800 | 14000 | 21000 | 24200
| Heating Maximum Capacity (5°F) | Btu/h |  |  | 10200 | 11500 | 17000 | 24100
| Heating Cap. Range Min - Max | Btu/h |  |  | 1,800~12,500 | 2,000~15,300 | 8,700~21,000 | 11,800~27,000
| HSPF |  |  |  | 10.8 | 10.6 | 10.3 | 11.6
| COP (47°F) | W/W |  |  | 2.93 | 3.22 | 2.88 | 3.5
| COP (17°F) | W/W |  |  | 1.8 | 2.2 | 1.8 | 2.7
| COP (5°F) | W/W |  |  | 1.8 | 1.86 | 1.8 | 1.8
Ducted | Indoor Model |  |  |  | 9K | 12K (208/230V) | 18K | 24K
| Energy Star |  |  |  | YES | YES | YES | YES
| Cooling System Tons |  |  |  | 0.75 | 1 | 1.375 | 2
| Cooling Rated Capacity | Btu/h |  |  | 9000 | 12000 | 16500 | 24000
| Cooling Cap. Range Min - Max | Btu/h |  |  | 2,400~12,500 | 2,250~14,400 | 6,500~18,800 | 6,500~27,800
| SEER |  |  |  | 23 | 21.5 | 19.6 | 20.6
| EER |  |  |  | 14 | 13 | 12.5 | 12.5
| Heating Rated Capacity (47°F) | Btu/h |  |  | 10000 | 12000 | 19000 | 24600
| Heating Rated Capacity (17°F) | Btu/h |  |  | 6400 | 8300 | 12700 | 14500
| Heating Maximum Capacity (17°F) | Btu/h |  |  | 11600 | 12900 | 21500 | 26500
| Heating Maximum Capacity (5°F) | Btu/h |  |  | 9900 | 12400 | 17800 | 24600
| Heating Cap. Range Min - Max | Btu/h |  |  | 1,700~15,600 | 1,800~16,300 | 8,900~22,000 | 12,200~32,200
| HSPF |  |  |  | 12 | 11.5 | 11 | 12.6
| COP (47°F) | W/W |  |  | 3.62 | 3.52 | 2.93 | 3.66
| COP (17°F) | W/W |  |  | 1.9 | 2 | 1.9 | 2.8
| COP (5°F) | W/W |  |  | 1.8 | 1.87 | 1.8 | 2.01
Mix Match Ducted | Indoor Model | [5 empty] | 24K
| Energy Star | [5 empty] | YES
| Cooling System Tons | [5 empty] | 1.4583
| Cooling Rated Capacity | Btu/h |  |  |  |  | 17500
| Cooling Cap. Range Min - Max | Btu/h |  |  |  |  | 6,500~22,500
| SEER | [5 empty] | 20
| EER | [5 empty] | 13.2
| Heating Rated Capacity (47°F) | Btu/h |  |  |  |  | 19000
| Heating Rated Capacity (17°F) | Btu/h |  |  |  |  | 12600
| Heating Maximum Capacity (17°F) | Btu/h |  |  |  |  | 21500
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  |  | 18000
| Heating Cap. Range Min - Max | Btu/h |  |  |  |  | 9,000~23,500
| HSPF | [5 empty] | 11.5
| COP (47°F) | W/W |  |  |  |  | 3.71
| COP (17°F) | W/W |  |  |  |  | 2.78
| COP (5°F) | W/W |  |  |  |  | 1.8
Console | Indoor Model |  |  |  |  | 12K (208/230V) | 18K (208/230V) | 24K (208/230V)
| Energy Star |  |  |  |  | YES | YES | NO
| Cooling System Tons |  |  |  |  | 1 | 1.4167 | 2
| Cooling Rated Capacity | Btu/h |  |  |  | 12000 | 17000 | 24000
| Cooling Cap. Range Min - Max | Btu/h |  |  |  | 2,800~13,500 | 7,800~19,900 | 9,000~26,800
| SEER |  |  |  |  | 23 | 20.2 | 20.2
| EER |  |  |  |  | 13 | 12.5 | 11.5
| Heating Rated Capacity (47°F) | Btu/h |  |  |  | 12000 | 18000 | 24600
| Heating Rated Capacity (17°F) | Btu/h |  |  |  | 8400 | 12000 | 14500
| Heating Maximum Capacity (17°F) | Btu/h |  |  |  | 13100 | 20700 | 26600
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  | 12100 | 16900 | 24100
| Heating Cap. Range Min - Max | Btu/h |  |  |  | 2,350~15,700 | 8,600~21,500 | 12,500~30,500
| HSPF |  |  |  |  | 11.5 | 10.6 | 11.6
| COP (47°F) | W/W |  |  |  | 3.22 | 3.19 | 3.52
| COP (17°F) | W/W |  |  |  | 2 | 1.8 | 2.7
| COP (5°F) | W/W |  |  |  | 1.84 | 1.8 | 1.8
Air Handler | Indoor Model | [5 empty] | 18K (208/230V) | 24K (208/230V) | 30K (208/230V) |  | 36K (208/230V)
| Energy Star | [5 empty] | YES | YES | NO |  | NO
| NEEP | [5 empty] | YES | YES | YES |  | YES
| MASSSAVE | [5 empty] | YES | YES | YES |  | YES
| CCHP | [5 empty] | YES | YES | NO |  | NO
| ASHP | [5 empty] | YES | YES | NO |  | NO
| ASHP COLD CLIMATE | [5 empty] | NO | NO | NO |  | NO
| Cooling System Tons | [5 empty] | 1.5 | 1.9167 | 2.5 |  | 3
| Cooling Rated Capacity | Btu/h |  |  |  |  | 18000 | 23000 | 30000 |  | 36000
| Cooling Cap. Range Min - Max | Btu/h |  |  |  |  | 6,800~20,000 | 7,500~26,000 | 9,500~31,200 |  | 11,600~41,000
| SEER | [5 empty] | 20 | 21 | 19 |  | 17
| EER | [5 empty] | 12.5 | 12.5 | 11.1 |  | 8.8
| Heating Rated Capacity (47°F) | Btu/h |  |  |  |  | 19000 | 26000 | 30000 |  | 38000
| Heating Rated Capacity (17°F) | Btu/h |  |  |  |  | 12000 | 16200 | 19200 |  | 25600
| Heating Maximum Capacity (17°F) | Btu/h |  |  |  |  | 18500 | 23400 | 19600 |  | 25600
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  |  | 18000 | 23000 | 18000 |  | 20500
| Heating Cap. Range Min - Max | Btu/h |  |  |  |  | 5,800~21,000 | 5,600~29,000 | 12,000~32,000 |  | 9,200~43,000
| HSPF | [5 empty] | 10 | 11.6 | 10 |  | 11.3
| COP (47°F) | W/W |  |  |  |  | 3.62 | 3.58 | 3.26 |  | 3.35
| COP (17°F) | W/W |  |  |  |  | 2.34 | 2.8 | 2.6 |  | 2.62
| COP (5°F) | W/W |  |  |  |  | 1.9 | 1.95 | 1.85 |  | 1.9
Copyright 2022 CAC/BDP • Atlanta, GA, 30339 | [10 empty] | Catalog No.: B38MARB-02SB
SUBJECT TO CHANGE WITHOUT NOTICE | [10 empty] | Replaces: B38MARB-01SB
| Outdoor Size |  | 12K - 115V | 6K | 9K | 12K - 208/230V | 18K | 24K | 30K | 36K | 36K - AHU Only
FB4C Fan Coil | Indoor Model |  |  |  |  | FB4CNF018L | FB4CNF018L | FB4CNF024L | FB4CNF030L | FB4CNF036L
| Indoor Model 2 |  |  |  |  | FB4CNP018L | FB4CNP018L | FB4CNP024L | FB4CNP030L | FB4CNP036L
| Indoor Model Capacity |  |  |  |  | 12K (208/230V) | 18K | 24K | 30K | 36K
| Energy Star |  |  |  |  | NO | NO | NO | NO | NO
| Cooling System Tons |  |  |  |  | 1 | 1.5167 | 1.7833 | 2.3667 | 2.85
| Cooling Rated Capacity | Btu/h |  |  |  | 12000 | 18200 | 21400 | 28400 | 34200
| Cooling Cap. Range Min - Max | Btu/h |  |  |  | 7300~14800 | 13900~21400 | 11100~26400 | 14200~32400 | 13700~41500
| SEER |  |  |  |  | 17.5 | 19/17 | 15.5/15 | 17.5 | 14.5
| EER |  |  |  |  | 10.5 | 12 | 11.5 | 10.5 | 9.8
| Heating Rated Capacity (47°F) | Btu/h |  |  |  | 13500 | 18900 | 26200 | 28400 | 35600
| Heating Rated Capacity (17°F) | Btu/h |  |  |  | 7200 | 14700 | 16100 | 19100 | 20000
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  | 7800 | 13600 | 18800 | 16100 | 21400
| Heating Cap. Range Min - Max | Btu/h |  |  |  | 5500~14700 | 11500~20600 | 11900~28600 | 11000~31000 | 10400~38800
| HSPF |  |  |  |  | 9 | 10.5 | 9.5 | 11.5 | 8.2
| COP (47°F) | W/W |  |  |  | 3.7 | 3.85 | 3.3 | 3.3 | 3.15
| COP (17°F) | W/W |  |  |  | 2.35 | 3.2 | 2.25 | 2.25 | 2.25
| COP (5°F) | W/W |  |  |  | 1.65 | 2 | 1.8 | 2 | 1.75
FMA4X Fan Coil | Indoor Model |  |  |  |  | FMA4X18**AL* | FMA4X18**AL* | FMA4X24**AL* | FMA4X30**AL* | FMA4X36**AL*
| Indoor Model Capacity |  |  |  |  | 12K (208/230V) | 18K | 24K | 30K | 36K
| Energy Star |  |  |  |  | NO | NO | NO | NO | NO
| Cooling System Tons |  |  |  |  | 1.0583 | 1.5 | 1.8333 | 2.4667 | 2.9
| Cooling Rated Capacity | Btu/h |  |  |  | 12700 | 18000 | 22000 | 29600 | 34800
| Cooling Cap. Range Min - Max | Btu/h |  |  |  | 7800~15700 | 13800~21200 | 11400~26900 | 15000~33700 | 14100~42200
| SEER |  |  |  |  | 15.5 | 17 | 15 | 16.5 | 15
| EER |  |  |  |  | 10.5 | 11.8 | 11.5 | 10 | 9.5
| Heating Rated Capacity (47°F) | Btu/h |  |  |  | 13700 | 19200 | 26200 | 29200 | 36400
| Heating Rated Capacity (17°F) | Btu/h |  |  |  | 7200 | 15000 | 16000 | 19400 | 20200
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  | 7700 | 13900 | 18600 | 16200 | 21400
| Heating Cap. Range Min - Max | Btu/h |  |  |  | 5700~14900 | 11600~20900 | 11900~28600 | 11400~31800 | 10600~39700
| HSPF |  |  |  |  | 9.5 | 11 | 10 | 12 | 9
| COP (47°F) | W/W |  |  |  | 4.05 | 3.85 | 3.5 | 3.7 | 3.35
| COP (17°F) | W/W |  |  |  | 2.45 | 3.3 | 2.4 | 2.8 | 2.4
| COP (5°F) | W/W |  |  |  | 1.7 | 2 | 1.85 | 2 | 1.9
FX4D Fan Coil | Indoor Model |  |  |  |  | FX4DNF019L | FX4DNF019L | FX4DNF025L | FX4DNF031L | FX4DN(B,F)037L
| Indoor Model Capacity |  |  |  |  | 12K (208/230V) | 18K | 24K | 30K | 36K
| Energy Star |  |  |  |  | NO | NO | NO | NO | NO
| Cooling System Tons |  |  |  |  | 1.0667 | 1.5417 | 1.8333 | 2.3333 | 2.9
| Cooling Rated Capacity | Btu/h |  |  |  | 12800 | 18500 | 22000 | 28000 | 34800
| Cooling Cap. Range Min - Max | Btu/h |  |  |  | 8100~16000 | 14000~21800 | 11400~27100 | 14100~32100 | 13900~42200
| SEER |  |  |  |  | 17 | 18 | 15.5 | 17 | 17
| EER |  |  |  |  | 11 | 12.2 | 11.5 | 10 | 9.5
| Heating Rated Capacity (47°F) | Btu/h |  |  |  | 13400 | 18500 | 25400 | 27800 | 34400
| Heating Rated Capacity (17°F) | Btu/h |  |  |  | 7200 | 14500 | 15500 | 18800 | 19000
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  | 7900 | 13500 | 18000 | 15900 | 20000
| Heating Cap. Range Min - Max | Btu/h |  |  |  | 5600~14600 | 11400~20200 | 11700~27700 | 10800~30300 | 9900~37500
| HSPF |  |  |  |  | 9.5 | 10.5 | 10.5 | 11.5 | 8.5
| COP (47°F) | W/W |  |  |  | 4.1 | 3.9 | 3.7 | 3.25 | 3.2
| COP (17°F) | W/W |  |  |  | 2.5 | 3.25 | 2.6 | 2.55 | 2.3
| COP (5°F) | W/W |  |  |  | 1.7 | 2 | 2 | 2 | 1.75
FV4C Fan Coil | Indoor Model |  |  |  |  | FV4CNF002L | FV4CNF002L | FV4CNF002L | FV4CN(B,F)003L | FV4CN(B,F)003L
| Indoor Model Capacity |  |  |  |  | 12K (208/230V) | 18K | 24K | 30K | 36K
| Energy Star |  |  |  |  | NO | NO | NO | NO | NO
| Cooling System Tons |  |  |  |  | 0.95833 | 1.45 | 1.85 | 2.4167 | 2.9667
| Cooling Rated Capacity | Btu/h |  |  |  | 11500 | 17400 | 22200 | 29000 | 35600
| Cooling Cap. Range Min - Max | Btu/h |  |  |  | 7800~15700 | 14100~21400 | 11100~26400 | 14100~32400 | 13700~41500
| SEER |  |  |  |  | 16.5 | 16 | 14.5 | 16 | 15
| EER |  |  |  |  | 11.65 | 11.6 | 11.4 | 10.65 | 9.3
| Heating Rated Capacity (47°F) | Btu/h |  |  |  | 11500 | 17100 | 24400 | 29400 | 37000
| Heating Rated Capacity (17°F) | Btu/h |  |  |  | 6200 | 13400 | 15200 | 19200 | 21800
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  | 6800 | 12500 | 17900 | 15800 | 24500
| Heating Cap. Range Min - Max | Btu/h |  |  |  | 5500~14600 | 11700~21000 | 11900~28600 | 11400~31400 | 10400~38800
| HSPF |  |  |  |  | 10 | 10.5 | 11 | 11 | 9.9
| COP (47°F) | W/W |  |  |  | 3.65 | 3.65 | 3.85 | 3.25 | 3.1
| COP (17°F) | W/W |  |  |  | 2.15 | 3.25 | 2.8 | 2.5 | 2.3
| COP (5°F) | W/W |  |  |  | 1.5 | 2 | 2 | 2 | 1.85
FMC-FMU Fan Coil | Indoor Model |  |  |  |  | FM(C,U)4Z18**AL* | FM(C,U)4Z18**AL* | FM(C,U)4Z24**AL* | FM(C,U)4Z30**AL* | FM(C,U)4Z36**AL*
| Indoor Model Capacity |  |  |  |  | 12K (208/230V) | 18K | 24K | 30K | 36K
| Energy Star |  |  |  |  | NO | NO | NO | NO | NO
| Cooling System Tons |  |  |  |  | 1.0833 | 1.5417 | 1.8167 | 2.3833 | 2.8667
| Cooling Rated Capacity | Btu/h |  |  |  | 13000 | 18500 | 21800 | 28600 | 34400
| Cooling Cap. Range Min - Max | Btu/h |  |  |  | 8100~16000 | 14100~21800 | 11500~26900 | 14500~32800 | 14200~42200
| SEER |  |  |  |  | 17 | 19 | 15.5 | 17.5 | 16.5
| EER |  |  |  |  | 11.6 | 12.2 | 11.5 | 10.5 | 9.5
| Heating Rated Capacity (47°F) | Btu/h |  |  |  | 13600 | 19300 | 26200 | 28800 | 36200
| Heating Rated Capacity (17°F) | Btu/h |  |  |  | 7200 | 15000 | 16100 | 19200 | 20200
| Heating Maximum Capacity (5°F) | Btu/h |  |  |  | 7800 | 13900 | 18800 | 16100 | 21500
| Heating Cap. Range Min - Max | Btu/h |  |  |  | 5600~14600 | 11700~21000 | 11800~28600 | 11100~31400 | 10500~39500
| HSPF |  |  |  |  | 10 | 11.5 | 10 | 12.5 | 9
| COP (47°F) | W/W |  |  |  | 4.15 | 4 | 3.4 | 3.5 | 3.35
| COP (17°F) | W/W |  |  |  | 2.5 | 3.4 | 2.25 | 2.75 | 2.4
| COP (5°F) | W/W |  |  |  | 1.7 | 2 | 1.75 | 2 | 1.9
Copyright 2022 CAC/BDP • Atlanta, GA, 30339 | [10 empty] | Catalog No.: B38MARB-02SB
SUBJECT TO CHANGE WITHOUT NOTICE | [10 empty] | Replaces: B38MARB-01SB
Dimensions
| Size |  | 12K - 115V | 6K | 9K | 12K - 208/230V | 18K | 24K | 30K | 36K | 36K - AHU Only
| Width (W) | in (mm) | 30.12 (765) | 30.12 (765) | 31.69 (805) | 31.69 (805) | 35.04 (890) | 37.24 (946) | 37.24 (946) | 37.24 (946) | 37.24 (946)
| Height (H) | in (mm) | 21.85 (555) | 21.85 (555) | 21.81 (554) | 21.81 (554) | 26.50 (673) | 31.89 (810) | 31.89 (810) | 31.89 (810) | 31.89 (810)
| Depth (D) | in (mm) | 11.93 (303) | 11.93 (303) | 12.99 (330) | 12.99 (330) | 13.46 (342) | 16.14 (410) | 16.14 (410) | 16.14 (410) | 16.14 (410)
| L1 | in (mm) | 17.81 (452.40) | 17.81 (452.40) | 20.1 (511) | 20.1 (511) | 26.1 (663) | 26.49 (672.96) | 26.49 (672.96) | 26.49 (672.96) | 26.49 (672.96)
| L2 | in (mm) | 11.25 (285.76) | 11.25 (285.76) | 12.5 (317.2) | 12.5 (317.2) | 13.65 (346.674) | 15.85 (402.6) | 15.85 (402.6) | 15.85 (402.6) | 15.85 (402.6)
| Operating Weight | lbs (kg) | 66.80 (30.3) | 63.71 (28.9) | 74.07 (33.6) | 73.63 (33.4) | 100.97 (45.8) | 134.48 (61) | 141.76 (64.3) | 150.13 (68.1) | 155.42 (70.5)
| Shipping Width | in (mm) | 34.92 (887) | 34.92 (887) | 36.02 (915) | 36.02 (915) | 39.17 (995) | 42.91 (1090) | 42.91 (1090) | 42.91 (1090) | 42.91 (1090)
| Shipping Height | in (mm) | 24.02 (610) | 24.02 (610) | 24.21 (615) | 24.21 (615) | 29.13 (740) | 34.84 (885) | 34.84 (885) | 34.84 (885) | 34.84 (885)
| Shipping Depth | in (mm) | 13.27 (337) | 13.27 (337) | 14.57 (370) | 14.57 (370) | 15.67 (398) | 19.69 (500) | 19.69 (500) | 19.69 (500) | 19.69 (500)
| Shipping Weight | lbs (kg) | 72.31 (32.8) | 69 (31.3) | 80.25 (36.4) | 79.37 (36) | 108.03 (49) | 144.40 (65.5) | 152.56 (69.2) | 158.95 (72.1) | 166.23 (75.4)
Copyright 2022 CAC/BDP • Atlanta, GA, 30339 | [10 empty] | Catalog No.: B38MARB-02SB
SUBJECT TO CHANGE WITHOUT NOTICE | [10 empty] | Replaces: B38MARB-01SB