## Multizone Sizing Tool
Multi-zone design quick select - VERSION 1.2
|  | Outdoor Unit Selection | [7 empty] | Piping size and charge Information
|  | Outdoor Unit Size | 24 | [6 empty] | Model | Liquid Pipe (in) | Gas Pipe (in)
|  | Outdoor Unit Model | 38MGRQ24C--3 | [6 empty] | 40MAQB09B--3 | 0.25 | 0.375
|  | Indoor Unit Type | Non-Ducted Indoor Units | [6 empty] | 40MHHQ09---3 | 0.25 | 0.375
|  | Cooling rated capacity | 24
|  | Heating rated capacity | 23
|  | Min number indoor units | 2
|  | Max number indoor units | 3 | [6 empty] | Total Piping Length (ft) |  | 55
[10 empty] | Additional Ref. Charge (oz) |  | No added charge
Capacity Reduction
|  | Outdoor Design Conditions (F) |  |  | Cooling | Heating
|  | Cooling Design Temp DB (°F) | 95 |  | 0.97589 | 0
|  | Heating Design Temp DB (°F) | 45 |  | 0 | 0.98896
|  | Altitude (ft) | 1000 |  | 0.9801 | 0.9801 | For a more accurate selection and calculation, consider using: VROOM Ductless & VRF Selection Tool
|  | Defrost Correction |  |  | 0 | 1 |  |  |  | PIPING REQUIREMENTS
|  | Total Derate |  |  | 0.95647 | 0.96928 |  |  |  | Minimum piping length per indoor unit (ft) |  | 10
[10 empty] | Maximum piping length per indoor unit (ft) |  | 98
|  | Indoor Design Conditions (°F) | [7 empty] | Max total piping length no additional ref. charge (ft) |  | 74
|  | Indoor Cooling Design Temp DB (°F) | 80 | [6 empty] | Maximum total piping length (ft) |  | 197
|  | Indoor Heating Design Temp DB (°F) | 70 | [6 empty] | Maximum vertical piping lift/drop (ft) |  | 49
[10 empty] | Max height difference between indoor units (ft) |  | 32
|  | Will each indoor unit in this system be on the same floor/level of the home? |  |  | Yes
|  | Room Name | Room size (ft²)* | Indoor Type | Model Number | Rated Cooling Capacity | Rated Heating Capacity | Corrected Cooling Capacity | Corrected Heating Capacity | Corrected Sensible Capacity | Description | Pipe length to ODU (ft)
| 1 | Bedroom 1 |  | High Wall | 40MAQB09B--3 | 9 | 10.9 | 10.0076 | 11.5887 | 7.7631 | High Wall Mid Carrier | 10
| 2 | Bedroom 2 |  | High Wall | 40MHHQ09---3 | 8.5 | 9.8 | 9.0511 | 10.6194 | 6.8066 | High Wall Entry | 45
| 3 | Bedroom 3
| 4 | Bedroom 4
| 5 | Bedroom 5
| Total Capacity |  |  |  |  | 17.5 | 20.7 | 19.0587 | 22.2082 | 14.5697
| % of Capacity |  |  |  |  | 72.92% | 90% | 79.41% | 96.56%
Instructions: Enter all fields highlighted in green. Entering room names and sizes is optional. If no errors or warnings appear the selection is valid. Piping lengths should be entered as the one way length to each indoor unit. All Indoor units are connected in a home run style with the outdoor unit. Consult the Multi-zone Combinations tab for approved combinations. Previously added Indoor Type, Model Number and Pipe length can be deleted manually using the keyboard.
Errors And Warnings
Product Line up
| High Wall |  |  |  | Ducted | Cassette |  | Console | Air Handler | Outdoor Unit
[6 empty] | 2x2 | 3x3
| 40MAQ/619P*B/DHMSHA |  | 40MPHA/619PHA/DHMPHA
Floor 12
[5 empty] | 9-24 | 9-18 | 24 | Floor-Ceiling 18-24 | 24 | 18 | 24-30 | 36K - 48
| 40MHHQ**---3 |  |  |  | 40MBDQ**---3 | 40MBCQ**---3 |  | 40MBFQ**---3 | 40MBAA | 38MGRQ**---3
*Room size calculation may not be accurate for your area. Always consider running a full load calculation.
DISCLAIMERS AND PROHIBITION ON COPYING This Multi-zone design quick select tool is intended for use only by Carrier Corporation employees and distributors of Carrier® ductless products. *Room size calculation may not be accurate for your area. Always consider running a full load calculation. Performance and specifications are subject to change without notice. It is intended only for general reference to assist with selecting Carrier® ductless products and may not be current or up to date. Data is provided “as is” and Carrier Corporation disclaims all warranties, whether express, implied, statutory or otherwise. Carrier Corporation is not liable for any direct or indirect damages or any other liability in connection with use of this tool. This tool may not be reproduced, disclosed, or distributed to any person without prior written authorization from an officer of Carrier Corporation. Any unauthorized reproduction, disclosure, or distribution of copies by any person of any portion of this work may be a violation of Copyright Law of the United States of America and other countries, could result in the awarding of Statutory Damages of up to $250,000 (17 USC 504) for infringement, and may result in further civil and criminal penalties. Confidential and Proprietary – Not for Further Distribution. Copyright © 2020 Carrier Corporation. All rights reserved.

## Multi-zone Combinations
Multi-zone Combinations
Heat Pump
Outdoor Unit Model | 2-Zone | 3-Zone | 4-Zone | 5-Zone
38MGRQ18B--3 | 9+9
9+12
12+12
38MGRQ24C--3 | 9+9 | 9+9+9
| 9+12 | 9+9+12
| 9+18 | 9+9+18
| 12+12 | 9+12+12
| 12+18 | 12+12+12
18+18
38MGRQ30D--3 | 9+9 | 9+9+9 | 9+9+9+9
| 9+12 | 9+9+12 | 9+9+9+12
| 9+18 | 9+9+18 | 9+9+9+18
| 9+24 | 9+9+24 | 9+9+12+12
| 12+12 | 9+12+12 | 9+9+12+18
| 12+18 | 9+12+18 | 9+12+12+12
| 12+24 | 9+12+24 | 12+12+12+12
| 18+18 | 9+18+18
12+12+12
12+12+18
12+18+18
12+12+24
38MGRQ36D--3 | 9+18 | 9+9+9 | 9+9+9+9
| 9+24 | 9+9+12 | 9+9+9+12
| 12+12 | 9+9+18 | 9+9+9+18
| 12+18 | 9+9+24 | 9+9+9+24
| 12+24 | 9+12+12 | 9+9+12+12
| 18+18 | 9+12+18 | 9+9+12+18
| 18+24 | 9+12+24 | 9+9+12+24
| 24+24 | 9+18+18 | 9+9+18+18
|  | 9+18+24 | 9+9+18+24
|  | 9+24+24 | 9+12+12+12
|  | 12+12+12 | 9+12+12+18
|  | 12+12+18 | 9+12+12+24
|  | 12+12+24 | 9+12+18+18
|  | 12+18+18 | 9+18+18+18
|  | 12+18+24 | 12+12+12+12
|  | 12+24+24 | 12+12+12+18
|  | 18+18+18 | 12+12+12+24
|  | 18+18+24 | 12+12+18+18
38MGRQ48E--3 | 9+18 | 9+9+9 | 9+9+9+9 | 9+9+9+9+9
| 9+24 | 9+9+12 | 9+9+9+12 | 9+9+9+9+12
| 12+12 | 9+9+18 | 9+9+9+18 | 9+9+9+9+18
| 12+18 | 9+9+24 | 9+9+9+24 | 9+9+9+9+24
| 12+24 | 9+12+12 | 9+9+12+12 | 9+9+9+12+12
| 18+18 | 9+12+18 | 9+9+12+18 | 9+9+9+12+18
| 18+24 | 9+12+24 | 9+9+12+24 | 9+9+9+18+18
| 24+24 | 9+18+18 | 9+9+18+18 | 9+9+12+12+12
|  | 9+18+24 | 9+9+18+24 | 9+9+12+12+18
|  | 9+24+24 | 9+12+12+12 | 9+12+12+12+12
|  | 12+12+12 | 9+12+12+18 | 9+12+12+12+18
|  | 12+12+18 | 9+12+12+24 | 12+12+12+12+12
|  | 12+12+24 | 9+12+18+18
|  | 12+18+18 | 9+18+18+18
|  | 12+18+24 | 12+12+12+12
|  | 12+24+24 | 12+12+12+18
|  | 18+18+18 | 12+12+12+24
|  | 18+18+24 | 12+12+18+18

## Revision
No. | User name | Date | Type of revision | Version
1 | Diego Salazar | 2020-06-15 | Initial release | 1
2 | Diego Salazar | 2020-06-17 | Added Rated Capacities based on the Indoor unit type combination | 1.1
3 | Diego Salazar | 2020-07-28 | Added Air Handler 40MBAA, Added Multi-zone Combinations tab | 1.2
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37

## Calculations (hidden)
[11 empty] | Cooling Temp |  | 95
Nominal | 24 | [9 empty] | Heating Temp |  | 45
[15 empty] | Non-Ducted Indoor Units |  |  | Mixed Ducted and Non-Ducted Indoor Units |  | Ducted Indoor Units | [6 empty] | Max Pipe per IDU | Max Pipe length | Pipe length no additional charge | Maximum piping lift/drop (ft)
[12 empty] | Size | Outdoor Model number | Maximum number of IDUs | Cooling Rated Capacity | Heating Rated Capacity (47°F) |  | Cooling Rated Capacity | Heating Rated Capacity (47°F) | Cooling Rated Capacity | Heating Rated Capacity (47°F) | Maximum number of IDUs | 3 |  | 38MGRQ18B--3 |  | 82 | 131 | 49 | 49
[12 empty] | 18 | 38MGRQ18B--3 | 2 | 18 | 19 | 1.3333 | 18 | 18.7 | 18 | 18.5 | Model Selected | 38MGRQ24C--3 |  | 38MGRQ24C--3 |  | 98 | 197 | 74 | 49
[12 empty] | 24 | 38MGRQ24C--3 | 3 | 24 | 23 | 1.5 | 24 | 24 | 24 | 24 | Number of indoors selected | 2 |  | 38MGRQ30D--3 |  | 115 | 263 | 98 | 49
[12 empty] | 30 | 38MGRQ30D--3 | 4 | 30 | 28 | 1.6 | 30 | 29 | 30 | 30 |  |  |  | 38MGRQ36D--3 |  | 115 | 328 | 123 | 65
[12 empty] | 36 | 38MGRQ36D--3 | 4 | 36 | 36 | 1.6667 | 36 | 36.4 | 36 | 37 |  |  |  | 38MGRQ48E--3 |  | 115 | 328 | 123 | 65
| TC | SC | [9 empty] | 48 | 38MGRQ48E--3 | 5 | 48 | 48 | 1.25 | 48.5 | 49 | 49 | 50
-13 | 1.1208 | 53.8 | [24 empty] | 98 | 197 | 74 | 49
-4 | 1.1487 | 55.14
0 | 1.1392 | 54.68 | [7 empty] | Cool Correct | Heat Correct | Defrost Correct |  |  | Indoor Type | Model Number | Type | Size | Cooling Rated Capacity | Heating Rated Capacity (47°F) | Type
5 | 1.1523 | 55.31 | [5 empty] | Non duct |  | 1 | 1.5835 | 1 |  |  | High Wall | 40MAQB09B--3 | High Wall Mid Carrier | 9 | 9 | 10.9 | L
17 | 1.1698 | 56.15 | [10 empty] | Indoor Type List |  | High Wall | 40MAQB12B--3 | High Wall Mid Carrier | 12 | 12 | 11.8 | L
47 | 1.1817 | 56.72 | [10 empty] | High Wall |  | High Wall | 40MAQB18B--3 | High Wall Mid Carrier | 18 | 17 | 18 | L | Indoor Unit 1 | Indoor Unit 2 | Indoor Unit 3 | Indoor Unit 4 | Indoor Unit 5
77 | 1.2554 | 60.26 | [10 empty] | Cassette |  | High Wall | 40MAQB24B--3 | High Wall Mid Carrier | 24 | 24 | 24 | L | 9 | 9
86 | 1.1838 | 56.82 | [10 empty] | Ducted |  | High Wall | 619PEQ009BBMA | High Wall Mid Bryant | 9 | 9 | 10.9 | L | [6 empty] | 98
95 | 1.1075 | 53.16 | [10 empty] | Air Handler |  | High Wall | 619PEQ012BBMA | High Wall Mid Bryant | 12 | 12 | 11.8 | L | 9+9
104 | 0.85313 | 40.95 | [10 empty] | Console |  | High Wall | 619PEQ018BBMA | High Wall Mid Bryant | 18 | 17 | 18 | L | Non-Ducted Indoor Units
113 | 0.80354 | 38.57 | [12 empty] | High Wall | 619PEQ024BBMA | High Wall Mid Bryant | 24 | 24 | 24 | L | Size | Cooling Capacity | Heating Capacity | Sensible Capacity
122 | 0.73417 | 35.24 | [12 empty] | High Wall | DHMSHAQ09XA3 | High Wall Mid | 9 | 9 | 10.9 | L | 9 | 10.4631 | 11.956 | 8.1164
[15 empty] | High Wall | DHMSHAQ12XA3 | High Wall Mid | 12 | 12 | 11.8 | L | 9 | 10.4631 | 11.956 | 8.1164
[15 empty] | High Wall | DHMSHAQ18XA3 | High Wall Mid | 18 | 17 | 18 | L | #NUM! | 0 | 0 | 0
| 18K | 24k | 30k | 36k | 48k |  |  |  | 38MGRQ18B--3 | 38MGRQ24C--3 | 38MGRQ30D--3 | 38MGRQ36D--3 | 38MGRQ48E--3 |  | High Wall | DHMSHAQ24XA3 | High Wall Mid | 24 | 24 | 24 | L | #NUM! | 0 | 0 | 0
-13 | 1.2172 | 1.5104 | 1.371 | 1.1828 | 1.1208 |  |  | x | 95 | 95 | 95 | 95 | 95 |  | High Wall | 40MPHAQ09XA3 | High Wall High Carrier | 9 | 9 | 10 | L | #NUM! | 0 | 0 | 0
-4 | 1.2478 | 1.5479 | 1.405 | 1.2122 | 1.1487 |  |  | x1 | 95 | 95 | 95 | 95 | 95 |  | High Wall | 40MPHAQ12XA3 | High Wall High Carrier | 12 | 12 | 12 | L
0 | 1.2322 | 1.5517 | 1.417 | 1.2031 | 1.1392 |  |  | y1 | 1.1967 | 1.3646 | 1.294 | 1.1525 | 1.1075 |  | High Wall | 619PHAQ09XA3 | High Wall High Bryant | 9 | 9 | 10 | L
5 | 1.2517 | 1.545 | 1.4203 | 1.2264 | 1.1523 |  |  | x2 | 104 | 104 | 104 | 104 | 104 |  | High Wall | 619PHAQ12XA3 | High Wall High Bryant | 12 | 12 | 12 | L
17 | 1.2694 | 1.5629 | 1.4033 | 1.2372 | 1.1698 |  |  | y2 | 0.82333 | 1.0296 | 1.0723 | 0.95667 | 0.85313 |  | High Wall | DHMPHAQ09XA3 | High Wall High | 9 | 9 | 10 | L
47 | 1.3417 | 1.57 | 1.4203 | 1.2506 | 1.1817 | [9 empty] | High Wall | DHMPHAQ12XA3 | High Wall High | 12 | 12 | 12 | L
77 | 1.395 | 1.5637 | 1.4137 | 1.2761 | 1.2554 |  |  | y | 1.1967 | 1.3646 | 1.294 | 1.1525 | 1.1075 |  | High Wall | 40MHHQ09---3 | High Wall Entry | 9 | 8.5 | 9.8 | L
86 | 1.325 | 1.4746 | 1.3543 | 1.2147 | 1.1838 | [9 empty] | High Wall | 40MHHQ12---3 | High Wall Entry | 12 | 12 | 12 | L
95 | 1.1967 | 1.3646 | 1.294 | 1.1525 | 1.1075 | [9 empty] | High Wall | 40MHHQ18---3 | High Wall Entry | 18 | 18 | 18 | L
104 | 0.82333 | 1.0296 | 1.0723 | 0.95667 | 0.85313 | [9 empty] | High Wall | 40MHHQ24---3 | High Wall Entry | 24 | 22 | 25 | L
113 | 0.79 | 0.99833 | 1.0157 | 0.88694 | 0.80354 | [9 empty] | Cassette | 40MBCQ09---3 | Cassette 2x2 | 9 | 9 | 9 | L
122 | 0.57778 | 0.83958 | 0.91767 | 0.75444 | 0.73417 | [9 empty] | Cassette | 40MBCQ12---3 | Cassette 2x2 | 12 | 12 | 12 | L
[15 empty] | Cassette | 40MBCQ18---3 | Cassette 2x2 | 18 | 16 | 18 | L
[15 empty] | Cassette | 40MBCQ24---3 | Cassette 3x3 | 24 | 24 | 24 | L
[15 empty] | Ducted | 40MBDQ09---3 | Ducted | 9 | 9 | 10 | D
[15 empty] | Ducted | 40MBDQ12---3 | Ducted | 12 | 12 | 12 | D
[15 empty] | Ducted | 40MBDQ18---3 | Ducted | 18 | 16.5 | 19 | D
[15 empty] | Ducted | 40MBDQ24---3 | Ducted | 24 | 24 | 24 | D
[15 empty] | Air Handler | 40MBAAQ24XA3 | Air handler | 24 | 24 | 24 | D
[15 empty] | Console | 40MBFQ12---3 | Console | 12 | 12 | 12 | L
[15 empty] | Console | 40MBFQ18---3 | Floor Ceiling | 18 | 18 | 18 | L
[15 empty] | Console | 40MBFQ24---3 | Floor Ceiling | 24 | 24 | 24 | L
[28 empty] | Indoor Model | Size | Cooling Capacity | Heating Capacity | Sensible Capacity
[27 empty] | L | 40MAQB09B--3 | 9 | 10.4631 | 11.956 | 8.1164
[27 empty] | L | 40MHHQ09---3 | 9 | 9.4631 | 10.956 | 7.1164
0
0
0
[26 empty] | 0 | 1
[25 empty] | Room Name | Room size (ft²)* | Model Number | Corrected Cooling Capacity | Corrected Heating Capacity | Estimated heating load | Swing Season Heating Load
[25 empty] | Bedroom 1 | 0 | 40MAQB09B--3 | 10.0076 | 11.5887 | 0 | 0 | 0
[25 empty] | Bedroom 2 | 0 | 40MHHQ09---3 | 9.0511 | 10.6194 | 0 | 0 | 0
[25 empty] | Bedroom 3 | 0 | 0 |  |  | 0 | 0 | 0
[25 empty] | Bedroom 4 | 0 | 0 |  |  | 0 | 0 | 0
[25 empty] | Bedroom 5 | 0 | 0 |  |  | 0 | 0 | 0
0
[22 empty] | Indoor Model | Liqiuid Pipe size | Gas Pipe size
[22 empty] | 40MAQB09B--3 | 0.25 | 0.375
[10 empty] | Heating Design Temp (°F) |  | x | 45 | [8 empty] | 40MAQB12B--3 | 0.25 | 0.5
|  | 38MGRQ18B--3 | 38MGRQ24C--3 | 38MGRQ30D--3 | 38MGRQ36D--3 | 38MGRQ48E--3 |  |  |  | 19 | 0.95 | x1 | 45 | [8 empty] | 40MAQB18B--3 | 0.25 | 0.5
| x | 45 | 45 | 45 | 45 | 45 |  |  |  | 25 | 0.89 | y1 | 1 | [8 empty] | 40MAQB24B--3 | 0.375 | 0.625
| x1 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 |  |  |  | 30 | 0.87 | x2 | #REF! | [8 empty] | 619PEQ009BBMA | 0.25 | 0.375
| y1 | 1.2611 | 1.5748 | 1.3289 | 1.4039 | 1.1631 |  |  |  | 35 | 0.9 | y2 | #REF! | [8 empty] | 619PEQ012BBMA | 0.25 | 0.5
| x2 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 |  |  |  | 40 | 1 | [10 empty] | 619PEQ018BBMA | 0.25 | 0.5
| y2 | 1.4037 | 1.77 | 1.4382 | 1.5103 | 1.3696 |  |  |  | 45 | 1 | y | #REF! | [8 empty] | 619PEQ024BBMA | 0.375 | 0.625
[22 empty] | DHMSHAQ09XA3 | 0.25 | 0.375
| y | 1.2674 | 1.5835 | 1.3338 | 1.4086 | 1.1723 | [15 empty] | DHMSHAQ12XA3 | 0.25 | 0.5
[22 empty] | DHMSHAQ18XA3 | 0.25 | 0.5
[22 empty] | DHMSHAQ24XA3 | 0.375 | 0.625
|  | 18 |  | 24 |  | 30 |  | 36 |  | 48 | [11 empty] | 40MPHAQ09XA3 | 0.25 | 0.375
-22 | 5.52 | 0.29053 | 13.85 | 0.60217 | 16.7 | 0.59643 | 23.03 | 0.63972 | 23.33 | 0.48604 | [11 empty] | 40MPHAQ12XA3 | 0.25 | 0.5
-13 | 6.54 | 0.34421 | 17.59 | 0.76478 | 20.65 | 0.7375 | 27.69 | 0.76917 | 28.05 | 0.58437 | [11 empty] | 619PHAQ09XA3 | 0.25 | 0.375
-4 | 7.69 | 0.40474 | 19.84 | 0.86261 | 22.05 | 0.7875 | 29.04 | 0.80667 | 29.42 | 0.61292 | [11 empty] | 619PHAQ12XA3 | 0.25 | 0.5
0 | 8.14 | 0.42842 | 22.28 | 0.9687 | 24.02 | 0.85786 | 31.77 | 0.8825 | 32.18 | 0.67042 | [11 empty] | DHMPHAQ09XA3 | 0.25 | 0.375
5 | 13.99 | 0.73632 | 24.17 | 1.0509 | 28.22 | 1.0079 | 36.08 | 1.0022 | 36.34 | 0.75708 | [11 empty] | DHMPHAQ12XA3 | 0.25 | 0.5
17 | 15.02 | 0.79053 | 25.15 | 1.0935 | 27.67 | 0.98821 | 37.41 | 1.0392 | 37.9 | 0.78958 | [11 empty] | 40MHHQ09---3 | 0.25 | 0.375
19.4 | 15.94 | 0.83895 | 25.52 | 1.1096 | 28.13 | 1.0046 | 37.75 | 1.0486 | 38.24 | 0.79667 | [11 empty] | 40MHHQ12---3 | 0.25 | 0.5
24.8 | 17.13 | 0.90158 | 27.74 | 1.2061 | 31.86 | 1.1379 | 39.77 | 1.1047 | 40.29 | 0.83937 | [11 empty] | 40MHHQ18---3 | 0.25 | 0.5
32 | 18.93 | 0.99632 | 29.89 | 1.2996 | 33.96 | 1.2129 | 42.39 | 1.1775 | 42.94 | 0.89458 | [11 empty] | 40MHHQ24---3 | 0.375 | 0.625
39.2 | 19.66 | 1.0347 | 31.21 | 1.357 | 36.08 | 1.2886 | 46.46 | 1.2906 | 47.06 | 0.98042 | [11 empty] | 40MBCQ09---3 | 0.25 | 0.375
44.6 | 23.96 | 1.2611 | 36.22 | 1.5748 | 37.21 | 1.3289 | 50.54 | 1.4039 | 55.83 | 1.1631 | [11 empty] | 40MBCQ12---3 | 0.25 | 0.5
53.6 | 26.67 | 1.4037 | 40.71 | 1.77 | 40.27 | 1.4382 | 54.37 | 1.5103 | 65.74 | 1.3696 | [11 empty] | 40MBCQ18---3 | 0.25 | 0.5
[22 empty] | 40MBCQ24---3 | 0.375 | 0.625
[22 empty] | 40MBDQ09---3 | 0.25 | 0.375
[22 empty] | 40MBDQ12---3 | 0.25 | 0.5
[22 empty] | 40MBDQ18---3 | 0.25 | 0.5
[22 empty] | 40MBDQ24---3 | 0.375 | 0.625
[22 empty] | 40MBAAQ24XA3 | 0.375 | 0.625
[22 empty] | 40MBFQ12---3 | 0.25 | 0.5
[22 empty] | 40MBFQ18---3 | 0.25 | 0.5
[22 empty] | 40MBFQ24---3 | 0.375 | 0.625

## Defrost Correction (hidden)
Outdoor Temperature | Defrost Correction
-13 | 0.95
-12 | 0.95
-11 | 0.95
-10 | 0.95
-9 | 0.95
-8 | 0.95
-7 | 0.95
-6 | 0.95
-5 | 0.95
-4 | 0.95
-3 | 0.95
-2 | 0.95
-1 | 0.95
0 | 0.95
1 | 0.95
2 | 0.95
3 | 0.95
4 | 0.95
5 | 0.95
6 | 0.95
7 | 0.95
8 | 0.95
9 | 0.95
10 | 0.95
11 | 0.95
12 | 0.95
13 | 0.95
14 | 0.95
15 | 0.95
16 | 0.95
17 | 0.95
18 | 0.95
19 | 0.95
20 | 0.95
21 | 0.95
22 | 0.95
23 | 0.95
24 | 0.95
25 | 0.9
26 | 0.9
27 | 0.9
28 | 0.89
29 | 0.89
30 | 0.89
31 | 0.89
32 | 0.88
33 | 0.88
34 | 0.88
35 | 0.88
36 | 0.89
37 | 0.89
38 | 0.89
39 | 0.98
40 | 0.98
41 | 0.98
42 | 0.98
43 | 1

## Non-Ducted (hidden)
Non-Ducted Indoor Units | [26 empty] | NOMINAL COMBINATIONS | [6 empty] | COOLING ESTIMATED CAPACITY CAPPED | [5 empty] | COOLING CAPPED CAPACITY BASED ON INDOOR UNIT | [5 empty] | COOLING ORIGINAL ESTIMATED CAPACITY | [5 empty] | COOLING CALCULATION UNCAPPED | [5 empty] | HEATING ESTIMATED CAPACITY CAPPED | [5 empty] | HEATING CAPPED CAPACITY BASED ON INDOOR UNIT | [5 empty] | HEATING ORIGINAL ESTIMATED CAPACITY |  |  |  |  | HEATING CALCULATION UNCAPPED | [5 empty] | SENSIBLE ESTIMATED CAPACITY BASED ON RATIO
[24 empty] | Variables of indoor |  | Size |  | Size |  |  |  |  | No. of Zones | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Heating Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h)
[21 empty] | Size |  |  | Indoor Unit Sizes | Defined by size/variable 9 | 18K | 18 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[21 empty] | INDOOR DB | 80 |  | 9 | 1 | 9+9 | 18 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 18 | 9 | 9 |  |  |  | 21.2967 | 10.6483 | 10.6483 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | Zone 1: 11.956; Zone 2: 11.956; Zone 1: 9500; Zone 2: 9500 | 23.9413 | 11.9706 | 11.9706 |  |  |  | 15.8621 | 7.9311 | 7.9311
[21 empty] | OUTDOOR Cool Design Temp (°F) | 95 |  | 12 | 1.3333 | 9+12 | 18 | 9 | 12 |  |  |  |  | 21.2967 | 9.1271 | 12.1695 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 19 | 8.5 | 10.5 |  |  |  | 21.2967 | 9.1271 | 12.1695 |  |  |  | 23.9413 | 10.2606 | 13.6807 |  |  |  | 26.901 | Zone 1: 11.956; Zone 2: 14.945; Zone 1: 9000; Zone 2: 11000 | 23.9413 | 10.2606 | 13.6807 |  |  |  | 16.1429 | 6.9184 | 9.2245
[21 empty] | OUTDOOR Heat Design Temp (°F) | 45 |  | 18 | 2 | 12+12 | 18 | 12 | 12 |  |  |  |  | 21.2967 | 10.6483 | 10.6483 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 19 | 9.5 | 9.5 |  |  |  | 21.2967 | 10.6483 | 10.6483 |  |  |  | 23.9413 | 11.9706 | 11.9706 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 10000; Zone 2: 10000 | 23.9413 | 11.9706 | 11.9706 |  |  |  | 16.1429 | 8.0715 | 8.0715
[21 empty] | Total Cooling | 32.0467 |  | 24 | 2.6667 | 24K | 24 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[21 empty] | Total Heating | 36.2107 |  |  |  | 9+9 | 24 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 19 | 9.5 | 9.5 |  |  |  | 32.0467 | 16.0233 | 16.0233 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 11.956; 10000 Zone 1: 10000; 10000 Zone 2: 10000 | 36.2107 | 18.1053 | 18.1053 |  |  |  | 16.2329 | 8.1164 | 8.1164
[21 empty] | Corrected total cooling after derate | 30.6515 |  |  |  | 9+12 | 24 | 9 | 12 |  |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 21.5 | 9.5 | 12 |  |  |  | 32.0467 | 13.7343 | 18.3124 |  |  |  | 26.901 | 11.956 | 14.945 |  |  |  | 26.901 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 14.945; 10000 Zone 1: 10000; 10000 Zone 2: 13000 | 36.2107 | 15.5189 | 20.6918 |  |  |  | 18.262 | 8.1164 | 10.1456
[21 empty] | Corrected total heating after derate | 35.0982 |  |  |  | 9+18 | 24 | 9 | 18 |  |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 25 | 8.4 | 16.6 |  |  |  | 32.0467 | 10.6822 | 21.3644 |  |  |  | 36.0965 | 11.956 | 24.1404 |  |  |  | 36.5548 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 24.5988; 10000 Zone 1: 9000; 10000 Zone 2: 18000 | 36.2107 | 12.0702 | 24.1404 |  |  |  | 23.4921 | 8.1164 | 15.3756
[26 empty] | 12+12 | 24 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 24 | 12 | 12 |  |  |  | 32.0467 | 16.0233 | 16.0233 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | 14.945 Zone 1: 14.945; 14.945 Zone 2: 14.945; 10000 Zone 1: 13000; 10000 Zone 2: 13000 | 36.2107 | 18.1053 | 18.1053 |  |  |  | 20.2911 | 10.1456 | 10.1456
[26 empty] | 12+18 | 24 | 12 | 18 |  |  |  |  | 32.0467 | 12.8187 | 19.228 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 26 | 10 | 16 |  |  |  | 32.0467 | 12.8187 | 19.228 |  |  |  | 36.2107 | 14.4843 | 21.7264 |  |  |  | 39.5438 | 14.945 Zone 1: 14.945; 14.945 Zone 2: 24.5988; 10000 Zone 1: 11200; 10000 Zone 2: 16800 | 36.2107 | 14.4843 | 21.7264 |  |  |  | 24.8592 | 9.9437 | 14.9155
[26 empty] | 18+18 | 24 | 18 | 18 |  |  |  |  | 32.0467 | 16.0233 | 16.0233 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 28 | 14 | 14 |  |  |  | 32.0467 | 16.0233 | 16.0233 |  |  |  | 36.2107 | 18.1053 | 18.1053 |  |  |  | 49.1976 | 14.945 Zone 1: 24.5988; 14.945 Zone 2: 24.5988; 10000 Zone 1: 15000; 10000 Zone 2: 15000 | 36.2107 | 18.1053 | 18.1053 |  |  |  | 24.8592 | 12.4296 | 12.4296
[26 empty] | 9+9+9 | 24 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 27 | 9 | 9 | 9 |  |  | 32.0467 | 10.6822 | 10.6822 | 10.6822 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 9500 | 9500 | 9500 |  |  | 36.2107 | 12.0702 | 12.0702 | 12.0702 |  |  | 24.3493 | 8.1164 | 8.1164 | 8.1164
[26 empty] | 9+9+12 | 24 | 9 | 9 | 12 |  |  |  | 32.0467 | 9.614 | 9.614 | 12.8187 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 29.001 | 8.667 | 8.667 | 11.667 |  |  | 32.0467 | 9.614 | 9.614 | 12.8187 |  |  | 36.2107 | 10.8632 | 10.8632 | 14.4843 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 9500 | 9500 | 12000 |  |  | 36.2107 | 10.8632 | 10.8632 | 14.4843 |  |  | 24.8592 | 7.4578 | 7.4578 | 9.9437
[26 empty] | 9+9+18 | 24 | 9 | 9 | 18 |  |  |  | 32.0467 | 8.0117 | 8.0117 | 16.0233 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 29.999 | 8.333 | 8.333 | 13.333 |  |  | 32.0467 | 8.0117 | 8.0117 | 16.0233 |  |  | 36.2107 | 9.0527 | 9.0527 | 18.1053 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 9000 | 9000 | 14000 |  |  | 36.2107 | 9.0527 | 9.0527 | 18.1053 |  |  | 24.8592 | 6.2148 | 6.2148 | 12.4296
[26 empty] | 9+12+12 | 24 | 9 | 12 | 12 |  |  |  | 32.0467 | 8.74 | 11.6533 | 11.6533 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 28.5 | 8.5 | 10 | 10 |  |  | 32.0467 | 8.74 | 11.6533 | 11.6533 |  |  | 36.2107 | 9.8756 | 13.1675 | 13.1675 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 8500 | 11500 | 11500 |  |  | 36.2107 | 9.8756 | 13.1675 | 13.1675 |  |  | 24.8592 | 6.7798 | 9.0397 | 9.0397
[26 empty] | 12+12+12 | 24 | 12 | 12 | 12 |  |  |  | 32.0467 | 10.6822 | 10.6822 | 10.6822 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 29.001 | 9.667 | 9.667 | 9.667 |  |  | 32.0467 | 10.6822 | 10.6822 | 10.6822 |  |  | 36.2107 | 12.0702 | 12.0702 | 12.0702 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 10667 | 10667 | 10667 |  |  | 36.2107 | 12.0702 | 12.0702 | 12.0702 |  |  | 24.8592 | 8.2864 | 8.2864 | 8.2864
[26 empty] | 30K | 30 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[26 empty] | 9+9 | 30 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20 | 10 | 10 |  |  |  | 38.8456 | 19.4228 | 19.4228 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | Zone 1: 11.956; Zone 2: 11.956; Zone 1: 10500; Zone 2: 10500 | 37.1299 | 18.565 | 18.565 |  |  |  | 16.7409 | 8.3705 | 8.3705
[26 empty] | 9+12 | 30 | 9 | 12 |  |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 21.5 | 9.5 | 12 |  |  |  | 38.8456 | 16.6481 | 22.1975 |  |  |  | 26.901 | 11.956 | 14.945 |  |  |  | 26.901 | Zone 1: 11.956; Zone 2: 14.945; Zone 1: 10000; Zone 2: 13000 | 37.1299 | 15.9128 | 21.2171 |  |  |  | 18.8335 | 8.3705 | 10.4631
[26 empty] | 9+18 | 30 | 9 | 18 |  |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 38.8456 | 12.9485 | 25.897 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 37.1299 | 12.3766 | 24.7533 |  |  |  | 24.2273 | 8.3705 | 15.8568
| COOLING PERFORMANCE DATA | [24 empty] | 9+24 | 30 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33 | 9 | 24 |  |  |  | 38.8456 | 10.5942 | 28.2513 |  |  |  | 37.1299 | 10.1263 | 27.0036 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 37.1299 | 10.1263 | 27.0036 |  |  |  | 27.9322 | 8.3705 | 19.5617
| Model | Cooling |  |  | Outdoor conditions (DB) | [20 empty] | 12+12 | 30 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 24 | 12 | 12 |  |  |  | 38.8456 | 19.4228 | 19.4228 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 37.1299 | 18.565 | 18.565 |  |  |  | 20.9261 | 10.4631 | 10.4631
|  | Indoor Conditions DB | [23 empty] | 12+18 | 30 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 38.8456 | 15.5382 | 23.3073 |  |  |  | 37.1299 | 14.852 | 22.278 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 18000 | 37.1299 | 14.852 | 22.278 |  |  |  | 26.3199 | 10.4631 | 15.8568
|  | DB | WB |  | -13 | -4 | 0 | 5 | 17 | 47 | 77 | 86 | 95 | 104 | 113 | 122.0001 |  |  |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | CAPACITY |  |  | 12+24 | 30 | 12 | 24 |  |  |  |  | 37.4007 | 12.9485 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 34 | 11 | 23 |  |  |  | 38.8456 | 12.9485 | 25.897 |  |  |  | 37.1299 | 12.3766 | 24.7533 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 12000; Zone 2: 24000 | 37.1299 | 12.3766 | 24.7533 |  |  |  | 29.9205 | 10.3588 | 19.5617
| 18 | 69.8 | 59 | TC | 19.12 | 19.86 | 19.66 | 19.26 | 18.87 | 20.69 | 21.78 | 19.94 | 17.92 | 12 | 11.58 | 9.89 | 17.92 |  |  | INTERPOLATION | 21.2967 | 18 | 21.2967 |  |  | 18+18 | 30 | 18 | 18 |  |  |  |  | 38.8456 | 19.4228 | 19.4228 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 33 | 16.5 | 16.5 |  |  |  | 38.8456 | 19.4228 | 19.4228 |  |  |  | 37.1299 | 18.565 | 18.565 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 17000; Zone 2: 17000 | 37.1299 | 18.565 | 18.565 |  |  |  | 31.0763 | 15.5382 | 15.5382
| 18 | 75.2 | 62.6 | TC | 20.54 | 21.45 | 21.23 | 20.81 | 20.38 | 22.35 | 23.52 | 21.54 | 19.35 | 12.96 | 12.51 | 10.13 | 19.35 | [8 empty] | 9+9+9 | 30 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 27.999 | 9.333 | 9.333 | 9.333 |  |  | 38.8456 | 12.9485 | 12.9485 | 12.9485 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 9667 | 9667 | 9667 |  |  | 37.1299 | 12.3766 | 12.3766 | 12.3766 |  |  | 25.1114 | 8.3705 | 8.3705 | 8.3705
| 18 | 80.6 | 66.2 | TC | 21.91 | 22.46 | 22.18 | 22.53 | 22.85 | 24.15 | 25.11 | 23.85 | 21.54 | 14.82 | 14.22 | 10.4 | 21.54 |  |  | EXTRAPOLATION | 20.9171 |  |  |  |  | 9+9+12 | 30 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 30 | 9 | 9 | 12 |  |  | 38.8456 | 11.6537 | 11.6537 | 15.5382 |  |  | 37.1299 | 11.139 | 11.139 | 14.852 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 9500 | 9500 | 12500 |  |  | 37.1299 | 11.139 | 11.139 | 14.852 |  |  | 27.204 | 8.3705 | 8.3705 | 10.4631
| 18 | 89.6 | 73.4 | TC | 23.89 | 24.48 | 24.18 | 24.56 | 24.91 | 26.32 | 27.37 | 26 | 23.48 | 16.15 | 15.5 | 11.34 | 23.48 | [8 empty] | 9+9+18 | 30 | 9 | 9 | 18 |  |  |  | 38.8456 | 9.7114 | 9.7114 | 19.4228 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 33 | 8.5 | 8.5 | 16 |  |  | 38.8456 | 9.7114 | 9.7114 | 19.4228 |  |  | 37.1299 | 9.2825 | 9.2825 | 18.565 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 8500 | 8500 | 17000 |  |  | 37.1299 | 9.2825 | 9.2825 | 18.565 |  |  | 31.0763 | 7.7691 | 7.7691 | 15.5382
| 24 | 69.8 | 59 | TC | 31.96 | 32.76 | 32.58 | 32.6 | 32.15 | 32.75 | 32.44 | 26.94 | 24.46 | 19.98 | 17.56 | 15.45 | 24.46 |  |  | INTERPOLATION | 32.0467 | 24 | 32.0467 |  |  | 9+9+24 | 30 | 9 | 9 | 24 |  |  |  | 38.8456 | 8.324 | 8.324 | 22.1975 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 35 | 7.5 | 7.5 | 20 |  |  | 38.8456 | 8.324 | 8.324 | 22.1975 |  |  | 37.1299 | 7.9564 | 7.9564 | 21.2171 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 8500 | 8500 | 21000 |  |  | 37.1299 | 7.9564 | 7.9564 | 21.2171 |  |  | 31.0763 | 6.6592 | 6.6592 | 17.7579
| 24 | 75.2 | 62.6 | TC | 34.53 | 35.39 | 35.19 | 35.21 | 34.72 | 35.37 | 35.04 | 29.1 | 26.42 | 21.58 | 18.96 | 16.69 | 26.42 | [8 empty] | 9+12+12 | 30 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 31.5 | 8.5 | 11.5 | 11.5 |  |  | 38.8456 | 10.5942 | 14.1257 | 14.1257 |  |  | 37.1299 | 10.1263 | 13.5018 | 13.5018 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 9000 | 12000 | 12000 |  |  | 37.1299 | 10.1263 | 13.5018 | 13.5018 |  |  | 29.2966 | 8.3705 | 10.4631 | 10.4631
| 24 | 80.6 | 66.2 | TC | 36.25 | 37.15 | 37.24 | 37.08 | 37.51 | 37.68 | 37.53 | 35.39 | 32.75 | 24.71 | 23.96 | 20.15 | 32.75 |  |  | EXTRAPOLATION | 30.3529 |  |  |  |  | 9+12+18 | 30 | 9 | 12 | 18 |  |  |  | 38.8456 | 8.9644 | 11.9525 | 17.9287 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 34 | 8 | 11 | 15 |  |  | 38.8456 | 8.9644 | 11.9525 | 17.9287 |  |  | 37.1299 | 8.5684 | 11.4246 | 17.1369 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 8500 | 11500 | 16000 |  |  | 37.1299 | 8.5684 | 11.4246 | 17.1369 |  |  | 31.0763 | 7.1715 | 9.5619 | 14.3429
| 24 | 89.6 | 73.4 | TC | 38.78 | 39.75 | 39.85 | 39.68 | 40.14 | 40.32 | 40.16 | 37.87 | 35.04 | 26.44 | 25.64 | 21.56 | 35.04 | [8 empty] | 9+12+24 | 30 | 9 | 12 | 24 |  |  |  | 38.8456 | 7.7691 | 10.3588 | 20.7176 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 36 | 7 | 9 | 20 |  |  | 38.8456 | 7.7691 | 10.3588 | 20.7176 |  |  | 37.1299 | 7.426 | 9.9013 | 19.8026 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 8500 | 9500 | 21000 |  |  | 37.1299 | 7.426 | 9.9013 | 19.8026 |  |  | 31.0763 | 6.2153 | 8.287 | 16.574
| 30 | 69.8 | 59 | TC | 39.15 | 40.12 | 40.28 | 39.54 | 39.18 | 40.81 | 39.79 | 37.98 | 36.16 | 28.21 | 26.56 | 23.46 | 36.16 |  |  | INTERPOLATION | 38.8456 | 30 | 38.8456 |  |  | 9+18+18 | 30 | 9 | 18 | 18 |  |  |  | 38.8456 | 7.7691 | 15.5382 | 15.5382 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 36 | 8 | 14 | 14 |  |  | 38.8456 | 7.7691 | 15.5382 | 15.5382 |  |  | 37.1299 | 7.426 | 14.852 | 14.852 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 8500 | 14500 | 14500 |  |  | 37.1299 | 7.426 | 14.852 | 14.852 |  |  | 31.0763 | 6.2153 | 12.4305 | 12.4305
| 30 | 75.2 | 62.6 | TC | 40.32 | 41.32 | 41.49 | 40.73 | 40.36 | 42.03 | 41.38 | 41.02 | 39.05 | 30.47 | 28.68 | 25.34 | 39.05 | [8 empty] | 12+12+12 | 30 | 12 | 12 | 12 |  |  |  | 38.8456 | 12.9485 | 12.9485 | 12.9485 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 33.999 | 11.333 | 11.333 | 11.333 |  |  | 38.8456 | 12.9485 | 12.9485 | 12.9485 |  |  | 37.1299 | 12.3766 | 12.3766 | 12.3766 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 12000 | 12000 | 12000 |  |  | 37.1299 | 12.3766 | 12.3766 | 12.3766 |  |  | 31.0763 | 10.3588 | 10.3588 | 10.3588
| 30 | 80.6 | 66.2 | TC | 41.13 | 42.15 | 42.51 | 42.61 | 42.1 | 42.61 | 42.41 | 40.63 | 38.82 | 32.17 | 30.47 | 27.53 | 38.82 |  |  | EXTRAPOLATION | 39.3082 |  |  |  |  | 12+12+18 | 30 | 12 | 12 | 18 |  |  |  | 38.8456 | 11.0987 | 11.0987 | 16.6481 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 36 | 11 | 11 | 14 |  |  | 38.8456 | 11.0987 | 11.0987 | 16.6481 |  |  | 37.1299 | 10.6086 | 10.6086 | 15.9128 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12000 | 12000 | 15000 |  |  | 37.1299 | 10.6086 | 10.6086 | 15.9128 |  |  | 31.0763 | 8.879 | 8.879 | 13.3184
| 30 | 89.6 | 73.4 | TC | 44.41 | 45.52 | 45.91 | 46.02 | 45.47 | 46.02 | 45.8 | 43.88 | 41.93 | 34.74 | 32.91 | 29.73 | 41.93 | [8 empty] | 12+18+18 | 30 | 12 | 18 | 18 |  |  |  | 38.8456 | 9.7114 | 14.5671 | 14.5671 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 35.999 | 9.333 | 13.333 | 13.333 |  |  | 38.8456 | 9.7114 | 14.5671 | 14.5671 |  |  | 37.1299 | 9.2825 | 13.9237 | 13.9237 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 10000 | 14500 | 14500 |  |  | 37.1299 | 9.2825 | 13.9237 | 13.9237 |  |  | 31.0763 | 7.7691 | 11.6536 | 11.6536
| 36 | 69.8 | 59 | TC | 37.82 | 38.76 | 38.32 | 39.02 | 39.41 | 40.44 | 40.91 | 36.89 | 33.97 | 27.85 | 25.6 | 23.33 | 33.97 |  |  | INTERPOLATION | 40.9567 | 36 | 40.9567 |  |  | 12+12+24 | 30 | 12 | 12 | 24 |  |  |  | 38.8456 | 9.7114 | 9.7114 | 19.4228 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 36 | 8 | 8 | 20 |  |  | 38.8456 | 9.7114 | 9.7114 | 19.4228 |  |  | 37.1299 | 9.2825 | 9.2825 | 18.565 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 9000 | 9000 | 21000 |  |  | 37.1299 | 9.2825 | 9.2825 | 18.565 |  |  | 31.0763 | 7.7691 | 7.7691 | 15.5382
| 36 | 75.2 | 62.6 | TC | 38.96 | 39.93 | 39.47 | 40.19 | 40.59 | 41.65 | 42.54 | 39.84 | 36.69 | 30.07 | 27.65 | 25.2 | 36.69 | [8 empty] | 9+9+9+9 | 30 | 9 | 9 | 9 | 9 |  | 4 | 38.8456 | 9.7114 | 9.7114 | 9.7114 | 9.7114 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 36 | 9 | 9 | 9 | 9 |  | 38.8456 | 9.7114 | 9.7114 | 9.7114 | 9.7114 |  | 37.1299 | 9.2825 | 9.2825 | 9.2825 | 9.2825 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 37.1299 | 9.2825 | 9.2825 | 9.2825 | 9.2825 |  | 31.0763 | 7.7691 | 7.7691 | 7.7691 | 7.7691
| 36 | 80.6 | 66.2 | TC | 42.58 | 43.64 | 43.31 | 44.15 | 44.54 | 45.02 | 45.94 | 43.73 | 41.49 | 34.44 | 31.93 | 27.16 | 41.49 |  |  | EXTRAPOLATION | 39.9149 |  |  |  |  | 9+9+9+12 | 30 | 9 | 9 | 9 | 12 |  |  | 38.8456 | 8.9644 | 8.9644 | 8.9644 | 11.9525 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 36.5 | 8.5 | 8.5 | 8.5 | 11 |  | 38.8456 | 8.9644 | 8.9644 | 8.9644 | 11.9525 |  | 37.1299 | 8.5684 | 8.5684 | 8.5684 | 11.4246 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9000 | 9000 | 9000 | 12000 |  | 37.1299 | 8.5684 | 8.5684 | 8.5684 | 11.4246 |  | 31.0763 | 7.1715 | 7.1715 | 7.1715 | 9.5619
| 36 | 89.6 | 73.4 | TC | 45.98 | 47.13 | 46.78 | 47.68 | 48.1 | 48.63 | 49.61 | 47.23 | 44.8 | 37.2 | 34.48 | 29.34 | 44.8 | [8 empty] | 9+9+9+18 | 30 | 9 | 9 | 9 | 18 |  |  | 38.8456 | 7.7691 | 7.7691 | 7.7691 | 15.5382 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 37 | 8 | 8 | 8 | 13 |  | 38.8456 | 7.7691 | 7.7691 | 7.7691 | 15.5382 |  | 37.1299 | 7.426 | 7.426 | 7.426 | 14.852 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 8500 | 8500 | 8500 | 14000 |  | 37.1299 | 7.426 | 7.426 | 7.426 | 14.852 |  | 31.0763 | 6.2153 | 6.2153 | 6.2153 | 12.4305
| 48 | 69.8 | 59 | TC | 41.22 | 42.25 | 42.51 | 41.87 | 41.24 | 41.97 | 41.47 | 39.32 | 36.26 | 32.97 | 29.86 | 26.54 | 36.26 |  |  | INTERPOLATION | 51.6044 | 48 | 51.6044 |  |  | 9+9+12+12 | 30 | 9 | 9 | 12 | 12 |  |  | 38.8456 | 8.324 | 8.324 | 11.0987 | 11.0987 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 37 | 8 | 8 | 10.5 | 10.5 |  | 38.8456 | 8.324 | 8.324 | 11.0987 | 11.0987 |  | 37.1299 | 7.9564 | 7.9564 | 10.6086 | 10.6086 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 8500 | 8500 | 11000 | 11000 |  | 37.1299 | 7.9564 | 7.9564 | 10.6086 | 10.6086 |  | 31.0763 | 6.6592 | 6.6592 | 8.879 | 8.879
| 48 | 75.2 | 62.6 | TC | 44.52 | 45.63 | 45.91 | 45.22 | 44.54 | 45.33 | 44.79 | 42.47 | 39.16 | 35.61 | 32.25 | 28.66 | 39.16 | [8 empty] | 9+9+12+18 | 30 | 9 | 9 | 12 | 18 |  |  | 38.8456 | 7.2835 | 7.2835 | 9.7114 | 14.5671 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 38 | 7.5 | 7.5 | 9 | 14 |  | 38.8456 | 7.2835 | 7.2835 | 9.7114 | 14.5671 |  | 37.1299 | 6.9619 | 6.9619 | 9.2825 | 13.9237 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 8000 | 8000 | 9500 | 14500 |  | 37.1299 | 6.9619 | 6.9619 | 9.2825 | 13.9237 |  | 31.0763 | 5.8268 | 5.8268 | 7.7691 | 11.6536
| 48 | 80.6 | 66.2 | TC | 53.8 | 55.14 | 54.68 | 55.31 | 56.15 | 56.72 | 60.26 | 56.82 | 53.16 | 40.95 | 38.57 | 35.24 | 53.16 |  |  | EXTRAPOLATION | 47.3976 |  |  |  |  | 9+12+12+12 | 30 | 9 | 12 | 12 | 12 |  |  | 38.8456 | 7.7691 | 10.3588 | 10.3588 | 10.3588 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 37 | 7 | 10 | 10 | 10 |  | 38.8456 | 7.7691 | 10.3588 | 10.3588 | 10.3588 |  | 37.1299 | 7.426 | 9.9013 | 9.9013 | 9.9013 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 8000 | 10500 | 10500 | 10500 |  | 37.1299 | 7.426 | 9.9013 | 9.9013 | 9.9013 |  | 31.0763 | 6.2153 | 8.287 | 8.287 | 8.287
| 48 | 89.6 | 73.4 | TC | 56.49 | 57.9 | 57.41 | 58.08 | 58.96 | 59.56 | 63.27 | 59.66 | 55.82 | 43 | 40.5 | 37.04 | 55.82 | [8 empty] | 12+12+12+12 | 30 | 12 | 12 | 12 | 12 |  |  | 38.8456 | 9.7114 | 9.7114 | 9.7114 | 9.7114 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 38 | 9.5 | 9.5 | 9.5 | 9.5 |  | 38.8456 | 9.7114 | 9.7114 | 9.7114 | 9.7114 |  | 37.1299 | 9.2825 | 9.2825 | 9.2825 | 9.2825 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 10000 | 10000 | 10000 | 10000 |  | 37.1299 | 9.2825 | 9.2825 | 9.2825 | 9.2825 |  | 31.0763 | 7.7691 | 7.7691 | 7.7691 | 7.7691
| 18 | 69.8 | 59 | SC | 15.11 | 15.49 | 15.34 | 15.03 | 14.72 | 16.14 | 17 | 15.95 | 15.23 | 12 | 11.58 | 9.89 | [9 empty] | 36K | 36 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
| 18 | 75.2 | 62.6 | SC | 15.35 | 15.61 | 15.29 | 15.4 | 15.28 | 16.98 | 18.35 | 17.01 | 15.87 | 11.53 | 11.88 | 9.93 | [9 empty] | 9+18 | 36 | 9 | 18 |  |  |  | 2 | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 40.9567 | 13.6522 | 27.3044 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 50.3204 | 16.7735 | 33.5469 |  |  |  | 25.9055 | 8.9503 | 16.9552
| 18 | 80.6 | 66.2 | SC | 16.44 | 16.85 | 16.64 | 18.05 | 17.14 | 18.11 | 18.33 | 17.89 | 16.16 | 14.52 | 14.08 | 10.4 | [9 empty] | 9+24 | 36 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33.5 | 9.5 | 24 |  |  |  | 40.9567 | 11.17 | 29.7867 |  |  |  | 42.246 | 11.956 | 30.29 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 50.3204 | 13.7237 | 36.5966 |  |  |  | 29.867 | 8.9503 | 20.9168
| 18 | 89.6 | 73.4 | SC | 17.2 | 17.63 | 17.65 | 18.17 | 18.68 | 19.22 | 22.44 | 21.84 | 20.19 | 15.18 | 14.88 | 11.11 | [9 empty] | 12+12 | 36 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 25 | 12.5 | 12.5 |  |  |  | 40.9567 | 20.4783 | 20.4783 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 50.3204 | 25.1602 | 25.1602 |  |  |  | 22.3757 | 11.1879 | 11.1879
| 24 | 69.8 | 59 | SC | 22.38 | 22.94 | 22.81 | 22.82 | 22.51 | 22.93 | 25.47 | 22.82 | 21.7 | 19.42 | 17.21 | 15.45 | [9 empty] | 12+18 | 36 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 40.9567 | 16.3827 | 24.574 |  |  |  | 39.5438 | 14.945 | 24.5988 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 19000 | 50.3204 | 20.1282 | 30.1922 |  |  |  | 28.1431 | 11.1879 | 16.9552
| 24 | 75.2 | 62.6 | SC | 24.17 | 24.77 | 24.63 | 24.65 | 24.31 | 24.76 | 26.28 | 23.86 | 22.72 | 19.42 | 18.02 | 16.52 | [9 empty] | 12+24 | 36 | 12 | 24 |  |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 36 | 12 | 24 |  |  |  | 40.9567 | 13.6522 | 27.3044 |  |  |  | 45.235 | 14.945 | 30.29 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 50.3204 | 16.7735 | 33.5469 |  |  |  | 32.1046 | 11.1879 | 20.9168
| 24 | 80.6 | 66.2 | SC | 25.38 | 26.01 | 26.07 | 25.96 | 26.26 | 26.38 | 26.95 | 26.08 | 25.06 | 22.09 | 23.84 | 20.05 | [9 empty] | 18+18 | 36 | 18 | 18 |  |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 37 | 18.5 | 18.5 |  |  |  | 40.9567 | 20.4783 | 20.4783 |  |  |  | 49.1976 | 24.5988 | 24.5988 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 19000; Zone 2: 19000 | 50.3204 | 25.1602 | 25.1602 |  |  |  | 33.9105 | 16.9552 | 16.9552
| 24 | 89.6 | 73.4 | SC | 27.15 | 27.83 | 27.89 | 27.77 | 28.09 | 30.64 | 32.93 | 32.19 | 31.19 | 24.32 | 24.61 | 21.56 | [9 empty] | 18+24 | 36 | 18 | 24 |  |  |  |  | 40.9567 | 17.5529 | 23.4038 |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 40 | 17.5 | 22.5 |  |  |  | 40.9567 | 17.5529 | 23.4038 |  |  |  | 50.3204 | 21.5659 | 28.7545 |  |  |  | 54.8888 | Zone 1: 24.5988; Zone 2: 30.29; Zone 1: 18000; Zone 2: 23000 | 50.3204 | 21.5659 | 28.7545 |  |  |  | 35.0349 | 15.0149 | 20.0199
| 30 | 69.8 | 59 | SC | 27.4 | 28.08 | 28.2 | 27.68 | 27.43 | 30.61 | 31.57 | 30.73 | 29.86 | 26.4 | 26.18 | 23.12 | [9 empty] | 24+24 | 36 | 24 | 24 |  |  |  |  | 40.9567 | 20.4783 | 20.4783 |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 42 | 21 | 21 |  |  |  | 40.9567 | 20.4783 | 20.4783 |  |  |  | 50.3204 | 25.1602 | 25.1602 |  |  |  | 60.58 | Zone 1: 30.29; Zone 2: 30.29; Zone 1: 22000; Zone 2: 22000 | 50.3204 | 25.1602 | 25.1602 |  |  |  | 35.0349 | 17.5174 | 17.5174
| 30 | 75.2 | 62.6 | SC | 28.23 | 28.93 | 29.04 | 28.51 | 28.25 | 31.53 | 33.93 | 36.1 | 35.15 | 28.03 | 27.25 | 24.83 | [9 empty] | 9+9+9 | 36 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 28.5 | 9.5 | 9.5 | 9.5 |  |  | 40.9567 | 13.6522 | 13.6522 | 13.6522 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 11000 | 11000 | 11000 |  |  | 50.3204 | 16.7735 | 16.7735 | 16.7735 |  |  | 26.8509 | 8.9503 | 8.9503 | 8.9503
| 30 | 80.6 | 66.2 | SC | 28.79 | 29.51 | 29.76 | 29.83 | 29.47 | 31.96 | 32.3 | 31.45 | 30.57 | 28.3 | 30.18 | 27.25 | [9 empty] | 9+9+12 | 36 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 31 | 9.5 | 9.5 | 12 |  |  | 40.9567 | 12.287 | 12.287 | 16.3827 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 10500 | 10500 | 13000 |  |  | 50.3204 | 15.0961 | 15.0961 | 20.1282 |  |  | 29.0884 | 8.9503 | 8.9503 | 11.1879
| 30 | 89.6 | 73.4 | SC | 31.1 | 31.87 | 32.14 | 32.21 | 31.83 | 34.51 | 37.56 | 38.61 | 37.73 | 31.96 | 31.26 | 29.73 | [9 empty] | 9+9+18 | 36 | 9 | 9 | 18 |  |  |  | 40.2994 | 10.2392 | 10.2392 | 19.8211 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 37 | 9.5 | 9.5 | 18 |  |  | 40.9567 | 10.2392 | 10.2392 | 20.4783 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 10000 | 10000 | 19000 |  |  | 50.3204 | 12.5801 | 12.5801 | 25.1602 |  |  | 34.4727 | 8.7587 | 8.7587 | 16.9552
| 36 | 69.8 | 59 | SC | 26.47 | 27.13 | 26.82 | 27.31 | 28.38 | 30.33 | 31.91 | 30.25 | 28.88 | 24.5 | 23.55 | 22.4 | [9 empty] | 9+9+24 | 36 | 9 | 9 | 24 |  |  |  | 40.9567 | 8.7764 | 8.7764 | 23.4038 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 40.5 | 9 | 9 | 22.5 |  |  | 40.9567 | 8.7764 | 8.7764 | 23.4038 |  |  | 50.3204 | 10.7829 | 10.7829 | 28.7545 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 9500 | 9500 | 23500 |  |  | 50.3204 | 10.7829 | 10.7829 | 28.7545 |  |  | 35.0349 | 7.5075 | 7.5075 | 20.0199
| 36 | 75.2 | 62.6 | SC | 27.27 | 27.95 | 27.63 | 28.13 | 28.42 | 31.24 | 34.88 | 35.06 | 33.02 | 27.67 | 26.26 | 24.69 | [9 empty] | 9+12+12 | 36 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 34.5 | 9.5 | 12.5 | 12.5 |  |  | 40.9567 | 11.17 | 14.8933 | 14.8933 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 10000 | 12500 | 12500 |  |  | 50.3204 | 13.7237 | 18.2983 | 18.2983 |  |  | 31.326 | 8.9503 | 11.1879 | 11.1879
| 36 | 80.6 | 66.2 | SC | 29.81 | 30.55 | 30.32 | 30.91 | 31.18 | 33.77 | 35.83 | 34.99 | 35.26 | 31 | 30.33 | 26.62 | [9 empty] | 9+12+18 | 36 | 9 | 12 | 18 |  |  |  | 40.9567 | 9.4515 | 12.6021 | 18.9031 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 39 | 9 | 12 | 18 |  |  | 40.9567 | 9.4515 | 12.6021 | 18.9031 |  |  | 49.7822 | 11.6124 | 14.945 | 23.2248 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 9500 | 12500 | 18000 |  |  | 50.3204 | 11.6124 | 15.4832 | 23.2248 |  |  | 35.0349 | 8.085 | 10.78 | 16.1699
| 36 | 89.6 | 73.4 | SC | 32.19 | 32.99 | 32.74 | 33.38 | 33.67 | 36.47 | 40.68 | 41.56 | 40.32 | 34.22 | 32.76 | 29.34 | [9 empty] | 9+12+24 | 36 | 9 | 12 | 24 |  |  |  | 40.9567 | 8.1913 | 10.9218 | 21.8436 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 42.5 | 9 | 12 | 21.5 |  |  | 40.9567 | 8.1913 | 10.9218 | 21.8436 |  |  | 50.3204 | 10.0641 | 13.4188 | 26.8375 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 9500 | 12500 | 22000 |  |  | 50.3204 | 10.0641 | 13.4188 | 26.8375 |  |  | 35.0349 | 7.007 | 9.3426 | 18.6853
| 48 | 69.8 | 59 | SC | 28.86 | 29.58 | 29.76 | 29.31 | 28.87 | 30.64 | 37.24 | 36.86 | 35.53 | 32.97 | 29.86 | 26.54 | [9 empty] | 9+18+18 | 36 | 9 | 18 | 18 |  |  |  | 40.9567 | 8.1913 | 16.3827 | 16.3827 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 45 | 9 | 18 | 18 |  |  | 40.9567 | 8.1913 | 16.3827 | 16.3827 |  |  | 50.3204 | 10.0641 | 20.1282 | 20.1282 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 9500 | 18500 | 18500 |  |  | 50.3204 | 10.0641 | 20.1282 | 20.1282 |  |  | 35.0349 | 7.007 | 14.014 | 14.014
| 48 | 75.2 | 62.6 | SC | 32.5 | 33.31 | 33.51 | 33.01 | 32.51 | 34.9 | 37.17 | 36.1 | 34.07 | 32.05 | 32.25 | 28.66 | [9 empty] | 9+18+24 | 36 | 9 | 18 | 24 |  |  |  | 40.9567 | 7.2276 | 14.4553 | 19.2737 |  |  | 54.7364 | 10.4631 | 19.8211 | 24.4522 |  |  | 46 | 8.5 | 16 | 21.5 |  |  | 40.9567 | 7.2276 | 14.4553 | 19.2737 |  |  | 50.3204 | 8.8801 | 17.7601 | 23.6802 |  |  | 66.8448 | 11.956 | 24.5988 | 30.29 |  |  | 9000 | 17000 | 22000 |  |  | 50.3204 | 8.8801 | 17.7601 | 23.6802 |  |  | 35.0349 | 6.1826 | 12.3653 | 16.487
| 48 | 80.6 | 66.2 | SC | 40.35 | 41.36 | 41.01 | 42.12 | 42.11 | 42.54 | 46.04 | 44.49 | 42.79 | 37.95 | 38.57 | 35.24 | [9 empty] | 9+24+24 | 36 | 9 | 24 | 24 |  |  |  | 40.9567 | 6.4668 | 17.2449 | 17.2449 |  |  | 59.3676 | 10.4631 | 24.4522 | 24.4522 |  |  | 48 | 8 | 20 | 20 |  |  | 40.9567 | 6.4668 | 17.2449 | 17.2449 |  |  | 50.3204 | 7.9453 | 21.1875 | 21.1875 |  |  | 72.536 | 11.956 | 30.29 | 30.29 |  |  | 8500 | 21000 | 21000 |  |  | 50.3204 | 7.9453 | 21.1875 | 21.1875 |  |  | 35.0349 | 5.5318 | 14.7515 | 14.7515
| 48 | 89.6 | 73.4 | SC | 41.8 | 42.84 | 42.49 | 42.98 | 43.63 | 46.45 | 52.52 | 51.31 | 50.24 | 40.85 | 40.5 | 37.04 | [9 empty] | 12+12+12 | 36 | 12 | 12 | 12 |  |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 36 | 12 | 12 | 12 |  |  | 40.9567 | 13.6522 | 13.6522 | 13.6522 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 13000 | 13000 | 13000 |  |  | 50.3204 | 16.7735 | 16.7735 | 16.7735 |  |  | 33.5636 | 11.1879 | 11.1879 | 11.1879
| 18 | 69.8 | 59 | SCR | 79.03% | 78% | 78.03% | 78.04% | 78.01% | 78.01% | 78.05% | 79.99% | 84.99% | 100% | 100% | 100% | 84.99% |  |  | INTERPOLATION | 75.8% | 18 | 75.8% |  |  | 12+12+18 | 36 | 12 | 12 | 18 |  |  |  | 40.9567 | 11.7019 | 11.7019 | 17.5529 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 41 | 12 | 12 | 17 |  |  | 40.9567 | 11.7019 | 11.7019 | 17.5529 |  |  | 50.3204 | 14.3773 | 14.3773 | 21.5659 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12500 | 12500 | 18000 |  |  | 50.3204 | 14.3773 | 14.3773 | 21.5659 |  |  | 35.0349 | 10.01 | 10.01 | 15.0149
| 18 | 75.2 | 62.6 | SCR | 74.73% | 72.77% | 72.02% | 74% | 74.98% | 75.97% | 78.02% | 78.97% | 82.02% | 88.97% | 94.96% | 98.03% | 82.02% | [8 empty] | 12+12+24 | 36 | 12 | 12 | 24 |  |  |  | 40.9567 | 10.2392 | 10.2392 | 20.4783 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 44 | 11 | 11 | 22 |  |  | 40.9567 | 10.2392 | 10.2392 | 20.4783 |  |  | 50.3204 | 12.5801 | 12.5801 | 25.1602 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 11500 | 11500 | 23000 |  |  | 50.3204 | 12.5801 | 12.5801 | 25.1602 |  |  | 35.0349 | 8.7587 | 8.7587 | 17.5174
| 18 | 80.6 | 66.2 | SCR | 75.03% | 75.02% | 75.02% | 80.12% | 75.01% | 74.99% | 73% | 75.01% | 75.02% | 97.98% | 99.02% | 100% | 75.02% |  |  | EXTRAPOLATION | 82.02% |  |  |  |  | 12+18+18 | 36 | 12 | 18 | 18 |  |  |  | 40.9567 | 10.2392 | 15.3587 | 15.3587 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 44 | 11 | 16.5 | 16.5 |  |  | 40.9567 | 10.2392 | 15.3587 | 15.3587 |  |  | 50.3204 | 12.5801 | 18.8701 | 18.8701 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 11500 | 17000 | 17000 |  |  | 50.3204 | 12.5801 | 18.8701 | 18.8701 |  |  | 35.0349 | 8.7587 | 13.1381 | 13.1381
| 18 | 89.6 | 73.4 | SCR | 72% | 72.02% | 72.99% | 73.98% | 74.99% | 73.02% | 81.99% | 84% | 85.99% | 93.99% | 96% | 97.97% | 85.99% | [8 empty] | 12+18+24 | 36 | 12 | 18 | 24 |  |  |  | 40.9567 | 9.1015 | 13.6522 | 18.203 |  |  | 57.3522 | 13.0789 | 19.8211 | 24.4522 |  |  | 47.5 | 10.5 | 15.5 | 21.5 |  |  | 40.9567 | 9.1015 | 13.6522 | 18.203 |  |  | 50.3204 | 11.1823 | 16.7735 | 22.3646 |  |  | 69.8338 | 14.945 | 24.5988 | 30.29 |  |  | 11000 | 16000 | 22000 |  |  | 50.3204 | 11.1823 | 16.7735 | 22.3646 |  |  | 35.0349 | 7.7855 | 11.6783 | 15.5711
| 24 | 69.8 | 59 | SCR | 70.03% | 70.02% | 70.01% | 70% | 70.02% | 70.02% | 78.51% | 84.71% | 88.72% | 97.2% | 98.01% | 100% | 88.72% |  |  | INTERPOLATION | 77.57% | 24 | 77.57% |  |  | 12+24+24 | 36 | 12 | 24 | 24 |  |  |  | 40.9567 | 8.1913 | 16.3827 | 16.3827 |  |  | 61.9833 | 13.0789 | 24.4522 | 24.4522 |  |  | 50 | 10 | 20 | 20 |  |  | 40.9567 | 8.1913 | 16.3827 | 16.3827 |  |  | 50.3204 | 10.0641 | 20.1282 | 20.1282 |  |  | 75.525 | 14.945 | 30.29 | 30.29 |  |  | 11000 | 20500 | 20500 |  |  | 50.3204 | 10.0641 | 20.1282 | 20.1282 |  |  | 35.0349 | 7.007 | 14.014 | 14.014
| 24 | 75.2 | 62.6 | SCR | 70% | 69.99% | 69.99% | 70.01% | 70.02% | 70% | 75% | 81.99% | 86% | 89.99% | 95.04% | 98.98% | 86% | [8 empty] | 18+18+18 | 36 | 18 | 18 | 18 |  |  |  | 40.9567 | 13.6522 | 13.6522 | 13.6522 |  |  | 59.4633 | 19.8211 | 19.8211 | 19.8211 |  |  | 48 | 16 | 16 | 16 |  |  | 40.9567 | 13.6522 | 13.6522 | 13.6522 |  |  | 50.3204 | 16.7735 | 16.7735 | 16.7735 |  |  | 73.7965 | 24.5988 | 24.5988 | 24.5988 |  |  | 16500 | 16500 | 16500 |  |  | 50.3204 | 16.7735 | 16.7735 | 16.7735 |  |  | 35.0349 | 11.6783 | 11.6783 | 11.6783
| 24 | 80.6 | 66.2 | SCR | 70.01% | 70.01% | 70.01% | 70.01% | 70.01% | 70.01% | 71.81% | 73.69% | 76.52% | 89.4% | 99.5% | 99.5% | 76.52% |  |  | EXTRAPOLATION | 85.01% |  |  |  |  | 18+18+24 | 36 | 18 | 18 | 24 |  |  |  | 40.9567 | 12.287 | 12.287 | 16.3827 |  |  | 64.0944 | 19.8211 | 19.8211 | 24.4522 |  |  | 50 | 15 | 15 | 20 |  |  | 40.9567 | 12.287 | 12.287 | 16.3827 |  |  | 50.3204 | 15.0961 | 15.0961 | 20.1282 |  |  | 79.4876 | 24.5988 | 24.5988 | 30.29 |  |  | 15500 | 15500 | 21000 |  |  | 50.3204 | 15.0961 | 15.0961 | 20.1282 |  |  | 35.0349 | 10.5105 | 10.5105 | 14.014
| 24 | 89.6 | 73.4 | SCR | 70.01% | 70.01% | 69.99% | 69.98% | 69.98% | 75.99% | 82% | 85% | 89.01% | 91.98% | 95.98% | 100% | 89.01% | [8 empty] | 9+9+9+9 | 36 | 9 | 9 | 9 | 9 |  | 4 | 40.9567 | 10.2392 | 10.2392 | 10.2392 | 10.2392 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 37 | 9.25 | 9.25 | 9.25 | 9.25 |  | 40.9567 | 10.2392 | 10.2392 | 10.2392 | 10.2392 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 50.3204 | 12.5801 | 12.5801 | 12.5801 | 12.5801 |  | 35.0349 | 8.7587 | 8.7587 | 8.7587 | 8.7587
| 30 | 69.8 | 59 | SCR | 69.99% | 69.99% | 70.01% | 70.01% | 70.01% | 75.01% | 79.34% | 80.91% | 82.58% | 93.58% | 98.57% | 98.55% | 82.58% |  |  | INTERPOLATION | 80% | 30 | 80% |  |  | 9+9+9+12 | 36 | 9 | 9 | 9 | 12 |  |  | 40.9567 | 9.4515 | 9.4515 | 9.4515 | 12.6021 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 39 | 9 | 9 | 9 | 12 |  | 40.9567 | 9.4515 | 9.4515 | 9.4515 | 12.6021 |  | 49.7822 | 11.6124 | 11.6124 | 11.6124 | 14.945 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9500 | 9500 | 9500 | 12500 |  | 50.3204 | 11.6124 | 11.6124 | 11.6124 | 15.4832 |  | 35.0349 | 8.085 | 8.085 | 8.085 | 10.78
| 30 | 75.2 | 62.6 | SCR | 70.01% | 70.01% | 69.99% | 70% | 70% | 75.02% | 82% | 88.01% | 90.01% | 91.99% | 95.01% | 97.99% | 90.01% | [8 empty] | 9+9+9+18 | 36 | 9 | 9 | 9 | 18 |  |  | 40.9567 | 8.1913 | 8.1913 | 8.1913 | 16.3827 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 44 | 9 | 9 | 9 | 17 |  | 40.9567 | 8.1913 | 8.1913 | 8.1913 | 16.3827 |  | 50.3204 | 10.0641 | 10.0641 | 10.0641 | 20.1282 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 9500 | 9500 | 9500 | 17500 |  | 50.3204 | 10.0641 | 10.0641 | 10.0641 | 20.1282 |  | 35.0349 | 7.007 | 7.007 | 7.007 | 14.014
| 30 | 80.6 | 66.2 | SCR | 70% | 70.01% | 70.01% | 70.01% | 70% | 75.01% | 76.16% | 77.41% | 78.75% | 87.97% | 99.05% | 98.98% | 78.75% |  |  | EXTRAPOLATION | 85.59% |  |  |  |  | 9+9+9+24 | 36 | 9 | 9 | 9 | 24 |  |  | 40.9567 | 7.2276 | 7.2276 | 7.2276 | 19.2737 |  | 55.8416 | 10.4631 | 10.4631 | 10.4631 | 24.4522 |  | 46 | 8.5 | 8.5 | 8.5 | 20.5 |  | 40.9567 | 7.2276 | 7.2276 | 7.2276 | 19.2737 |  | 50.3204 | 8.8801 | 8.8801 | 8.8801 | 23.6802 |  | 66.1581 | 11.956 | 11.956 | 11.956 | 30.29 |  | 9000 | 9000 | 9000 | 21000 |  | 50.3204 | 8.8801 | 8.8801 | 8.8801 | 23.6802 |  | 35.0349 | 6.1826 | 6.1826 | 6.1826 | 16.487
| 30 | 89.6 | 73.4 | SCR | 70.03% | 70.01% | 70.01% | 69.99% | 70% | 74.99% | 82.01% | 87.99% | 89.98% | 92% | 94.99% | 100% | 89.98% | [8 empty] | 9+9+12+12 | 36 | 9 | 9 | 12 | 12 |  |  | 40.9567 | 8.7764 | 8.7764 | 11.7019 | 11.7019 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 42 | 9 | 9 | 12 | 12 |  | 40.9567 | 8.7764 | 8.7764 | 11.7019 | 11.7019 |  | 50.3204 | 10.7829 | 10.7829 | 14.3773 | 14.3773 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 9500 | 9500 | 13000 | 13000 |  | 50.3204 | 10.7829 | 10.7829 | 14.3773 | 14.3773 |  | 35.0349 | 7.5075 | 7.5075 | 10.01 | 10.01
| 36 | 69.8 | 59 | SCR | 69.99% | 69.99% | 69.99% | 69.99% | 72.01% | 75% | 78% | 82% | 85.02% | 87.97% | 91.99% | 96.01% | 85.02% |  |  | INTERPOLATION | 85.54% | 36 | 85.54% |  |  | 9+9+12+18 | 36 | 9 | 9 | 12 | 18 |  |  | 40.9567 | 7.6794 | 7.6794 | 10.2392 | 15.3587 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 45 | 9 | 9 | 10.5 | 16.5 |  | 40.9567 | 7.6794 | 7.6794 | 10.2392 | 15.3587 |  | 50.3204 | 9.4351 | 9.4351 | 12.5801 | 18.8701 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 9500 | 9500 | 11500 | 17500 |  | 50.3204 | 9.4351 | 9.4351 | 12.5801 | 18.8701 |  | 35.0349 | 6.569 | 6.569 | 8.7587 | 13.1381
| 36 | 75.2 | 62.6 | SCR | 69.99% | 70% | 70% | 69.99% | 70.02% | 75.01% | 81.99% | 88% | 90% | 92.02% | 94.97% | 97.98% | 90% | [8 empty] | 9+9+12+24 | 36 | 9 | 9 | 12 | 24 |  |  | 40.9567 | 6.8261 | 6.8261 | 9.1015 | 18.203 |  | 58.4573 | 10.4631 | 10.4631 | 13.0789 | 24.4522 |  | 48 | 8.5 | 8.5 | 10.5 | 20.5 |  | 40.9567 | 6.8261 | 6.8261 | 9.1015 | 18.203 |  | 50.3204 | 8.3867 | 8.3867 | 11.1823 | 22.3646 |  | 69.1471 | 11.956 | 11.956 | 14.945 | 30.29 |  | 9000 | 9000 | 11000 | 21000 |  | 50.3204 | 8.3867 | 8.3867 | 11.1823 | 22.3646 |  | 35.0349 | 5.8391 | 5.8391 | 7.7855 | 15.5711
| 36 | 80.6 | 66.2 | SCR | 70.01% | 70% | 70.01% | 70.01% | 70% | 75.01% | 77.99% | 80.01% | 84.98% | 90.01% | 94.99% | 98.01% | 84.98% |  |  | EXTRAPOLATION | 87.7% |  |  |  |  | 9+9+18+18 | 36 | 9 | 9 | 18 | 18 |  |  | 40.9567 | 6.8261 | 6.8261 | 13.6522 | 13.6522 |  | 60.5684 | 10.4631 | 10.4631 | 19.8211 | 19.8211 |  | 48 | 8.5 | 8.5 | 15.5 | 15.5 |  | 40.9567 | 6.8261 | 6.8261 | 13.6522 | 13.6522 |  | 50.3204 | 8.3867 | 8.3867 | 16.7735 | 16.7735 |  | 73.1097 | 11.956 | 11.956 | 24.5988 | 24.5988 |  | 9000 | 9000 | 16000 | 16000 |  | 50.3204 | 8.3867 | 8.3867 | 16.7735 | 16.7735 |  | 35.0349 | 5.8391 | 5.8391 | 11.6783 | 11.6783
| 36 | 89.6 | 73.4 | SCR | 70.01% | 70% | 69.99% | 70.01% | 70% | 74.99% | 82% | 87.99% | 90% | 91.99% | 95.01% | 100% | 90% | [8 empty] | 9+9+18+24 | 36 | 9 | 9 | 18 | 24 |  |  | 40.9567 | 6.1435 | 6.1435 | 12.287 | 16.3827 |  | 65.1996 | 10.4631 | 10.4631 | 19.8211 | 24.4522 |  | 50.5 | 8 | 8 | 14.5 | 20 |  | 40.9567 | 6.1435 | 6.1435 | 12.287 | 16.3827 |  | 50.3204 | 7.5481 | 7.5481 | 15.0961 | 20.1282 |  | 78.8009 | 11.956 | 11.956 | 24.5988 | 30.29 |  | 8500 | 8500 | 15000 | 20000 |  | 50.3204 | 7.5481 | 7.5481 | 15.0961 | 20.1282 |  | 35.0349 | 5.2552 | 5.2552 | 10.5105 | 14.014
| 48 | 69.8 | 59 | SCR | 70.01% | 70.01% | 70.01% | 70% | 70% | 73% | 89.8% | 93.74% | 97.99% | 100% | 100% | 100% | 97.99% |  |  | INTERPOLATION | 81.22% | 48 | 81.22% |  |  | 9+12+12+12 | 36 | 9 | 12 | 12 | 12 |  |  | 40.9567 | 8.1913 | 10.9218 | 10.9218 | 10.9218 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 45 | 9 | 12 | 12 | 12 |  | 40.9567 | 8.1913 | 10.9218 | 10.9218 | 10.9218 |  | 50.3204 | 10.0641 | 13.4188 | 13.4188 | 13.4188 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 9500 | 12500 | 12500 | 12500 |  | 50.3204 | 10.0641 | 13.4188 | 13.4188 | 13.4188 |  | 35.0349 | 7.007 | 9.3426 | 9.3426 | 9.3426
| 48 | 75.2 | 62.6 | SCR | 73% | 73% | 72.99% | 73% | 72.99% | 76.99% | 82.99% | 85% | 87% | 90% | 100% | 100% | 87% | [8 empty] | 9+12+12+18 | 36 | 9 | 12 | 12 | 18 |  |  | 40.9567 | 7.2276 | 9.6369 | 9.6369 | 14.4553 |  | 56.442 | 10.4631 | 13.0789 | 13.0789 | 19.8211 |  | 46 | 9 | 10.5 | 10.5 | 16 |  | 40.9567 | 7.2276 | 9.6369 | 9.6369 | 14.4553 |  | 50.3204 | 8.8801 | 11.8401 | 11.8401 | 17.7601 |  | 66.4449 | 11.956 | 14.945 | 14.945 | 24.5988 |  | 9500 | 11500 | 11500 | 16500 |  | 50.3204 | 8.8801 | 11.8401 | 11.8401 | 17.7601 |  | 35.0349 | 6.1826 | 8.2435 | 8.2435 | 12.3653
| 48 | 80.6 | 66.2 | SCR | 75% | 75.01% | 75% | 76.15% | 75% | 75% | 76.4% | 78.3% | 80.49% | 92.67% | 100% | 100% | 80.49% |  |  | EXTRAPOLATION | 88.43% |  |  |  |  | 9+12+12+24 | 36 | 9 | 12 | 12 | 24 |  |  | 40.9567 | 6.4668 | 8.6225 | 8.6225 | 17.2449 |  | 61.0731 | 10.4631 | 13.0789 | 13.0789 | 24.4522 |  | 48.5 | 8.5 | 10 | 10 | 20 |  | 40.9567 | 6.4668 | 8.6225 | 8.6225 | 17.2449 |  | 50.3204 | 7.9453 | 10.5938 | 10.5938 | 21.1875 |  | 72.1361 | 11.956 | 14.945 | 14.945 | 30.29 |  | 9000 | 10500 | 10500 | 20500 |  | 50.3204 | 7.9453 | 10.5938 | 10.5938 | 21.1875 |  | 35.0349 | 5.5318 | 7.3758 | 7.3758 | 14.7515
| 48 | 89.6 | 73.4 | SCR | 74% | 73.99% | 74.01% | 74% | 74% | 77.99% | 83.01% | 86% | 90% | 95% | 100% | 100% | 90% | [8 empty] | 9+12+18+18 | 36 | 9 | 12 | 18 | 18 |  |  | 40.9567 | 6.4668 | 8.6225 | 12.9337 | 12.9337 |  | 63.1842 | 10.4631 | 13.0789 | 19.8211 | 19.8211 |  | 48.5 | 8.5 | 10 | 15 | 15 |  | 40.9567 | 6.4668 | 8.6225 | 12.9337 | 12.9337 |  | 50.3204 | 7.9453 | 10.5938 | 15.8907 | 15.8907 |  | 76.0987 | 11.956 | 14.945 | 24.5988 | 24.5988 |  | 9000 | 10500 | 15500 | 15500 |  | 50.3204 | 7.9453 | 10.5938 | 15.8907 | 15.8907 |  | 35.0349 | 5.5318 | 7.3758 | 11.0636 | 11.0636
| 18 | 69.8 | 59 | Input | 1.37 | 1.41 | 1.48 | 1.53 | 1.57 | 1.6 | 1.63 | 1.79 | 1.96 | 1.47 | 1.52 | 1.32 | [9 empty] | 9+18+18+18 | 36 | 9 | 18 | 18 | 18 |  |  | 40.9567 | 5.851 | 11.7019 | 11.7019 | 11.7019 |  | 69.9264 | 10.4631 | 19.8211 | 19.8211 | 19.8211 |  | 50 | 8 | 14 | 14 | 14 |  | 40.9567 | 5.851 | 11.7019 | 11.7019 | 11.7019 |  | 50.3204 | 7.1886 | 14.3773 | 14.3773 | 14.3773 |  | 85.7525 | 11.956 | 24.5988 | 24.5988 | 24.5988 |  | 8500 | 14500 | 14500 | 14500 |  | 50.3204 | 7.1886 | 14.3773 | 14.3773 | 14.3773 |  | 35.0349 | 5.005 | 10.01 | 10.01 | 10.01
| 18 | 75.2 | 62.6 | Input | 1.4 | 1.46 | 1.53 | 1.58 | 1.62 | 1.65 | 1.68 | 1.84 | 2.01 | 1.5 | 1.54 | 1.35 | [9 empty] | 12+12+12+12 | 36 | 12 | 12 | 12 | 12 |  |  | 40.9567 | 10.2392 | 10.2392 | 10.2392 | 10.2392 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 48 | 12 | 12 | 12 | 12 |  | 40.9567 | 10.2392 | 10.2392 | 10.2392 | 10.2392 |  | 50.3204 | 12.5801 | 12.5801 | 12.5801 | 12.5801 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 12500 | 12500 | 12500 | 12500 |  | 50.3204 | 12.5801 | 12.5801 | 12.5801 | 12.5801 |  | 35.0349 | 8.7587 | 8.7587 | 8.7587 | 8.7587
| 18 | 80.6 | 66.2 | Input | 1.41 | 1.45 | 1.51 | 1.58 | 1.62 | 1.65 | 1.68 | 1.88 | 2.05 | 1.52 | 1.57 | 1.36 | [9 empty] | 12+12+12+18 | 36 | 12 | 12 | 12 | 18 |  |  | 40.9567 | 9.1015 | 9.1015 | 9.1015 | 13.6522 |  | 59.0578 | 13.0789 | 13.0789 | 13.0789 | 19.8211 |  | 49 | 11 | 11 | 11 | 16 |  | 40.9567 | 9.1015 | 9.1015 | 9.1015 | 13.6522 |  | 50.3204 | 11.1823 | 11.1823 | 11.1823 | 16.7735 |  | 69.4339 | 14.945 | 14.945 | 14.945 | 24.5988 |  | 11500 | 11500 | 11500 | 16500 |  | 50.3204 | 11.1823 | 11.1823 | 11.1823 | 16.7735 |  | 35.0349 | 7.7855 | 7.7855 | 7.7855 | 11.6783
| 18 | 89.6 | 73.4 | Input | 1.46 | 1.5 | 1.56 | 1.63 | 1.67 | 1.72 | 1.73 | 1.93 | 2.14 | 1.57 | 1.62 | 1.41 | [9 empty] | 12+12+12+24 | 36 | 12 | 12 | 12 | 24 |  |  | 40.9567 | 8.1913 | 8.1913 | 8.1913 | 16.3827 |  | 63.6889 | 13.0789 | 13.0789 | 13.0789 | 24.4522 |  | 50 | 10 | 10 | 10 | 20 |  | 40.9567 | 8.1913 | 8.1913 | 8.1913 | 16.3827 |  | 50.3204 | 10.0641 | 10.0641 | 10.0641 | 20.1282 |  | 75.1251 | 14.945 | 14.945 | 14.945 | 30.29 |  | 10500 | 10500 | 10500 | 20500 |  | 50.3204 | 10.0641 | 10.0641 | 10.0641 | 20.1282 |  | 35.0349 | 7.007 | 7.007 | 7.007 | 14.014
| 24 | 69.8 | 59 | Input | 2.26 | 2.32 | 2.31 | 2.34 | 2.36 | 2.38 | 2.41 | 2.26 | 2.5 | 2.39 | 2.58 | 2.62 | [9 empty] | 12+12+18+18 | 36 | 12 | 12 | 18 | 18 |  |  | 40.9567 | 8.1913 | 8.1913 | 12.287 | 12.287 |  | 65.8 | 13.0789 | 13.0789 | 19.8211 | 19.8211 |  | 50 | 10 | 10 | 15 | 15 |  | 40.9567 | 8.1913 | 8.1913 | 12.287 | 12.287 |  | 50.3204 | 10.0641 | 10.0641 | 15.0961 | 15.0961 |  | 79.0877 | 14.945 | 14.945 | 24.5988 | 24.5988 |  | 10500 | 10500 | 15500 | 15500 |  | 50.3204 | 10.0641 | 10.0641 | 15.0961 | 15.0961 |  | 35.0349 | 7.007 | 7.007 | 10.5105 | 10.5105
| 24 | 75.2 | 62.6 | Input | 2.3 | 2.36 | 2.35 | 2.38 | 2.4 | 2.42 | 2.45 | 2.3 | 2.54 | 2.43 | 2.6 | 2.66 | [9 empty] | 48K | 48 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
| 24 | 80.6 | 66.2 | Input | 2.2 | 2.25 | 2.28 | 2.34 | 2.35 | 2.41 | 2.47 | 2.75 | 3.04 | 2.48 | 2.62 | 2.74 |  | 1 | Match outdoor size | [6 empty] | 9+18 | 48 | 9 | 18 |  |  |  | 2 | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 51.6044 | 17.2015 | 34.403 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 55.8364 | 18.6121 | 37.2243 |  |  |  | 24.5957 | 8.4977 | 16.0979
| 24 | 89.6 | 73.4 | Input | 2.26 | 2.32 | 2.35 | 2.38 | 2.42 | 2.48 | 2.54 | 2.82 | 3.11 | 2.55 | 2.69 | 2.81 |  | 2 | Interpolate & Extrapolate based on indoor and outdoor conditions | [6 empty] | 9+24 | 48 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33.5 | 9.5 | 24 |  |  |  | 51.6044 | 14.0739 | 37.5305 |  |  |  | 42.246 | 11.956 | 30.29 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 55.8364 | 15.2281 | 40.6083 |  |  |  | 28.3569 | 8.4977 | 19.8591
| 30 | 69.8 | 59 | Input | 3.08 | 3.16 | 3.18 | 3.12 | 3.21 | 3.24 | 3.28 | 3.62 | 3.99 | 3.13 | 3.25 | 2.66 |  | 3 | Derate for altitude | [6 empty] | 12+12 | 48 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 25 | 12.5 | 12.5 |  |  |  | 51.6044 | 25.8022 | 25.8022 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 55.8364 | 27.9182 | 27.9182 |  |  |  | 21.2443 | 10.6222 | 10.6222
| 30 | 75.2 | 62.6 | Input | 3.13 | 3.21 | 3.23 | 3.17 | 3.26 | 3.29 | 3.33 | 3.67 | 4.04 | 3.18 | 3.3 | 2.71 |  | 4 | Derate for piping | [6 empty] | 12+18 | 48 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 51.6044 | 20.6418 | 30.9627 |  |  |  | 39.5438 | 14.945 | 24.5988 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 19000 | 55.8364 | 22.3346 | 33.5019 |  |  |  | 26.7201 | 10.6222 | 16.0979
| 30 | 80.6 | 66.2 | Input | 3.13 | 3.21 | 3.25 | 3.29 | 3.31 | 3.38 | 3.42 | 3.67 | 4.05 | 3.21 | 3.31 | 2.76 |  | 5 | Divide by number of units in the system | [6 empty] | 12+24 | 48 | 12 | 24 |  |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 36 | 12 | 24 |  |  |  | 51.6044 | 17.2015 | 34.403 |  |  |  | 45.235 | 14.945 | 30.29 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 12500; Zone 2: 25000 | 55.8364 | 18.6121 | 37.2243 |  |  |  | 30.4813 | 10.6222 | 19.8591
| 30 | 89.6 | 73.4 | Input | 3.19 | 3.27 | 3.31 | 3.35 | 3.37 | 3.44 | 3.48 | 3.73 | 4.11 | 3.27 | 3.37 | 2.82 |  | 6 | Calculate per indoor | [6 empty] | 18+18 | 48 | 18 | 18 |  |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 37 | 18.5 | 18.5 |  |  |  | 51.6044 | 25.8022 | 25.8022 |  |  |  | 49.1976 | 24.5988 | 24.5988 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 19000; Zone 2: 19000 | 55.8364 | 27.9182 | 27.9182 |  |  |  | 32.1959 | 16.0979 | 16.0979
| 36 | 69.8 | 59 | Input | 2.69 | 2.76 | 2.83 | 2.87 | 2.91 | 2.98 | 3.03 | 3.39 | 3.79 | 3.68 | 3.76 | 3.41 |  | 7 | Redefine variable | [6 empty] | 18+24 | 48 | 18 | 24 |  |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 40 | 17.5 | 22.5 |  |  |  | 51.6044 | 22.1162 | 29.4883 |  |  |  | 54.2199 | 23.9299 | 30.29 |  |  |  | 54.8888 | Zone 1: 24.5988; Zone 2: 30.29; Zone 1: 18000; Zone 2: 23000 | 55.8364 | 23.9299 | 31.9065 |  |  |  | 35.9571 | 16.0979 | 19.8591
| 36 | 75.2 | 62.6 | Input | 2.74 | 2.81 | 2.88 | 2.92 | 2.96 | 3.03 | 3.08 | 3.44 | 3.84 | 3.73 | 3.81 | 3.46 |  | 8 | Calculate indoor with new variable | [6 empty] | 24+24 | 48 | 24 | 24 |  |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 42 | 21 | 21 |  |  |  | 51.6044 | 25.8022 | 25.8022 |  |  |  | 55.8364 | 27.9182 | 27.9182 |  |  |  | 60.58 | Zone 1: 30.29; Zone 2: 30.29; Zone 1: 22000; Zone 2: 22000 | 55.8364 | 27.9182 | 27.9182 |  |  |  | 39.7183 | 19.8591 | 19.8591
| 36 | 80.6 | 66.2 | Input | 2.79 | 2.86 | 2.89 | 2.91 | 2.95 | 3.06 | 3.1 | 3.48 | 3.91 | 3.8 | 3.85 | 3.47 | [9 empty] | 9+9+9 | 48 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 28.5 | 9.5 | 9.5 | 9.5 |  |  | 51.6044 | 17.2015 | 17.2015 | 17.2015 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 11000 | 11000 | 11000 |  |  | 55.8364 | 18.6121 | 18.6121 | 18.6121 |  |  | 25.4932 | 8.4977 | 8.4977 | 8.4977
| 36 | 89.6 | 73.4 | Input | 2.85 | 2.92 | 2.95 | 2.97 | 3.01 | 3.12 | 3.16 | 3.54 | 3.97 | 3.86 | 3.91 | 3.53 | [9 empty] | 9+9+12 | 48 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 31 | 9.5 | 9.5 | 12 |  |  | 51.6044 | 15.4813 | 15.4813 | 20.6418 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 10500 | 10500 | 13000 |  |  | 55.8364 | 16.7509 | 16.7509 | 22.3346 |  |  | 27.6176 | 8.4977 | 8.4977 | 10.6222
| 48 | 69.8 | 59 | Input | 2.19 | 2.24 | 2.28 | 2.35 | 2.38 | 2.41 | 2.46 | 2.78 | 3.11 | 3.45 | 3.64 | 3.08 | [9 empty] | 9+9+18 | 48 | 9 | 9 | 18 |  |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 37 | 9.5 | 9.5 | 18 |  |  | 51.6044 | 12.9011 | 12.9011 | 25.8022 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 10000 | 10000 | 19000 |  |  | 55.8364 | 13.9591 | 13.9591 | 27.9182 |  |  | 33.0934 | 8.4977 | 8.4977 | 16.0979
| 48 | 75.2 | 62.6 | Input | 2.25 | 2.31 | 2.35 | 2.42 | 2.45 | 2.48 | 2.53 | 2.85 | 3.18 | 3.52 | 3.71 | 3.15 | [9 empty] | 9+9+24 | 48 | 9 | 9 | 24 |  |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 40.5 | 9 | 9 | 22.5 |  |  | 51.6044 | 11.0581 | 11.0581 | 29.4883 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 9500 | 9500 | 23500 |  |  | 55.8364 | 11.9649 | 11.9649 | 31.9065 |  |  | 36.8546 | 8.4977 | 8.4977 | 19.8591
| 48 | 80.6 | 66.2 | Input | 2.99 | 3.06 | 3.15 | 3.25 | 3.29 | 3.46 | 3.94 | 4.36 | 4.8 | 3.79 | 3.98 | 3.43 | [9 empty] | 9+12+12 | 48 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 34.5 | 9.5 | 12.5 | 12.5 |  |  | 51.6044 | 14.0739 | 18.7653 | 18.7653 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 10000 | 13000 | 13000 |  |  | 55.8364 | 15.2281 | 20.3042 | 20.3042 |  |  | 29.7421 | 8.4977 | 10.6222 | 10.6222
| 48 | 89.6 | 73.4 | Input | 3.05 | 3.13 | 3.22 | 3.32 | 3.36 | 3.53 | 4.01 | 4.43 | 4.87 | 3.86 | 4.05 | 3.5 | [9 empty] | 9+12+18 | 48 | 9 | 12 | 18 |  |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 39 | 9 | 12 | 18 |  |  | 51.6044 | 11.9087 | 15.8783 | 23.8174 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 9500 | 12500 | 19000 |  |  | 55.8364 | 12.8853 | 17.1804 | 25.7707 |  |  | 35.2178 | 8.4977 | 10.6222 | 16.0979
| LEGEND | [24 empty] | 9+12+24 | 48 | 9 | 12 | 24 |  |  |  | 47.852 | 10.3209 | 13.0789 | 24.4522 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 42.5 | 9 | 12 | 21.5 |  |  | 51.6044 | 10.3209 | 13.7612 | 27.5224 |  |  | 55.8364 | 11.1673 | 14.8897 | 29.7794 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 9500 | 12500 | 22000 |  |  | 55.8364 | 11.1673 | 14.8897 | 29.7794 |  |  | 38.8635 | 8.3822 | 10.6222 | 19.8591
| DB - Dry Bulb | [24 empty] | 9+18+18 | 48 | 9 | 18 | 18 |  |  |  | 49.9631 | 10.3209 | 19.8211 | 19.8211 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 45 | 9 | 18 | 18 |  |  | 51.6044 | 10.3209 | 20.6418 | 20.6418 |  |  | 55.8364 | 11.1673 | 22.3346 | 22.3346 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 9500 | 18500 | 18500 |  |  | 55.8364 | 11.1673 | 22.3346 | 22.3346 |  |  | 40.5781 | 8.3822 | 16.0979 | 16.0979
| WB - Wet Bulb | [24 empty] | 9+18+24 | 48 | 9 | 18 | 24 |  |  |  | 51.6044 | 9.1067 | 18.2133 | 24.2844 |  |  | 54.7364 | 10.4631 | 19.8211 | 24.4522 |  |  | 46 | 8.5 | 16 | 21.5 |  |  | 51.6044 | 9.1067 | 18.2133 | 24.2844 |  |  | 55.8364 | 9.8535 | 19.707 | 26.276 |  |  | 66.8448 | 11.956 | 24.5988 | 30.29 |  |  | 9500 | 16500 | 22000 |  |  | 55.8364 | 9.8535 | 19.707 | 26.276 |  |  | 41.9111 | 7.3961 | 14.7922 | 19.7229
| TC - Total Net Capacity (1000 Btu/hour) | [24 empty] | 9+24+24 | 48 | 9 | 24 | 24 |  |  |  | 51.6044 | 8.1481 | 21.7282 | 21.7282 |  |  | 59.3676 | 10.4631 | 24.4522 | 24.4522 |  |  | 48 | 8 | 20 | 20 |  |  | 51.6044 | 8.1481 | 21.7282 | 21.7282 |  |  | 55.8364 | 8.8163 | 23.5101 | 23.5101 |  |  | 72.536 | 11.956 | 30.29 | 30.29 |  |  | 8500 | 21000 | 21000 |  |  | 55.8364 | 8.8163 | 23.5101 | 23.5101 |  |  | 41.9111 | 6.6175 | 17.6468 | 17.6468
| SC - Sensible Capacity (1000 Btu/hour) | [24 empty] | 12+12+12 | 48 | 12 | 12 | 12 |  |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 36 | 12 | 12 | 12 |  |  | 51.6044 | 17.2015 | 17.2015 | 17.2015 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 13000 | 13000 | 13000 |  |  | 55.8364 | 18.6121 | 18.6121 | 18.6121 |  |  | 31.8665 | 10.6222 | 10.6222 | 10.6222
| Input - Total Power (kW) | [24 empty] | 12+12+18 | 48 | 12 | 12 | 18 |  |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 41 | 12 | 12 | 17 |  |  | 51.6044 | 14.7441 | 14.7441 | 22.1162 |  |  | 53.8199 | 14.945 | 14.945 | 23.9299 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12500 | 12500 | 18000 |  |  | 55.8364 | 15.9533 | 15.9533 | 23.9299 |  |  | 37.3423 | 10.6222 | 10.6222 | 16.0979
[26 empty] | 12+12+24 | 48 | 12 | 12 | 24 |  |  |  | 50.2544 | 12.9011 | 12.9011 | 24.4522 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 44 | 11 | 11 | 22 |  |  | 51.6044 | 12.9011 | 12.9011 | 25.8022 |  |  | 55.8364 | 13.9591 | 13.9591 | 27.9182 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 11500 | 11500 | 23000 |  |  | 55.8364 | 13.9591 | 13.9591 | 27.9182 |  |  | 40.8147 | 10.4778 | 10.4778 | 19.8591
| HEATING PERFORMANCE DATA | [24 empty] | 12+18+18 | 48 | 12 | 18 | 18 |  |  |  | 51.6044 | 12.9011 | 19.3517 | 19.3517 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 44 | 11 | 16.5 | 16.5 |  |  | 51.6044 | 12.9011 | 19.3517 | 19.3517 |  |  | 55.8364 | 13.9591 | 20.9387 | 20.9387 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 11500 | 17000 | 17000 |  |  | 55.8364 | 13.9591 | 20.9387 | 20.9387 |  |  | 41.9111 | 10.4778 | 15.7167 | 15.7167
| Model | Heating |  |  |  | Outdoor conditions (DB) | [19 empty] | 12+18+24 | 48 | 12 | 18 | 24 |  |  |  | 51.6044 | 11.4677 | 17.2015 | 22.9353 |  |  | 57.3522 | 13.0789 | 19.8211 | 24.4522 |  |  | 48 | 10.5 | 16 | 21.5 |  |  | 51.6044 | 11.4677 | 17.2015 | 22.9353 |  |  | 55.8364 | 12.4081 | 18.6121 | 24.8162 |  |  | 69.8338 | 14.945 | 24.5988 | 30.29 |  |  | 11000 | 16000 | 22000 |  |  | 55.8364 | 12.4081 | 18.6121 | 24.8162 |  |  | 41.9111 | 9.3136 | 13.9704 | 18.6272
|  | Indoor Conditions DB | [23 empty] | 12+24+24 | 48 | 12 | 24 | 24 |  |  |  | 51.6044 | 10.3209 | 20.6418 | 20.6418 |  |  | 61.9833 | 13.0789 | 24.4522 | 24.4522 |  |  | 50 | 10 | 20 | 20 |  |  | 51.6044 | 10.3209 | 20.6418 | 20.6418 |  |  | 55.8364 | 11.1673 | 22.3346 | 22.3346 |  |  | 75.525 | 14.945 | 30.29 | 30.29 |  |  | 11000 | 20500 | 20500 |  |  | 55.8364 | 11.1673 | 22.3346 | 22.3346 |  |  | 41.9111 | 8.3822 | 16.7644 | 16.7644
[5 empty] | -22 | -13 | -4 | 0 | 5 | 17 | 19.4 | 24.8 | 32 | 39.2 | 44.6 | 53.6 |  |  |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | CAPACITY |  |  | 18+18+18 | 48 | 18 | 18 | 18 |  |  |  | 51.6044 | 17.2015 | 17.2015 | 17.2015 |  |  | 59.4633 | 19.8211 | 19.8211 | 19.8211 |  |  | 48 | 16 | 16 | 16 |  |  | 51.6044 | 17.2015 | 17.2015 | 17.2015 |  |  | 55.8364 | 18.6121 | 18.6121 | 18.6121 |  |  | 73.7965 | 24.5988 | 24.5988 | 24.5988 |  |  | 16500 | 16500 | 16500 |  |  | 55.8364 | 18.6121 | 18.6121 | 18.6121 |  |  | 41.9111 | 13.9704 | 13.9704 | 13.9704
| 18 | 59 |  | TC | 7.74 | 9.54 | 11.6 | 12.54 | 14.4 | 19.21 | 19.46 | 20.59 | 20.74 | 21.67 | 25.82 | 27.35 | 25.888 |  |  | INTERPOLATION | 23.9413 | 18 | 23.9413 |  |  | 18+18+24 | 48 | 18 | 18 | 24 |  |  |  | 51.6044 | 15.4813 | 15.4813 | 20.6418 |  |  | 64.0944 | 19.8211 | 19.8211 | 24.4522 |  |  | 50 | 15 | 15 | 20 |  |  | 51.6044 | 15.4813 | 15.4813 | 20.6418 |  |  | 55.8364 | 16.7509 | 16.7509 | 22.3346 |  |  | 79.4876 | 24.5988 | 24.5988 | 30.29 |  |  | 15500 | 15500 | 21000 |  |  | 55.8364 | 16.7509 | 16.7509 | 22.3346 |  |  | 41.9111 | 12.5733 | 12.5733 | 16.7644
| 18 | 64.4 |  | TC | 7.63 | 9.4 | 11.43 | 12.35 | 14.01 | 18.92 | 19.17 | 20.28 | 20.43 | 21.34 | 25.43 | 26.94 | 25.4971 | [8 empty] | 9+9+9+9 | 48 | 9 | 9 | 9 | 9 |  | 4 | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 37 | 9.25 | 9.25 | 9.25 | 9.25 |  | 51.6044 | 12.9011 | 12.9011 | 12.9011 | 12.9011 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 55.8364 | 13.9591 | 13.9591 | 13.9591 | 13.9591 |  | 33.9909 | 8.4977 | 8.4977 | 8.4977 | 8.4977
| 18 | 69 |  | TC | 5.52 | 6.54 | 7.69 | 8.14 | 13.99 | 15.02 | 15.94 | 17.13 | 18.93 | 19.66 | 23.96 | 26.67 | 24.0804 |  |  | EXTRAPOLATION | 24.0587 |  |  |  |  | 9+9+9+12 | 48 | 9 | 9 | 9 | 12 |  |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 39 | 9 | 9 | 9 | 12 |  | 51.6044 | 11.9087 | 11.9087 | 11.9087 | 15.8783 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9500 | 9500 | 9500 | 12500 |  | 55.8364 | 12.8853 | 12.8853 | 12.8853 | 17.1804 |  | 36.1154 | 8.4977 | 8.4977 | 8.4977 | 10.6222
| 18 | 71.6 |  | TC | 5.84 | 6.44 | 7.57 | 8.02 | 13.65 | 14.79 | 15.7 | 16.87 | 18.65 | 19.37 | 23.6 | 26.27 | 23.7187 | [8 empty] | 9+9+9+18 | 48 | 9 | 9 | 9 | 18 |  |  | 50.7838 | 10.3209 | 10.3209 | 10.3209 | 19.8211 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 44 | 9 | 9 | 9 | 17 |  | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 20.6418 |  | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 22.3346 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 9500 | 9500 | 9500 | 17500 |  | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 22.3346 |  | 41.2446 | 8.3822 | 8.3822 | 8.3822 | 16.0979
| 24 | 59 |  | TC | 14.13 | 17.95 | 20.25 | 22.73 | 24.45 | 25.66 | 26.04 | 28.31 | 30.43 | 32.22 | 36.92 | 40.88 | 37.096 |  |  | INTERPOLATION | 36.2107 | 24 | 36.2107 |  |  | 9+9+9+24 | 48 | 9 | 9 | 9 | 24 |  |  | 51.6044 | 9.1067 | 9.1067 | 9.1067 | 24.2844 |  | 55.8416 | 10.4631 | 10.4631 | 10.4631 | 24.4522 |  | 46 | 8.5 | 8.5 | 8.5 | 20.5 |  | 51.6044 | 9.1067 | 9.1067 | 9.1067 | 24.2844 |  | 55.8364 | 9.8535 | 9.8535 | 9.8535 | 26.276 |  | 66.1581 | 11.956 | 11.956 | 11.956 | 30.29 |  | 9000 | 9000 | 9000 | 21000 |  | 55.8364 | 9.8535 | 9.8535 | 9.8535 | 26.276 |  | 41.9111 | 7.3961 | 7.3961 | 7.3961 | 19.7229
| 24 | 64.4 |  | TC | 13.95 | 17.73 | 20 | 22.45 | 24.35 | 25.34 | 25.72 | 27.96 | 30.12 | 31.89 | 36.37 | 40.27 | 36.5433 | [8 empty] | 9+9+12+12 | 48 | 9 | 9 | 12 | 12 |  |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 42 | 9 | 9 | 12 | 12 |  | 51.6044 | 11.0581 | 11.0581 | 14.7441 | 14.7441 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 9500 | 9500 | 13000 | 13000 |  | 55.8364 | 11.9649 | 11.9649 | 15.9533 | 15.9533 |  | 38.2398 | 8.4977 | 8.4977 | 10.6222 | 10.6222
| 24 | 69 |  | TC | 13.85 | 17.59 | 19.84 | 22.28 | 24.17 | 25.15 | 25.52 | 27.74 | 29.89 | 31.21 | 36.22 | 40.71 | 36.4196 |  |  | EXTRAPOLATION | 36.1368 |  |  |  |  | 9+9+12+18 | 48 | 9 | 9 | 12 | 18 |  |  | 51.6044 | 9.6758 | 9.6758 | 12.9011 | 19.3517 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 46 | 9 | 9 | 11 | 17 |  | 51.6044 | 9.6758 | 9.6758 | 12.9011 | 19.3517 |  | 55.8364 | 10.4693 | 10.4693 | 13.9591 | 20.9387 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 9500 | 9500 | 11500 | 17500 |  | 55.8364 | 10.4693 | 10.4693 | 13.9591 | 20.9387 |  | 41.9111 | 7.8583 | 7.8583 | 10.4778 | 15.7167
| 24 | 71.6 |  | TC | 13.78 | 17.5 | 19.75 | 22.16 | 23.55 | 25.02 | 25.39 | 27.6 | 29.74 | 30.78 | 35.68 | 40.1 | 35.8764 | [8 empty] | 9+9+12+24 | 48 | 9 | 9 | 12 | 24 |  |  | 51.6044 | 8.6007 | 8.6007 | 11.4677 | 22.9353 |  | 58.4573 | 10.4631 | 10.4631 | 13.0789 | 24.4522 |  | 48 | 8.5 | 8.5 | 10.5 | 20.5 |  | 51.6044 | 8.6007 | 8.6007 | 11.4677 | 22.9353 |  | 55.8364 | 9.3061 | 9.3061 | 12.4081 | 24.8162 |  | 69.1471 | 11.956 | 11.956 | 14.945 | 30.29 |  | 9000 | 9000 | 11000 | 21000 |  | 55.8364 | 9.3061 | 9.3061 | 12.4081 | 24.8162 |  | 41.9111 | 6.9852 | 6.9852 | 9.3136 | 18.6272
| 30 | 59 |  | TC | 18.66 | 22.54 | 24.52 | 26.84 | 29.23 | 31.77 | 32.06 | 33.46 | 35.15 | 37.09 | 38.47 | 41.89 | 38.622 |  |  | INTERPOLATION | 37.1299 | 30 | 37.1299 |  |  | 9+9+18+18 | 48 | 9 | 9 | 18 | 18 |  |  | 51.6044 | 8.6007 | 8.6007 | 17.2015 | 17.2015 |  | 60.5684 | 10.4631 | 10.4631 | 19.8211 | 19.8211 |  | 48 | 8.5 | 8.5 | 15.5 | 15.5 |  | 51.6044 | 8.6007 | 8.6007 | 17.2015 | 17.2015 |  | 55.8364 | 9.3061 | 9.3061 | 18.6121 | 18.6121 |  | 73.1097 | 11.956 | 11.956 | 24.5988 | 24.5988 |  | 9000 | 9000 | 16000 | 16000 |  | 55.8364 | 9.3061 | 9.3061 | 18.6121 | 18.6121 |  | 41.9111 | 6.9852 | 6.9852 | 13.9704 | 13.9704
| 30 | 64.4 |  | TC | 18.41 | 22.23 | 24.18 | 26.47 | 28.74 | 31.31 | 31.59 | 32.97 | 34.64 | 36.55 | 37.89 | 41.26 | 38.0398 | [8 empty] | 9+9+18+24 | 48 | 9 | 9 | 18 | 24 |  |  | 51.6044 | 7.7407 | 7.7407 | 15.4813 | 20.6418 |  | 65.1996 | 10.4631 | 10.4631 | 19.8211 | 24.4522 |  | 50.5 | 8 | 8 | 14.5 | 20 |  | 51.6044 | 7.7407 | 7.7407 | 15.4813 | 20.6418 |  | 55.8364 | 8.3755 | 8.3755 | 16.7509 | 22.3346 |  | 78.8009 | 11.956 | 11.956 | 24.5988 | 30.29 |  | 8500 | 8500 | 15000 | 20000 |  | 55.8364 | 8.3755 | 8.3755 | 16.7509 | 22.3346 |  | 41.9111 | 6.2867 | 6.2867 | 12.5733 | 16.7644
| 30 | 69 |  | TC | 16.7 | 20.65 | 22.05 | 24.02 | 28.22 | 27.67 | 28.13 | 31.86 | 33.96 | 36.08 | 37.21 | 40.27 | 37.346 |  |  | EXTRAPOLATION | 37.1241 |  |  |  |  | 9+12+12+12 | 48 | 9 | 12 | 12 | 12 |  |  | 49.5576 | 10.3209 | 13.0789 | 13.0789 | 13.0789 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 45 | 9 | 12 | 12 | 12 |  | 51.6044 | 10.3209 | 13.7612 | 13.7612 | 13.7612 |  | 55.8364 | 11.1673 | 14.8897 | 14.8897 | 14.8897 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 9500 | 12500 | 12500 | 12500 |  | 55.8364 | 11.1673 | 14.8897 | 14.8897 | 14.8897 |  | 40.2487 | 8.3822 | 10.6222 | 10.6222 | 10.6222
| 30 | 71.6 |  | TC | 15.51 | 19.42 | 21.79 | 23.73 | 25.99 | 27.27 | 27.72 | 31.38 | 33.45 | 35.54 | 36.65 | 39.67 | 36.7842 | [8 empty] | 9+12+12+18 | 48 | 9 | 12 | 12 | 18 |  |  | 51.6044 | 9.1067 | 12.1422 | 12.1422 | 18.2133 |  | 56.442 | 10.4631 | 13.0789 | 13.0789 | 19.8211 |  | 47 | 9 | 11 | 11 | 16 |  | 51.6044 | 9.1067 | 12.1422 | 12.1422 | 18.2133 |  | 55.8364 | 9.8535 | 13.138 | 13.138 | 19.707 |  | 66.4449 | 11.956 | 14.945 | 14.945 | 24.5988 |  | 9500 | 11500 | 11500 | 16500 |  | 55.8364 | 9.8535 | 13.138 | 13.138 | 19.707 |  | 41.9111 | 7.3961 | 9.8614 | 9.8614 | 14.7922
| 36 | 59 |  | TC | 23.82 | 28.67 | 30.78 | 33.61 | 36.66 | 39.29 | 39.91 | 41.15 | 43.1 | 45.78 | 56.86 | 62.85 | 57.1262 |  |  | INTERPOLATION | 50.3204 | 36 | 50.3204 |  |  | 9+12+12+24 | 48 | 9 | 12 | 12 | 24 |  |  | 51.6044 | 8.1481 | 10.8641 | 10.8641 | 21.7282 |  | 61.0731 | 10.4631 | 13.0789 | 13.0789 | 24.4522 |  | 48.5 | 8.5 | 10 | 10 | 20 |  | 51.6044 | 8.1481 | 10.8641 | 10.8641 | 21.7282 |  | 55.8364 | 8.8163 | 11.755 | 11.755 | 23.5101 |  | 72.1361 | 11.956 | 14.945 | 14.945 | 30.29 |  | 9000 | 10500 | 10500 | 20500 |  | 55.8364 | 8.8163 | 11.755 | 11.755 | 23.5101 |  | 41.9111 | 6.6175 | 8.8234 | 8.8234 | 17.6468
| 36 | 64.4 |  | TC | 23.52 | 28.29 | 30.37 | 33.15 | 36.15 | 38.7 | 39.31 | 40.53 | 42.46 | 45.09 | 56.01 | 61.91 | 56.2722 | [8 empty] | 9+12+18+18 | 48 | 9 | 12 | 18 | 18 |  |  | 51.6044 | 8.1481 | 10.8641 | 16.2961 | 16.2961 |  | 63.1842 | 10.4631 | 13.0789 | 19.8211 | 19.8211 |  | 48.5 | 8.5 | 10 | 15 | 15 |  | 51.6044 | 8.1481 | 10.8641 | 16.2961 | 16.2961 |  | 55.8364 | 8.8163 | 11.755 | 17.6326 | 17.6326 |  | 76.0987 | 11.956 | 14.945 | 24.5988 | 24.5988 |  | 9000 | 10500 | 15500 | 15500 |  | 55.8364 | 8.8163 | 11.755 | 17.6326 | 17.6326 |  | 41.9111 | 6.6175 | 8.8234 | 13.2351 | 13.2351
| 36 | 69 |  | TC | 23.03 | 27.69 | 29.04 | 31.77 | 36.08 | 37.41 | 37.75 | 39.77 | 42.39 | 46.46 | 50.54 | 54.37 | 50.7102 |  |  | EXTRAPOLATION | 50.8627 |  |  |  |  | 9+18+18+18 | 48 | 9 | 18 | 18 | 18 |  |  | 51.6044 | 7.3721 | 14.7441 | 14.7441 | 14.7441 |  | 69.9264 | 10.4631 | 19.8211 | 19.8211 | 19.8211 |  | 50 | 8 | 14 | 14 | 14 |  | 51.6044 | 7.3721 | 14.7441 | 14.7441 | 14.7441 |  | 55.8364 | 7.9766 | 15.9533 | 15.9533 | 15.9533 |  | 85.7525 | 11.956 | 24.5988 | 24.5988 | 24.5988 |  | 8500 | 14500 | 14500 | 14500 |  | 55.8364 | 7.9766 | 15.9533 | 15.9533 | 15.9533 |  | 41.9111 | 5.9873 | 11.9746 | 11.9746 | 11.9746
| 36 | 71.6 |  | TC | 22.63 | 27.2 | 28.52 | 31.2 | 34.64 | 36.66 | 36.99 | 38.97 | 41.54 | 45.53 | 49.53 | 53.28 | 49.6967 | [8 empty] | 12+12+12+12 | 48 | 12 | 12 | 12 | 12 |  |  | 51.6044 | 12.9011 | 12.9011 | 12.9011 | 12.9011 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 48 | 12 | 12 | 12 | 12 |  | 51.6044 | 12.9011 | 12.9011 | 12.9011 | 12.9011 |  | 55.8364 | 13.9591 | 13.9591 | 13.9591 | 13.9591 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 12500 | 12500 | 12500 | 12500 |  | 55.8364 | 13.9591 | 13.9591 | 13.9591 | 13.9591 |  | 41.9111 | 10.4778 | 10.4778 | 10.4778 | 10.4778
| 48 | 59 |  | TC | 23.97 | 28.85 | 30.97 | 33.82 | 37.29 | 39.53 | 40.16 | 41.41 | 43.37 | 46.06 | 57.21 | 67.67 | 57.6749 |  |  | INTERPOLATION | 55.8364 | 48 | 55.8364 |  |  | 12+12+12+18 | 48 | 12 | 12 | 12 | 18 |  |  | 51.6044 | 11.4677 | 11.4677 | 11.4677 | 17.2015 |  | 59.0578 | 13.0789 | 13.0789 | 13.0789 | 19.8211 |  | 49 | 11 | 11 | 11 | 16 |  | 51.6044 | 11.4677 | 11.4677 | 11.4677 | 17.2015 |  | 55.8364 | 12.4081 | 12.4081 | 12.4081 | 18.6121 |  | 69.4339 | 14.945 | 14.945 | 14.945 | 24.5988 |  | 11500 | 11500 | 11500 | 16500 |  | 55.8364 | 12.4081 | 12.4081 | 12.4081 | 18.6121 |  | 41.9111 | 9.3136 | 9.3136 | 9.3136 | 13.9704
| 48 | 64.4 |  | TC | 23.71 | 28.52 | 30.61 | 33.42 | 36.84 | 39.01 | 39.62 | 40.85 | 42.8 | 45.45 | 56.46 | 66.65 | 56.9129 | [8 empty] | 12+12+12+24 | 48 | 12 | 12 | 12 | 24 |  |  | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 20.6418 |  | 63.6889 | 13.0789 | 13.0789 | 13.0789 | 24.4522 |  | 50 | 10 | 10 | 10 | 20 |  | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 20.6418 |  | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 22.3346 |  | 75.1251 | 14.945 | 14.945 | 14.945 | 30.29 |  | 10500 | 10500 | 10500 | 20500 |  | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 22.3346 |  | 41.9111 | 8.3822 | 8.3822 | 8.3822 | 16.7644
| 48 | 69 |  | TC | 23.33 | 28.05 | 29.42 | 32.18 | 36.34 | 37.9 | 38.24 | 40.29 | 42.94 | 47.06 | 55.83 | 65.74 | 56.2704 |  |  | EXTRAPOLATION | 55.7525 |  |  |  |  | 12+12+18+18 | 48 | 12 | 12 | 18 | 18 |  |  | 51.6044 | 10.3209 | 10.3209 | 15.4813 | 15.4813 |  | 65.8 | 13.0789 | 13.0789 | 19.8211 | 19.8211 |  | 50 | 10 | 10 | 15 | 15 |  | 51.6044 | 10.3209 | 10.3209 | 15.4813 | 15.4813 |  | 55.8364 | 11.1673 | 11.1673 | 16.7509 | 16.7509 |  | 79.0877 | 14.945 | 14.945 | 24.5988 | 24.5988 |  | 10500 | 10500 | 15500 | 15500 |  | 55.8364 | 11.1673 | 11.1673 | 16.7509 | 16.7509 |  | 41.9111 | 8.3822 | 8.3822 | 12.5733 | 12.5733
| 48 | 71.6 |  | TC | 22.88 | 27.5 | 28.83 | 31.54 | 35.02 | 37.06 | 37.4 | 39.4 | 42 | 46.03 | 54.71 | 64.43 | 55.142 | [8 empty] | 9+9+9+9+9 | 48 | 9 | 9 | 9 | 9 | 9 | 5 | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 52.3156 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 45 | 9 | 9 | 9 | 9 | 9 | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 59.7801 | 11.956 | 11.956 | 11.956 | 11.956 | 11.956 | 9500 | 9500 | 9500 | 9500 | 9500 | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 41.9111 | 8.3822 | 8.3822 | 8.3822 | 8.3822 | 8.3822
| 18 | 59 |  | Input | 1.67 | 1.71 | 1.76 | 1.8 | 1.87 | 1.93 | 1.95 | 2.01 | 1.6 | 1.66 | 1.79 | 1.87 | [9 empty] | 9+9+9+9+12 | 48 | 9 | 9 | 9 | 9 | 12 |  | 51.6044 | 9.6758 | 9.6758 | 9.6758 | 9.6758 | 12.9011 | 54.9313 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 48 | 9 | 9 | 9 | 9 | 12 | 51.6044 | 9.6758 | 9.6758 | 9.6758 | 9.6758 | 12.9011 | 55.8364 | 10.4693 | 10.4693 | 10.4693 | 10.4693 | 13.9591 | 62.7691 | 11.956 | 11.956 | 11.956 | 11.956 | 14.945 | 9500 | 9500 | 9500 | 9500 | 13000 | 55.8364 | 10.4693 | 10.4693 | 10.4693 | 10.4693 | 13.9591 | 41.9111 | 7.8583 | 7.8583 | 7.8583 | 7.8583 | 10.4778
| 18 | 64.4 |  | Input | 1.7 | 1.74 | 1.79 | 1.83 | 1.9 | 1.96 | 1.98 | 2.04 | 1.63 | 1.69 | 1.82 | 1.9 | [9 empty] | 9+9+9+9+18 | 48 | 9 | 9 | 9 | 9 | 18 |  | 51.6044 | 8.6007 | 8.6007 | 8.6007 | 8.6007 | 17.2015 | 61.6736 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 19.8211 | 50 | 8.5 | 8.5 | 8.5 | 8.5 | 16 | 51.6044 | 8.6007 | 8.6007 | 8.6007 | 8.6007 | 17.2015 | 55.8364 | 9.3061 | 9.3061 | 9.3061 | 9.3061 | 18.6121 | 72.4229 | 11.956 | 11.956 | 11.956 | 11.956 | 24.5988 | 9000 | 9000 | 9000 | 9000 | 16500 | 55.8364 | 9.3061 | 9.3061 | 9.3061 | 9.3061 | 18.6121 | 41.9111 | 6.9852 | 6.9852 | 6.9852 | 6.9852 | 13.9704
| 18 | 69 |  | Input | 1.41 | 1.44 | 1.46 | 1.47 | 1.91 | 1.63 | 1.68 | 1.76 | 1.8 | 1.88 | 1.95 | 1.97 | [9 empty] | 9+9+9+9+24 | 48 | 9 | 9 | 9 | 9 | 24 |  | 51.6044 | 7.7407 | 7.7407 | 7.7407 | 7.7407 | 20.6418 | 66.3047 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 24.4522 | 52 | 8 | 8 | 8 | 8 | 20 | 51.6044 | 7.7407 | 7.7407 | 7.7407 | 7.7407 | 20.6418 | 55.8364 | 8.3755 | 8.3755 | 8.3755 | 8.3755 | 22.3346 | 78.1141 | 11.956 | 11.956 | 11.956 | 11.956 | 30.29 | 8500 | 8500 | 8500 | 8500 | 20500 | 55.8364 | 8.3755 | 8.3755 | 8.3755 | 8.3755 | 22.3346 | 41.9111 | 6.2867 | 6.2867 | 6.2867 | 6.2867 | 16.7644
| 18 | 71.6 |  | Input | 1.44 | 1.47 | 1.49 | 1.5 | 2.01 | 1.66 | 1.71 | 1.79 | 1.83 | 1.91 | 1.98 | 2 | [9 empty] | 9+9+9+12+12 | 48 | 9 | 9 | 9 | 12 | 12 |  | 51.6044 | 9.1067 | 9.1067 | 9.1067 | 12.1422 | 12.1422 | 57.5471 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 49 | 9 | 9 | 9 | 11 | 11 | 51.6044 | 9.1067 | 9.1067 | 9.1067 | 12.1422 | 12.1422 | 55.8364 | 9.8535 | 9.8535 | 9.8535 | 13.138 | 13.138 | 65.7581 | 11.956 | 11.956 | 11.956 | 14.945 | 14.945 | 9000 | 9000 | 9000 | 12000 | 12000 | 55.8364 | 9.8535 | 9.8535 | 9.8535 | 13.138 | 13.138 | 41.9111 | 7.3961 | 7.3961 | 7.3961 | 9.8614 | 9.8614
| 24 | 59 |  | Input | 2.93 | 3.19 | 3.23 | 3.45 | 3.63 | 2.66 | 2.79 | 2.87 | 2.65 | 2.78 | 2.96 | 2.71 | [9 empty] | 9+9+9+12+18 | 48 | 9 | 9 | 9 | 12 | 18 |  | 51.6044 | 8.1481 | 8.1481 | 8.1481 | 10.8641 | 16.2961 | 64.2893 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 19.8211 | 51 | 8 | 8 | 8 | 11 | 16 | 51.6044 | 8.1481 | 8.1481 | 8.1481 | 10.8641 | 16.2961 | 55.8364 | 8.8163 | 8.8163 | 8.8163 | 11.755 | 17.6326 | 75.4119 | 11.956 | 11.956 | 11.956 | 14.945 | 24.5988 | 8500 | 8500 | 8500 | 11500 | 17000 | 55.8364 | 8.8163 | 8.8163 | 8.8163 | 11.755 | 17.6326 | 41.9111 | 6.6175 | 6.6175 | 6.6175 | 8.8234 | 13.2351
| 24 | 64.4 |  | Input | 3 | 3.27 | 3.31 | 3.53 | 3.74 | 2.73 | 2.86 | 2.94 | 2.72 | 2.89 | 2.99 | 2.74 | [9 empty] | 9+9+9+18+18 | 48 | 9 | 9 | 9 | 18 | 18 |  | 51.6044 | 7.3721 | 7.3721 | 7.3721 | 14.7441 | 14.7441 | 71.0316 | 10.4631 | 10.4631 | 10.4631 | 19.8211 | 19.8211 | 52.5 | 7.5 | 7.5 | 7.5 | 15 | 15 | 51.6044 | 7.3721 | 7.3721 | 7.3721 | 14.7441 | 14.7441 | 55.8364 | 7.9766 | 7.9766 | 7.9766 | 15.9533 | 15.9533 | 85.0657 | 11.956 | 11.956 | 11.956 | 24.5988 | 24.5988 | 8000 | 8000 | 8000 | 15500 | 15500 | 55.8364 | 7.9766 | 7.9766 | 7.9766 | 15.9533 | 15.9533 | 41.9111 | 5.9873 | 5.9873 | 5.9873 | 11.9746 | 11.9746
| 24 | 69 |  | Input | 3.07 | 3.34 | 3.38 | 3.61 | 3.9 | 2.79 | 2.92 | 3.01 | 2.77 | 2.96 | 3.04 | 3.17 | [9 empty] | 9+9+12+12+12 | 48 | 9 | 9 | 12 | 12 | 12 |  | 51.6044 | 8.6007 | 8.6007 | 11.4677 | 11.4677 | 11.4677 | 60.1629 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 50 | 8.5 | 8.5 | 11 | 11 | 11 | 51.6044 | 8.6007 | 8.6007 | 11.4677 | 11.4677 | 11.4677 | 55.8364 | 9.3061 | 9.3061 | 12.4081 | 12.4081 | 12.4081 | 68.7471 | 11.956 | 11.956 | 14.945 | 14.945 | 14.945 | 9000 | 9000 | 12000 | 12000 | 12000 | 55.8364 | 9.3061 | 9.3061 | 12.4081 | 12.4081 | 12.4081 | 41.9111 | 6.9852 | 6.9852 | 9.3136 | 9.3136 | 9.3136
| 24 | 71.6 |  | Input | 3.14 | 3.42 | 3.46 | 3.7 | 3.83 | 2.85 | 2.99 | 3.08 | 2.84 | 3.01 | 3.07 | 3.2 | [9 empty] | 9+9+12+12+18 | 48 | 9 | 9 | 12 | 12 | 18 |  | 51.6044 | 7.7407 | 7.7407 | 10.3209 | 10.3209 | 15.4813 | 66.9051 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 19.8211 | 52 | 8.5 | 8.5 | 10 | 10 | 15 | 51.6044 | 7.7407 | 7.7407 | 10.3209 | 10.3209 | 15.4813 | 55.8364 | 8.3755 | 8.3755 | 11.1673 | 11.1673 | 16.7509 | 78.4009 | 11.956 | 11.956 | 14.945 | 14.945 | 24.5988 | 8500 | 8500 | 11000 | 11000 | 16000 | 55.8364 | 8.3755 | 8.3755 | 11.1673 | 11.1673 | 16.7509 | 41.9111 | 6.2867 | 6.2867 | 8.3822 | 8.3822 | 12.5733
| 30 | 59 |  | Input | 3.39 | 3.46 | 3.45 | 3.62 | 3.74 | 3.71 | 3.73 | 3.79 | 3.08 | 3.12 | 3.27 | 3.37 | [9 empty] | 9+12+12+12+12 | 48 | 9 | 12 | 12 | 12 | 12 |  | 51.6044 | 8.1481 | 10.8641 | 10.8641 | 10.8641 | 10.8641 | 62.7787 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 50 | 8 | 10.5 | 10.5 | 10.5 | 10.5 | 51.6044 | 8.1481 | 10.8641 | 10.8641 | 10.8641 | 10.8641 | 55.8364 | 8.8163 | 11.755 | 11.755 | 11.755 | 11.755 | 71.7361 | 11.956 | 14.945 | 14.945 | 14.945 | 14.945 | 8500 | 11000 | 11000 | 11000 | 11000 | 55.8364 | 8.8163 | 11.755 | 11.755 | 11.755 | 11.755 | 41.9111 | 6.6175 | 8.8234 | 8.8234 | 8.8234 | 8.8234
| 30 | 64.4 |  | Input | 3.42 | 3.49 | 3.53 | 3.75 | 3.86 | 3.84 | 3.86 | 3.92 | 3.11 | 3.15 | 3.3 | 3.4 | [9 empty] | 9+12+12+12+18 | 48 | 9 | 12 | 12 | 12 | 18 |  | 51.6044 | 7.3721 | 9.8294 | 9.8294 | 9.8294 | 14.7441 | 69.5209 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 19.8211 | 52.5 | 7.5 | 10 | 10 | 10 | 15 | 51.6044 | 7.3721 | 9.8294 | 9.8294 | 9.8294 | 14.7441 | 55.8364 | 7.9766 | 10.6355 | 10.6355 | 10.6355 | 15.9533 | 81.3899 | 11.956 | 14.945 | 14.945 | 14.945 | 24.5988 | 8000 | 10500 | 10500 | 10500 | 15500 | 55.8364 | 7.9766 | 10.6355 | 10.6355 | 10.6355 | 15.9533 | 41.9111 | 5.9873 | 7.9831 | 7.9831 | 7.9831 | 11.9746
| 30 | 69 |  | Input | 3.51 | 3.58 | 3.64 | 3.76 | 4.05 | 3.85 | 3.9 | 4.04 | 3.14 | 3.18 | 3.21 | 3.3 | [9 empty] | 12+12+12+12+12 | 48 | 12 | 12 | 12 | 12 | 12 |  | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 65.3944 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 52.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 51.6044 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 10.3209 | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 74.7251 | 14.945 | 14.945 | 14.945 | 14.945 | 14.945 | 11000 | 11000 | 11000 | 11000 | 11000 | 55.8364 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 11.1673 | 41.9111 | 8.3822 | 8.3822 | 8.3822 | 8.3822 | 8.3822
| 30 | 71.6 |  | Input | 3.64 | 3.61 | 3.77 | 3.79 | 3.81 | 3.88 | 3.93 | 4.07 | 3.17 | 3.21 | 3.24 | 3.33
| 36 | 59 |  | Input | 4.91 | 5.02 | 5.17 | 5.2 | 5.24 | 5.11 | 5.13 | 5.21 | 4.56 | 4.73 | 4.9 | 4.56
| 36 | 64.4 |  | Input | 4.97 | 5.08 | 5.23 | 5.26 | 5.33 | 5.17 | 5.19 | 5.27 | 4.62 | 4.79 | 4.96 | 4.62
| 36 | 69 |  | Input | 5.04 | 5.15 | 5.24 | 5.27 | 5.39 | 5.25 | 5.27 | 5.35 | 4.62 | 4.96 | 4.66 | 4.3
| 36 | 71.6 |  | Input | 5.09 | 5.2 | 5.29 | 5.32 | 5.34 | 5.3 | 5.32 | 5.4 | 4.67 | 5.01 | 4.71 | 4.35
| 48 | 59 |  | Input | 4.96 | 5.07 | 5.22 | 5.25 | 5.33 | 5.16 | 5.18 | 5.26 | 4.61 | 4.78 | 4.95 | 4.61
| 48 | 64.4 |  | Input | 5.07 | 5.18 | 5.33 | 5.37 | 5.51 | 5.27 | 5.29 | 5.38 | 4.71 | 4.89 | 5.06 | 4.71
| 48 | 69 |  | Input | 5.1 | 5.21 | 5.3 | 5.33 | 5.39 | 5.31 | 5.33 | 5.41 | 4.68 | 4.63 | 4.71 | 5.04
| 48 | 71.6 |  | Input | 5.15 | 5.26 | 5.35 | 5.38 | 5.4 | 5.36 | 5.38 | 5.46 | 4.73 | 5.07 | 4.76 | 5.09
| 18 | 59 |  | COP | 1.36 | 1.64 | 1.93 | 2.04 | 2.19 | 2.92 | 2.92 | 3 | 3.8 | 3.83 | 4.21 | 4.28
| 18 | 64.4 |  | COP | 1.31 | 1.58 | 1.87 | 1.98 | 2.16 | 2.83 | 2.84 | 2.91 | 3.67 | 3.7 | 4.1 | 4.16
| 18 | 69 |  | COP | 1.15 | 1.33 | 1.54 | 1.62 | 2.15 | 2.7 | 2.78 | 2.85 | 3.08 | 3.05 | 3.59 | 3.96
| 18 | 71.6 |  | COP | 1.19 | 1.28 | 1.49 | 1.57 | 1.99 | 2.61 | 2.69 | 2.76 | 2.99 | 2.97 | 3.49 | 3.85
| 24 | 59 |  | COP | 1.41 | 1.65 | 1.84 | 1.93 | 1.98 | 2.83 | 2.74 | 2.89 | 3.37 | 3.4 | 3.65 | 4.43
| 24 | 64.4 |  | COP | 1.36 | 1.59 | 1.77 | 1.86 | 1.91 | 2.73 | 2.64 | 2.79 | 3.25 | 3.23 | 3.56 | 4.31
| 24 | 69 |  | COP | 1.32 | 1.54 | 1.72 | 1.81 | 1.81 | 2.65 | 2.56 | 2.71 | 3.16 | 3.09 | 3.49 | 3.76
| 24 | 71.6 |  | COP | 1.29 | 1.5 | 1.67 | 1.76 | 1.8 | 2.57 | 2.49 | 2.63 | 3.07 | 3 | 3.41 | 3.67
| 30 | 59 |  | COP | 1.61 | 1.91 | 2.08 | 2.17 | 2.29 | 2.51 | 2.52 | 2.59 | 3.34 | 3.48 | 3.45 | 3.64
| 30 | 64.4 |  | COP | 1.58 | 1.87 | 2.01 | 2.07 | 2.18 | 2.39 | 2.4 | 2.47 | 3.26 | 3.4 | 3.37 | 3.56
| 30 | 69 |  | COP | 1.39 | 1.69 | 1.78 | 1.87 | 2.04 | 2.11 | 2.11 | 2.31 | 3.17 | 3.33 | 3.4 | 3.58
| 30 | 71.6 |  | COP | 1.25 | 1.58 | 1.69 | 1.84 | 2 | 2.06 | 2.07 | 2.26 | 3.09 | 3.24 | 3.32 | 3.49
| 36 | 59 |  | COP | 1.42 | 1.67 | 1.74 | 1.89 | 2.05 | 2.25 | 2.28 | 2.31 | 2.77 | 2.84 | 3.4 | 4.04
| 36 | 64.4 |  | COP | 1.39 | 1.63 | 1.7 | 1.85 | 2 | 2.19 | 2.22 | 2.25 | 2.7 | 2.76 | 3.31 | 3.93
| 36 | 69 |  | COP | 1.34 | 1.58 | 1.62 | 1.77 | 1.96 | 2.09 | 2.1 | 2.18 | 2.69 | 2.74 | 3.18 | 3.71
| 36 | 71.6 |  | COP | 1.3 | 1.53 | 1.58 | 1.72 | 1.9 | 2.03 | 2.04 | 2.11 | 2.61 | 2.66 | 3.08 | 3.59
| 48 | 59 |  | COP | 1.42 | 1.67 | 1.74 | 1.89 | 2.05 | 2.24 | 2.27 | 2.31 | 2.76 | 2.83 | 3.39 | 4.31
| 48 | 64.4 |  | COP | 1.37 | 1.61 | 1.68 | 1.83 | 1.98 | 2.17 | 2.19 | 2.23 | 2.66 | 2.73 | 3.27 | 4.15
| 48 | 69 |  | COP | 1.34 | 1.58 | 1.63 | 1.77 | 1.96 | 2.09 | 2.1 | 2.18 | 2.69 | 2.98 | 3.47 | 3.82
| 48 | 71.6 |  | COP | 1.3 | 1.53 | 1.58 | 1.72 | 1.9 | 2.03 | 2.04 | 2.11 | 2.6 | 2.66 | 3.37 | 3.71
LEGEND
DB - Dry Bulb
WB - Wet Bulb
TC - Total Net Capacity (1000 Btu/hour)
Input - Total Power (kW)
COP - W/W

## Mixed Ducted and Non-Ducted (hidden)
Mixed Ducted and Non-Ducted Indoor Units | [24 empty] | NOMINAL COMBINATIONS | [6 empty] | COOLING ESTIMATED CAPACITY CAPPED | [5 empty] | COOLING CAPPED CAPACITY BASED ON INDOOR UNIT | [5 empty] | COOLING ORIGINAL ESTIMATED CAPACITY | [5 empty] | COOLING CALCULATION UNCAPPED | [5 empty] | HEATING ESTIMATED CAPACITY CAPPED | [5 empty] | HEATING CAPPED CAPACITY BASED ON INDOOR UNIT | [5 empty] | HEATING ORIGINAL ESTIMATED CAPACITY |  |  |  |  | HEATING CALCULATION UNCAPPED | [5 empty] | SENSIBLE ESTIMATED CAPACITY BASED ON RATIO
[22 empty] | Variables of indoor |  | Size |  | Size |  |  |  |  | No. of Zones | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Heating Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h)
[22 empty] | Indoor Unit Sizes | Defined by size/variable 9 | 18K | 18 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[22 empty] | 9 | 1 | 9+9 | 18 | 9 | 9 |  |  |  | 2 | 20.7644 | 10.3822 | 10.3822 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 18 | 9 | 9 |  |  |  | 20.7644 | 10.3822 | 10.3822 |  |  |  | 22.1998 | 11.0999 | 11.0999 |  |  |  | 23.912 | Zone 1: 11.956; Zone 2: 11.956; Zone 1: 9500; Zone 2: 9500 | 22.1998 | 11.0999 | 11.0999 |  |  |  | 15.4182 | 7.7091 | 7.7091
[22 empty] | 12 | 1.3333 | 9+12 | 18 | 9 | 12 |  |  |  |  | 20.7644 | 8.899 | 11.8654 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 19 | 8.5 | 10.5 |  |  |  | 20.7644 | 8.899 | 11.8654 |  |  |  | 22.1998 | 9.5142 | 12.6856 |  |  |  | 26.901 | Zone 1: 11.956; Zone 2: 14.945; Zone 1: 9000; Zone 2: 11000 | 22.1998 | 9.5142 | 12.6856 |  |  |  | 15.4182 | 6.6078 | 8.8104
[22 empty] | 18 | 2 | 12+12 | 18 | 12 | 12 |  |  |  |  | 20.7644 | 10.3822 | 10.3822 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 19 | 9.5 | 9.5 |  |  |  | 20.7644 | 10.3822 | 10.3822 |  |  |  | 22.1998 | 11.0999 | 11.0999 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 10000; Zone 2: 10000 | 22.1998 | 11.0999 | 11.0999 |  |  |  | 15.4182 | 7.7091 | 7.7091
[22 empty] | 24 | 2.6667 | 24K | 24 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[24 empty] | 9+9 | 24 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 19 | 9.5 | 9.5 |  |  |  | 30.4794 | 15.2397 | 15.2397 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 11.956; 10000 Zone 1: 10000; 10000 Zone 2: 10000 | 35.9864 | 17.9932 | 17.9932 |  |  |  | 15.9237 | 7.9619 | 7.9619
[24 empty] | 9+12 | 24 | 9 | 12 |  |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 21.5 | 9.5 | 12 |  |  |  | 30.4794 | 13.0626 | 17.4168 |  |  |  | 26.901 | 11.956 | 14.945 |  |  |  | 26.901 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 14.945; 10000 Zone 1: 10000; 10000 Zone 2: 13000 | 35.9864 | 15.4227 | 20.5637 |  |  |  | 17.9142 | 7.9619 | 9.9523
[24 empty] | 9+18 | 24 | 9 | 18 |  |  |  |  | 29.9809 | 10.1598 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 25 | 8.4 | 16.6 |  |  |  | 30.4794 | 10.1598 | 20.3196 |  |  |  | 35.9469 | 11.956 | 23.9909 |  |  |  | 36.5548 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 24.5988; 10000 Zone 1: 9000; 10000 Zone 2: 18000 | 35.9864 | 11.9955 | 23.9909 |  |  |  | 22.8138 | 7.7311 | 15.0828
[24 empty] | 12+12 | 24 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 24 | 12 | 12 |  |  |  | 30.4794 | 15.2397 | 15.2397 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | 14.945 Zone 1: 14.945; 14.945 Zone 2: 14.945; 10000 Zone 1: 13000; 10000 Zone 2: 13000 | 35.9864 | 17.9932 | 17.9932 |  |  |  | 19.9046 | 9.9523 | 9.9523
[24 empty] | 12+18 | 24 | 12 | 18 |  |  |  |  | 30.4794 | 12.1918 | 18.2877 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 26 | 10 | 16 |  |  |  | 30.4794 | 12.1918 | 18.2877 |  |  |  | 35.9864 | 14.3946 | 21.5918 |  |  |  | 39.5438 | 14.945 Zone 1: 14.945; 14.945 Zone 2: 24.5988; 10000 Zone 1: 11200; 10000 Zone 2: 16800 | 35.9864 | 14.3946 | 21.5918 |  |  |  | 23.1932 | 9.2773 | 13.9159
[24 empty] | 18+18 | 24 | 18 | 18 |  |  |  |  | 30.4794 | 15.2397 | 15.2397 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 28 | 14 | 14 |  |  |  | 30.4794 | 15.2397 | 15.2397 |  |  |  | 35.9864 | 17.9932 | 17.9932 |  |  |  | 49.1976 | 14.945 Zone 1: 24.5988; 14.945 Zone 2: 24.5988; 10000 Zone 1: 15000; 10000 Zone 2: 15000 | 35.9864 | 17.9932 | 17.9932 |  |  |  | 23.1932 | 11.5966 | 11.5966
[24 empty] | 9+9+9 | 24 | 9 | 9 | 9 |  |  | 3 | 30.4794 | 10.1598 | 10.1598 | 10.1598 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 27 | 9 | 9 | 9 |  |  | 30.4794 | 10.1598 | 10.1598 | 10.1598 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 9500 | 9500 | 9500 |  |  | 35.9864 | 11.9955 | 11.9955 | 11.9955 |  |  | 23.1932 | 7.7311 | 7.7311 | 7.7311
[24 empty] | 9+9+12 | 24 | 9 | 9 | 12 |  |  |  | 30.4794 | 9.1438 | 9.1438 | 12.1918 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 29.001 | 8.667 | 8.667 | 11.667 |  |  | 30.4794 | 9.1438 | 9.1438 | 12.1918 |  |  | 35.9864 | 10.7959 | 10.7959 | 14.3946 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 9500 | 9500 | 12000 |  |  | 35.9864 | 10.7959 | 10.7959 | 14.3946 |  |  | 23.1932 | 6.958 | 6.958 | 9.2773
[24 empty] | 9+9+18 | 24 | 9 | 9 | 18 |  |  |  | 30.4794 | 7.6199 | 7.6199 | 15.2397 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 29.999 | 8.333 | 8.333 | 13.333 |  |  | 30.4794 | 7.6199 | 7.6199 | 15.2397 |  |  | 35.9864 | 8.9966 | 8.9966 | 17.9932 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 9000 | 9000 | 14000 |  |  | 35.9864 | 8.9966 | 8.9966 | 17.9932 |  |  | 23.1932 | 5.7983 | 5.7983 | 11.5966
[24 empty] | 9+12+12 | 24 | 9 | 12 | 12 |  |  |  | 30.4794 | 8.3126 | 11.0834 | 11.0834 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 28.5 | 8.5 | 10 | 10 |  |  | 30.4794 | 8.3126 | 11.0834 | 11.0834 |  |  | 35.9864 | 9.8145 | 13.086 | 13.086 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 8500 | 11500 | 11500 |  |  | 35.9864 | 9.8145 | 13.086 | 13.086 |  |  | 23.1932 | 6.3254 | 8.4339 | 8.4339
[24 empty] | 12+12+12 | 24 | 12 | 12 | 12 |  |  |  | 30.4794 | 10.1598 | 10.1598 | 10.1598 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 29.001 | 9.667 | 9.667 | 9.667 |  |  | 30.4794 | 10.1598 | 10.1598 | 10.1598 |  |  | 35.9864 | 11.9955 | 11.9955 | 11.9955 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 10667 | 10667 | 10667 |  |  | 35.9864 | 11.9955 | 11.9955 | 11.9955 |  |  | 23.1932 | 7.7311 | 7.7311 | 7.7311
[24 empty] | 30K | 30 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[24 empty] | 9+9 | 30 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20 | 10 | 10 |  |  |  | 37.9094 | 18.9547 | 18.9547 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | Zone 1: 11.956; Zone 2: 11.956; Zone 1: 10500; Zone 2: 10500 | 36.901 | 18.4505 | 18.4505 |  |  |  | 16.2181 | 8.109 | 8.109
[24 empty] | 9+12 | 30 | 9 | 12 |  |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 21.5 | 9.5 | 12 |  |  |  | 37.9094 | 16.2469 | 21.6625 |  |  |  | 26.901 | 11.956 | 14.945 |  |  |  | 26.901 | Zone 1: 11.956; Zone 2: 14.945; Zone 1: 10000; Zone 2: 13000 | 36.901 | 15.8147 | 21.0863 |  |  |  | 18.2453 | 8.109 | 10.1363
[24 empty] | 9+18 | 30 | 9 | 18 |  |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 37.9094 | 12.6365 | 25.273 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 36.901 | 12.3003 | 24.6006 |  |  |  | 23.4706 | 8.109 | 15.3616
| COOLING PERFORMANCE DATA | [22 empty] | 9+24 | 30 | 9 | 24 |  |  |  |  | 34.7912 | 10.3389 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33 | 9 | 24 |  |  |  | 37.9094 | 10.3389 | 27.5705 |  |  |  | 36.901 | 10.0639 | 26.8371 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 36.901 | 10.0639 | 26.8371 |  |  |  | 26.9636 | 8.0128 | 18.9508
| Model | Cooling |  |  | Outdoor conditions (DB) | [18 empty] | 12+12 | 30 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 24 | 12 | 12 |  |  |  | 37.9094 | 18.9547 | 18.9547 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 36.901 | 18.4505 | 18.4505 |  |  |  | 20.2726 | 10.1363 | 10.1363
|  | Indoor Conditions DB | [21 empty] | 12+18 | 30 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 37.9094 | 15.1638 | 22.7457 |  |  |  | 36.901 | 14.7604 | 22.1406 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 18000 | 36.901 | 14.7604 | 22.1406 |  |  |  | 25.4979 | 10.1363 | 15.3616
|  | DB | WB |  | -13 | -4 | 0 | 5 | 17 | 47 | 77 | 86 | 95 | 104 | 113 | 122.0001 |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | CAPACITY |  |  | 12+24 | 30 | 12 | 24 |  |  |  |  | 37.0887 | 12.6365 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 34 | 11 | 23 |  |  |  | 37.9094 | 12.6365 | 25.273 |  |  |  | 36.901 | 12.3003 | 24.6006 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 12000; Zone 2: 24000 | 36.901 | 12.3003 | 24.6006 |  |  |  | 28.7442 | 9.7934 | 18.9508
| 18 | 69.8 | 59 | TC | 18.71 | 19.255 | 19.045 | 19.005 | 18.875 | 19.905 | 21.02 | 19.205 | 17.225 | 11.64 | 11.11 | 9.875 | 17.225 | INTERPOLATION | 20.7644 | 18 | 20.7644 |  |  | 18+18 | 30 | 18 | 18 |  |  |  |  | 37.9094 | 18.9547 | 18.9547 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 33 | 16.5 | 16.5 |  |  |  | 37.9094 | 18.9547 | 18.9547 |  |  |  | 36.901 | 18.4505 | 18.4505 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 17000; Zone 2: 17000 | 36.901 | 18.4505 | 18.4505 |  |  |  | 29.3803 | 14.6901 | 14.6901
| 18 | 75.2 | 62.6 | TC | 20.15 | 20.795 | 20.565 | 20.53 | 20.385 | 21.5 | 22.7 | 20.745 | 18.6 | 12.57 | 12 | 10.13 | 18.6 | [6 empty] | 9+9+9 | 30 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 27.999 | 9.333 | 9.333 | 9.333 |  |  | 37.9094 | 12.6365 | 12.6365 | 12.6365 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 9667 | 9667 | 9667 |  |  | 36.901 | 12.3003 | 12.3003 | 12.3003 |  |  | 24.3271 | 8.109 | 8.109 | 8.109
| 18 | 80.6 | 66.2 | TC | 21.525 | 22 | 21.895 | 22.11 | 22.355 | 23.105 | 24.085 | 22.85 | 21.035 | 14.27 | 12.89 | 10.505 | 21.035 | EXTRAPOLATION | 20.304 |  |  |  |  | 9+9+12 | 30 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 30 | 9 | 9 | 12 |  |  | 37.9094 | 11.3728 | 11.3728 | 15.1638 |  |  | 36.901 | 11.0703 | 11.0703 | 14.7604 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 9500 | 9500 | 12500 |  |  | 36.901 | 11.0703 | 11.0703 | 14.7604 |  |  | 26.3544 | 8.109 | 8.109 | 10.1363
| 18 | 89.6 | 73.4 | TC | 23.465 | 23.98 | 23.865 | 24.1 | 24.37 | 25.185 | 26.255 | 24.91 | 22.93 | 15.55 | 14.05 | 11.45 | 22.93 | [6 empty] | 9+9+18 | 30 | 9 | 9 | 18 |  |  |  | 37.9094 | 9.4774 | 9.4774 | 18.9547 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 33 | 8.5 | 8.5 | 16 |  |  | 37.9094 | 9.4774 | 9.4774 | 18.9547 |  |  | 36.901 | 9.2252 | 9.2252 | 18.4505 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 8500 | 8500 | 17000 |  |  | 36.901 | 9.2252 | 9.2252 | 18.4505 |  |  | 29.3803 | 7.3451 | 7.3451 | 14.6901
| 24 | 69.8 | 59 | TC | 29.485 | 30.145 | 30 | 30.03 | 29.69 | 30.155 | 29.745 | 26.08 | 23.625 | 19.23 | 16.87 | 14.855 | 23.625 | INTERPOLATION | 30.4794 | 24 | 30.4794 |  |  | 9+9+24 | 30 | 9 | 9 | 24 |  |  |  | 37.9094 | 8.1235 | 8.1235 | 21.6625 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 35 | 7.5 | 7.5 | 20 |  |  | 37.9094 | 8.1235 | 8.1235 | 21.6625 |  |  | 36.901 | 7.9073 | 7.9073 | 21.0863 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 8500 | 8500 | 21000 |  |  | 36.901 | 7.9073 | 7.9073 | 21.0863 |  |  | 29.3803 | 6.2958 | 6.2958 | 16.7887
| 24 | 75.2 | 62.6 | TC | 31.85 | 32.56 | 32.4 | 32.435 | 32.065 | 32.565 | 32.125 | 28.17 | 25.515 | 20.77 | 18.215 | 16.045 | 25.515 | [6 empty] | 9+12+12 | 30 | 9 | 12 | 12 |  |  |  | 36.4967 | 10.3389 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 31.5 | 8.5 | 11.5 | 11.5 |  |  | 37.9094 | 10.3389 | 13.7853 | 13.7853 |  |  | 36.901 | 10.0639 | 13.4185 | 13.4185 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 9000 | 12000 | 12000 |  |  | 36.901 | 10.0639 | 13.4185 | 13.4185 |  |  | 28.2854 | 8.0128 | 10.1363 | 10.1363
| 24 | 80.6 | 66.2 | TC | 34.575 | 35.34 | 35.335 | 35.15 | 35.345 | 35.55 | 35.465 | 33.515 | 31.1 | 23.66 | 22.26 | 19.31 | 31.1 | EXTRAPOLATION | 29.0009 |  |  |  |  | 9+12+18 | 30 | 9 | 12 | 18 |  |  |  | 37.9094 | 8.7483 | 11.6644 | 17.4967 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 34 | 8 | 11 | 15 |  |  | 37.9094 | 8.7483 | 11.6644 | 17.4967 |  |  | 36.901 | 8.5156 | 11.3541 | 17.0312 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 8500 | 11500 | 16000 |  |  | 36.901 | 8.5156 | 11.3541 | 17.0312 |  |  | 29.3803 | 6.7801 | 9.0401 | 13.5601
| 24 | 89.6 | 73.4 | TC | 36.995 | 37.815 | 37.81 | 37.615 | 37.82 | 38.04 | 37.95 | 35.86 | 33.275 | 25.315 | 23.82 | 20.66 | 33.275 | [6 empty] | 9+12+24 | 30 | 9 | 12 | 24 |  |  |  | 37.9094 | 7.5819 | 10.1092 | 20.2184 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 36 | 7 | 9 | 20 |  |  | 37.9094 | 7.5819 | 10.1092 | 20.2184 |  |  | 36.901 | 7.3802 | 9.8403 | 19.6805 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 8500 | 9500 | 21000 |  |  | 36.901 | 7.3802 | 9.8403 | 19.6805 |  |  | 29.3803 | 5.8761 | 7.8347 | 15.6695
| 30 | 69.8 | 59 | TC | 36.955 | 37.775 | 37.73 | 37.58 | 37.665 | 38.505 | 38.375 | 36.625 | 34.69 | 26.57 | 24.56 | 21.805 | 34.69 | INTERPOLATION | 37.9094 | 30 | 37.9094 |  |  | 9+18+18 | 30 | 9 | 18 | 18 |  |  |  | 37.9094 | 7.5819 | 15.1638 | 15.1638 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 36 | 8 | 14 | 14 |  |  | 37.9094 | 7.5819 | 15.1638 | 15.1638 |  |  | 36.901 | 7.3802 | 14.7604 | 14.7604 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 8500 | 14500 | 14500 |  |  | 36.901 | 7.3802 | 14.7604 | 14.7604 |  |  | 29.3803 | 5.8761 | 11.7521 | 11.7521
| 30 | 75.2 | 62.6 | TC | 38.06 | 38.905 | 38.865 | 38.71 | 38.795 | 39.66 | 39.91 | 39.555 | 37.465 | 28.695 | 26.52 | 23.55 | 37.465 | [6 empty] | 12+12+12 | 30 | 12 | 12 | 12 |  |  |  | 37.9094 | 12.6365 | 12.6365 | 12.6365 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 33.999 | 11.333 | 11.333 | 11.333 |  |  | 37.9094 | 12.6365 | 12.6365 | 12.6365 |  |  | 36.901 | 12.3003 | 12.3003 | 12.3003 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 12000 | 12000 | 12000 |  |  | 36.901 | 12.3003 | 12.3003 | 12.3003 |  |  | 29.3803 | 9.7934 | 9.7934 | 9.7934
| 30 | 80.6 | 66.2 | TC | 40.45 | 41.34 | 41.465 | 41.905 | 41.59 | 41.615 | 41.265 | 39.77 | 37.965 | 30.74 | 28.805 | 25.53 | 37.965 | EXTRAPOLATION | 38.141 |  |  |  |  | 12+12+18 | 30 | 12 | 12 | 18 |  |  |  | 37.9094 | 10.8313 | 10.8313 | 16.2469 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 36 | 11 | 11 | 14 |  |  | 37.9094 | 10.8313 | 10.8313 | 16.2469 |  |  | 36.901 | 10.5431 | 10.5431 | 15.8147 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12000 | 12000 | 15000 |  |  | 36.901 | 10.5431 | 10.5431 | 15.8147 |  |  | 29.3803 | 8.3944 | 8.3944 | 12.5915
| 30 | 89.6 | 73.4 | TC | 43.68 | 44.645 | 44.78 | 45.255 | 44.92 | 44.945 | 44.565 | 42.95 | 41.005 | 33.195 | 31.11 | 27.57 | 41.005 | [6 empty] | 12+18+18 | 30 | 12 | 18 | 18 |  |  |  | 37.9094 | 9.4774 | 14.216 | 14.216 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 35.999 | 9.333 | 13.333 | 13.333 |  |  | 37.9094 | 9.4774 | 14.216 | 14.216 |  |  | 36.901 | 9.2252 | 13.8379 | 13.8379 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 10000 | 14500 | 14500 |  |  | 36.901 | 9.2252 | 13.8379 | 13.8379 |  |  | 29.3803 | 7.3451 | 11.0176 | 11.0176
| 36 | 69.8 | 59 | TC | 36.85 | 37.665 | 37.235 | 37.915 | 38.295 | 39.295 | 39.75 | 35.845 | 33.01 | 27.06 | 24.875 | 22.67 | 33.01 | INTERPOLATION | 39.9611 | 36 | 39.9611 |  |  | 12+12+24 | 30 | 12 | 12 | 24 |  |  |  | 37.9094 | 9.4774 | 9.4774 | 18.9547 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 36 | 8 | 8 | 20 |  |  | 37.9094 | 9.4774 | 9.4774 | 18.9547 |  |  | 36.901 | 9.2252 | 9.2252 | 18.4505 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 9000 | 9000 | 21000 |  |  | 36.901 | 9.2252 | 9.2252 | 18.4505 |  |  | 29.3803 | 7.3451 | 7.3451 | 14.6901
| 36 | 75.2 | 62.6 | TC | 38.86 | 39.715 | 39.255 | 39.97 | 40.37 | 41.425 | 42.11 | 38.71 | 35.65 | 29.22 | 26.865 | 24.485 | 35.65 | [6 empty] | 9+9+9+9 | 30 | 9 | 9 | 9 | 9 |  | 4 | 37.9094 | 9.4774 | 9.4774 | 9.4774 | 9.4774 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 36 | 9 | 9 | 9 | 9 |  | 37.9094 | 9.4774 | 9.4774 | 9.4774 | 9.4774 |  | 36.901 | 9.2252 | 9.2252 | 9.2252 | 9.2252 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 36.901 | 9.2252 | 9.2252 | 9.2252 | 9.2252 |  | 29.3803 | 7.3451 | 7.3451 | 7.3451 | 7.3451
| 36 | 80.6 | 66.2 | TC | 41.68 | 42.6 | 42.28 | 43.1 | 43.48 | 43.95 | 44.845 | 42.69 | 40.5 | 33.62 | 31.17 | 26.515 | 40.5 | EXTRAPOLATION | 38.7128 |  |  |  |  | 9+9+9+12 | 30 | 9 | 9 | 9 | 12 |  |  | 37.9094 | 8.7483 | 8.7483 | 8.7483 | 11.6644 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 36.5 | 8.5 | 8.5 | 8.5 | 11 |  | 37.9094 | 8.7483 | 8.7483 | 8.7483 | 11.6644 |  | 36.901 | 8.5156 | 8.5156 | 8.5156 | 11.3541 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9000 | 9000 | 9000 | 12000 |  | 36.901 | 8.5156 | 8.5156 | 8.5156 | 11.3541 |  | 29.3803 | 6.7801 | 6.7801 | 6.7801 | 9.0401
| 36 | 89.6 | 73.4 | TC | 44.4 | 45.385 | 45.045 | 45.915 | 46.32 | 46.825 | 47.775 | 45.48 | 43.145 | 35.82 | 33.205 | 28.265 | 43.145 | [6 empty] | 9+9+9+18 | 30 | 9 | 9 | 9 | 18 |  |  | 37.9094 | 7.5819 | 7.5819 | 7.5819 | 15.1638 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 37 | 8 | 8 | 8 | 13 |  | 37.9094 | 7.5819 | 7.5819 | 7.5819 | 15.1638 |  | 36.901 | 7.3802 | 7.3802 | 7.3802 | 14.7604 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 8500 | 8500 | 8500 | 14000 |  | 36.901 | 7.3802 | 7.3802 | 7.3802 | 14.7604 |  | 29.3803 | 5.8761 | 5.8761 | 5.8761 | 11.7521
| 48 | 69.8 | 59 | TC | 40.355 | 41.25 | 41.46 | 41.37 | 40.69 | 41.47 | 40.86 | 38.865 | 35.75 | 32.195 | 28.92 | 26.01 | 35.75 | INTERPOLATION | 48.49 | 48 | 48.49 |  |  | 9+9+12+12 | 30 | 9 | 9 | 12 | 12 |  |  | 37.9094 | 8.1235 | 8.1235 | 10.8313 | 10.8313 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 37 | 8 | 8 | 10.5 | 10.5 |  | 37.9094 | 8.1235 | 8.1235 | 10.8313 | 10.8313 |  | 36.901 | 7.9073 | 7.9073 | 10.5431 | 10.5431 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 8500 | 8500 | 11000 | 11000 |  | 36.901 | 7.9073 | 7.9073 | 10.5431 | 10.5431 |  | 29.3803 | 6.2958 | 6.2958 | 8.3944 | 8.3944
| 48 | 75.2 | 62.6 | TC | 43.585 | 44.55 | 44.775 | 44.68 | 43.945 | 44.79 | 44.13 | 41.975 | 38.61 | 34.77 | 31.235 | 28.09 | 38.61 | [6 empty] | 9+9+12+18 | 30 | 9 | 9 | 12 | 18 |  |  | 37.9094 | 7.108 | 7.108 | 9.4774 | 14.216 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 38 | 7.5 | 7.5 | 9 | 14 |  | 37.9094 | 7.108 | 7.108 | 9.4774 | 14.216 |  | 36.901 | 6.9189 | 6.9189 | 9.2252 | 13.8379 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 8000 | 8000 | 9500 | 14500 |  | 36.901 | 6.9189 | 6.9189 | 9.2252 | 13.8379 |  | 29.3803 | 5.5088 | 5.5088 | 7.3451 | 11.0176
| 48 | 80.6 | 66.2 | TC | 52.785 | 53.95 | 53.805 | 54.08 | 54.28 | 54.64 | 56.405 | 53.225 | 49.725 | 39.935 | 37.565 | 33.68 | 49.725 | EXTRAPOLATION | 45.1547 |  |  |  |  | 9+12+12+12 | 30 | 9 | 12 | 12 | 12 |  |  | 37.9094 | 7.5819 | 10.1092 | 10.1092 | 10.1092 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 37 | 7 | 10 | 10 | 10 |  | 37.9094 | 7.5819 | 10.1092 | 10.1092 | 10.1092 |  | 36.901 | 7.3802 | 9.8403 | 9.8403 | 9.8403 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 8000 | 10500 | 10500 | 10500 |  | 36.901 | 7.3802 | 9.8403 | 9.8403 | 9.8403 |  | 29.3803 | 5.8761 | 7.8347 | 7.8347 | 7.8347
| 48 | 89.6 | 73.4 | TC | 55.425 | 56.65 | 56.495 | 56.785 | 56.995 | 57.375 | 59.225 | 55.885 | 52.21 | 41.935 | 39.445 | 35.4 | 52.21 | [6 empty] | 12+12+12+12 | 30 | 12 | 12 | 12 | 12 |  |  | 37.9094 | 9.4774 | 9.4774 | 9.4774 | 9.4774 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 38 | 9.5 | 9.5 | 9.5 | 9.5 |  | 37.9094 | 9.4774 | 9.4774 | 9.4774 | 9.4774 |  | 36.901 | 9.2252 | 9.2252 | 9.2252 | 9.2252 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 10000 | 10000 | 10000 | 10000 |  | 36.901 | 9.2252 | 9.2252 | 9.2252 | 9.2252 |  | 29.3803 | 7.3451 | 7.3451 | 7.3451 | 7.3451
| 18 | 69.8 | 59 | SC | 13.96 | 14.275 | 14.12 | 14.08 | 13.97 | 14.76 | 16.085 | 14.995 | 14.165 | 11.455 | 10.91 | 9.81 | [7 empty] | 36K | 36 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
| 18 | 75.2 | 62.6 | SC | 14.59 | 14.855 | 14.81 | 15.195 | 15.285 | 16.335 | 17.71 | 16.385 | 15.255 | 11.185 | 11.4 | 9.93 | [7 empty] | 9+18 | 36 | 9 | 18 |  |  |  | 2 | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 39.9611 | 13.3204 | 26.6407 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 49.5103 | 16.5034 | 33.0069 |  |  |  | 24.1525 | 8.3446 | 15.8079
| 18 | 80.6 | 66.2 | SC | 15.62 | 15.965 | 15.885 | 16.615 | 16.22 | 16.775 | 17.235 | 16.595 | 15.415 | 13.315 | 12.63 | 10.445 | [7 empty] | 9+24 | 36 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33.5 | 9.5 | 24 |  |  |  | 39.9611 | 10.8985 | 29.0626 |  |  |  | 42.246 | 11.956 | 30.29 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 49.5103 | 13.5028 | 36.0075 |  |  |  | 27.846 | 8.3446 | 19.5014
| 18 | 89.6 | 73.4 | SC | 16.89 | 17.265 | 17.425 | 17.835 | 18.275 | 18.385 | 21.525 | 20.925 | 19.715 | 14.62 | 13.49 | 11.22 | [7 empty] | 12+12 | 36 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 25 | 12.5 | 12.5 |  |  |  | 39.9611 | 19.9806 | 19.9806 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 49.5103 | 24.7552 | 24.7552 |  |  |  | 20.8616 | 10.4308 | 10.4308
| 24 | 69.8 | 59 | SC | 20.645 | 21.105 | 21 | 21.02 | 20.785 | 21.11 | 23.15 | 21.375 | 20.31 | 18.12 | 16.535 | 14.805 | [7 empty] | 12+18 | 36 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 39.9611 | 15.9844 | 23.9767 |  |  |  | 39.5438 | 14.945 | 24.5988 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 19000 | 49.5103 | 19.8041 | 29.7062 |  |  |  | 26.2387 | 10.4308 | 15.8079
| 24 | 75.2 | 62.6 | SC | 22.295 | 22.79 | 22.68 | 22.705 | 22.45 | 22.8 | 24.095 | 23.095 | 21.945 | 18.69 | 17.31 | 15.885 | [7 empty] | 12+24 | 36 | 12 | 24 |  |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 36 | 12 | 24 |  |  |  | 39.9611 | 13.3204 | 26.6407 |  |  |  | 45.235 | 14.945 | 30.29 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 49.5103 | 16.5034 | 33.0069 |  |  |  | 29.9321 | 10.4308 | 19.5014
| 24 | 80.6 | 66.2 | SC | 24.205 | 24.74 | 24.735 | 24.605 | 24.745 | 24.885 | 24.995 | 24.275 | 23.28 | 20.425 | 22.06 | 19.215 | [7 empty] | 18+18 | 36 | 18 | 18 |  |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 37 | 18.5 | 18.5 |  |  |  | 39.9611 | 19.9806 | 19.9806 |  |  |  | 49.1976 | 24.5988 | 24.5988 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 19000; Zone 2: 19000 | 49.5103 | 24.7552 | 24.7552 |  |  |  | 31.6158 | 15.8079 | 15.8079
| 24 | 89.6 | 73.4 | SC | 25.895 | 26.47 | 26.465 | 26.325 | 26.47 | 28.91 | 31.12 | 30.485 | 29.62 | 23.29 | 22.865 | 20.66 | [7 empty] | 18+24 | 36 | 18 | 24 |  |  |  |  | 39.9611 | 17.1262 | 22.8349 |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 40 | 17.5 | 22.5 |  |  |  | 39.9611 | 17.1262 | 22.8349 |  |  |  | 49.5103 | 21.2187 | 28.2916 |  |  |  | 54.8888 | Zone 1: 24.5988; Zone 2: 30.29; Zone 1: 18000; Zone 2: 23000 | 49.5103 | 21.2187 | 28.2916 |  |  |  | 31.8701 | 13.6586 | 18.2115
| 30 | 69.8 | 59 | SC | 25.865 | 26.44 | 26.415 | 26.305 | 26.37 | 27.975 | 29.755 | 28.95 | 28.065 | 24.465 | 24.08 | 21.305 | [7 empty] | 24+24 | 36 | 24 | 24 |  |  |  |  | 39.9611 | 19.9806 | 19.9806 |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 42 | 21 | 21 |  |  |  | 39.9611 | 19.9806 | 19.9806 |  |  |  | 49.5103 | 24.7552 | 24.7552 |  |  |  | 60.58 | Zone 1: 30.29; Zone 2: 30.29; Zone 1: 22000; Zone 2: 22000 | 49.5103 | 24.7552 | 24.7552 |  |  |  | 31.8701 | 15.9351 | 15.9351
| 30 | 75.2 | 62.6 | SC | 26.65 | 27.24 | 27.2 | 27.095 | 27.155 | 29.745 | 32.725 | 34.81 | 33.72 | 26.4 | 25.2 | 23.08 | [7 empty] | 9+9+9 | 36 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 28.5 | 9.5 | 9.5 | 9.5 |  |  | 39.9611 | 13.3204 | 13.3204 | 13.3204 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 11000 | 11000 | 11000 |  |  | 49.5103 | 16.5034 | 16.5034 | 16.5034 |  |  | 25.0339 | 8.3446 | 8.3446 | 8.3446
| 30 | 80.6 | 66.2 | SC | 28.315 | 28.94 | 29.025 | 29.195 | 29.115 | 30.195 | 31.315 | 29.595 | 28.83 | 26.26 | 28.12 | 25.155 | [7 empty] | 9+9+12 | 36 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 31 | 9.5 | 9.5 | 12 |  |  | 39.9611 | 11.9883 | 11.9883 | 15.9844 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 10500 | 10500 | 13000 |  |  | 49.5103 | 14.8531 | 14.8531 | 19.8041 |  |  | 27.1201 | 8.3446 | 8.3446 | 10.4308
| 30 | 89.6 | 73.4 | SC | 30.58 | 31.255 | 31.35 | 31.675 | 31.445 | 33.705 | 36.545 | 37.795 | 36.9 | 30.54 | 29.555 | 27.57 | [7 empty] | 9+9+18 | 36 | 9 | 9 | 18 |  |  |  | 39.8017 | 9.9903 | 9.9903 | 19.8211 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 37 | 9.5 | 9.5 | 18 |  |  | 39.9611 | 9.9903 | 9.9903 | 19.9806 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 10000 | 10000 | 19000 |  |  | 49.5103 | 12.3776 | 12.3776 | 24.7552 |  |  | 31.743 | 7.9675 | 7.9675 | 15.8079
| 36 | 69.8 | 59 | SC | 25.795 | 26.365 | 26.065 | 26.54 | 27.205 | 28.52 | 30.425 | 28.49 | 27.26 | 23.795 | 23.81 | 22.205 | [7 empty] | 9+9+24 | 36 | 9 | 9 | 24 |  |  |  | 39.9611 | 8.5631 | 8.5631 | 22.8349 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 40.5 | 9 | 9 | 22.5 |  |  | 39.9611 | 8.5631 | 8.5631 | 22.8349 |  |  | 49.5103 | 10.6094 | 10.6094 | 28.2916 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 9500 | 9500 | 23500 |  |  | 49.5103 | 10.6094 | 10.6094 | 28.2916 |  |  | 31.8701 | 6.8293 | 6.8293 | 18.2115
| 36 | 75.2 | 62.6 | SC | 27.78 | 28.39 | 28.065 | 28.575 | 28.865 | 31.485 | 34.735 | 33.505 | 31.565 | 26.6 | 26.17 | 24.23 | [7 empty] | 9+12+12 | 36 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 34.5 | 9.5 | 12.5 | 12.5 |  |  | 39.9611 | 10.8985 | 14.5313 | 14.5313 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 10000 | 12500 | 12500 |  |  | 49.5103 | 13.5028 | 18.0038 | 18.0038 |  |  | 29.2062 | 8.3446 | 10.4308 | 10.4308
| 36 | 80.6 | 66.2 | SC | 29.175 | 29.82 | 29.6 | 30.175 | 30.435 | 31.895 | 33.445 | 32.485 | 31.855 | 28.39 | 30.305 | 26.245 | [7 empty] | 9+12+18 | 36 | 9 | 12 | 18 |  |  |  | 39.9611 | 9.2218 | 12.2957 | 18.4436 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 39 | 9 | 12 | 18 |  |  | 39.9611 | 9.2218 | 12.2957 | 18.4436 |  |  | 49.2214 | 11.4255 | 14.945 | 22.8509 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 9500 | 12500 | 18000 |  |  | 49.5103 | 11.4255 | 15.2339 | 22.8509 |  |  | 31.8701 | 7.3546 | 9.8062 | 14.7093
| 36 | 89.6 | 73.4 | SC | 31.935 | 32.64 | 32.395 | 33.025 | 33.315 | 35.795 | 39.405 | 39.585 | 38.83 | 33.47 | 32.345 | 28.265 | [7 empty] | 9+12+24 | 36 | 9 | 12 | 24 |  |  |  | 39.9611 | 7.9922 | 10.6563 | 21.3126 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 42.5 | 9 | 12 | 21.5 |  |  | 39.9611 | 7.9922 | 10.6563 | 21.3126 |  |  | 49.5103 | 9.9021 | 13.2028 | 26.4055 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 9500 | 12500 | 22000 |  |  | 49.5103 | 9.9021 | 13.2028 | 26.4055 |  |  | 31.8701 | 6.374 | 8.4987 | 16.9974
| 48 | 69.8 | 59 | SC | 28.255 | 28.88 | 29.025 | 28.96 | 28.485 | 30.275 | 37.065 | 36.16 | 35.07 | 31.915 | 28.92 | 26.01 | [7 empty] | 9+18+18 | 36 | 9 | 18 | 18 |  |  |  | 39.9611 | 7.9922 | 15.9844 | 15.9844 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 45 | 9 | 18 | 18 |  |  | 39.9611 | 7.9922 | 15.9844 | 15.9844 |  |  | 49.5103 | 9.9021 | 19.8041 | 19.8041 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 9500 | 18500 | 18500 |  |  | 49.5103 | 9.9021 | 19.8041 | 19.8041 |  |  | 31.8701 | 6.374 | 12.7481 | 12.7481
| 48 | 75.2 | 62.6 | SC | 31.815 | 32.52 | 32.685 | 32.615 | 32.08 | 34.485 | 36.625 | 35.68 | 33.59 | 31.295 | 31.235 | 28.09 | [7 empty] | 9+18+24 | 36 | 9 | 18 | 24 |  |  |  | 39.9611 | 7.052 | 14.1039 | 18.8052 |  |  | 54.7364 | 10.4631 | 19.8211 | 24.4522 |  |  | 46 | 8.5 | 16 | 21.5 |  |  | 39.9611 | 7.052 | 14.1039 | 18.8052 |  |  | 49.5103 | 8.7371 | 17.4742 | 23.299 |  |  | 66.8448 | 11.956 | 24.5988 | 30.29 |  |  | 9000 | 17000 | 22000 |  |  | 49.5103 | 8.7371 | 17.4742 | 23.299 |  |  | 31.8701 | 5.6241 | 11.2483 | 14.9977
| 48 | 80.6 | 66.2 | SC | 38.295 | 39.145 | 39.03 | 39.56 | 39.4 | 39.665 | 41.675 | 40.36 | 38.755 | 37.125 | 37.16 | 33.68 | [7 empty] | 9+24+24 | 36 | 9 | 24 | 24 |  |  |  | 39.9611 | 6.3096 | 16.8257 | 16.8257 |  |  | 59.3676 | 10.4631 | 24.4522 | 24.4522 |  |  | 48 | 8 | 20 | 20 |  |  | 39.9611 | 6.3096 | 16.8257 | 16.8257 |  |  | 49.5103 | 7.8174 | 20.8465 | 20.8465 |  |  | 72.536 | 11.956 | 30.29 | 30.29 |  |  | 8500 | 21000 | 21000 |  |  | 49.5103 | 7.8174 | 20.8465 | 20.8465 |  |  | 31.8701 | 5.0321 | 13.419 | 13.419
| 48 | 89.6 | 73.4 | SC | 41.01 | 41.915 | 41.81 | 42.02 | 42.175 | 44.75 | 49.16 | 48.065 | 46.99 | 39.835 | 39.445 | 35.4 | [7 empty] | 12+12+12 | 36 | 12 | 12 | 12 |  |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 36 | 12 | 12 | 12 |  |  | 39.9611 | 13.3204 | 13.3204 | 13.3204 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 13000 | 13000 | 13000 |  |  | 49.5103 | 16.5034 | 16.5034 | 16.5034 |  |  | 31.2924 | 10.4308 | 10.4308 | 10.4308
| 18 | 69.8 | 59 | SCR | 74.61% | 74.14% | 74.14% | 74.09% | 74.01% | 74.15% | 76.52% | 78.08% | 82.24% | 98.41% | 98.2% | 99.34% | 82.24% | INTERPOLATION | 74.25% | 18 | 74.25% |  |  | 12+12+18 | 36 | 12 | 12 | 18 |  |  |  | 39.9611 | 11.4175 | 11.4175 | 17.1262 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 41 | 12 | 12 | 17 |  |  | 39.9611 | 11.4175 | 11.4175 | 17.1262 |  |  | 49.5103 | 14.1458 | 14.1458 | 21.2187 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12500 | 12500 | 18000 |  |  | 49.5103 | 14.1458 | 14.1458 | 21.2187 |  |  | 31.8701 | 9.1058 | 9.1058 | 13.6586
| 18 | 75.2 | 62.6 | SCR | 72.41% | 71.44% | 72.02% | 74.01% | 74.98% | 75.98% | 78.02% | 78.98% | 82.02% | 88.98% | 95% | 98.03% | 82.02% | [6 empty] | 12+12+24 | 36 | 12 | 12 | 24 |  |  |  | 39.9611 | 9.9903 | 9.9903 | 19.9806 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 44 | 11 | 11 | 22 |  |  | 39.9611 | 9.9903 | 9.9903 | 19.9806 |  |  | 49.5103 | 12.3776 | 12.3776 | 24.7552 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 11500 | 11500 | 23000 |  |  | 49.5103 | 12.3776 | 12.3776 | 24.7552 |  |  | 31.8701 | 7.9675 | 7.9675 | 15.9351
| 18 | 80.6 | 66.2 | SCR | 72.57% | 72.57% | 72.55% | 75.15% | 72.56% | 72.6% | 71.56% | 72.63% | 73.28% | 93.31% | 97.98% | 99.43% | 73.28% | EXTRAPOLATION | 81.02% |  |  |  |  | 12+18+18 | 36 | 12 | 18 | 18 |  |  |  | 39.9611 | 9.9903 | 14.9854 | 14.9854 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 44 | 11 | 16.5 | 16.5 |  |  | 39.9611 | 9.9903 | 14.9854 | 14.9854 |  |  | 49.5103 | 12.3776 | 18.5664 | 18.5664 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 11500 | 17000 | 17000 |  |  | 49.5103 | 12.3776 | 18.5664 | 18.5664 |  |  | 31.8701 | 7.9675 | 11.9513 | 11.9513
| 18 | 89.6 | 73.4 | SCR | 71.98% | 72% | 73.01% | 74% | 74.99% | 73% | 81.98% | 84% | 85.98% | 94.02% | 96.01% | 97.99% | 85.98% | [6 empty] | 12+18+24 | 36 | 12 | 18 | 24 |  |  |  | 39.9611 | 8.8802 | 13.3204 | 17.7605 |  |  | 57.3522 | 13.0789 | 19.8211 | 24.4522 |  |  | 47.5 | 10.5 | 15.5 | 21.5 |  |  | 39.9611 | 8.8802 | 13.3204 | 17.7605 |  |  | 49.5103 | 11.0023 | 16.5034 | 22.0046 |  |  | 69.8338 | 14.945 | 24.5988 | 30.29 |  |  | 11000 | 16000 | 22000 |  |  | 49.5103 | 11.0023 | 16.5034 | 22.0046 |  |  | 31.8701 | 7.0823 | 10.6234 | 14.1645
| 24 | 69.8 | 59 | SCR | 70.02% | 70.01% | 70% | 70% | 70.01% | 70% | 77.83% | 81.96% | 85.97% | 94.23% | 98.01% | 99.66% | 85.97% | INTERPOLATION | 76.09% | 24 | 76.09% |  |  | 12+24+24 | 36 | 12 | 24 | 24 |  |  |  | 39.9611 | 7.9922 | 15.9844 | 15.9844 |  |  | 61.9833 | 13.0789 | 24.4522 | 24.4522 |  |  | 50 | 10 | 20 | 20 |  |  | 39.9611 | 7.9922 | 15.9844 | 15.9844 |  |  | 49.5103 | 9.9021 | 19.8041 | 19.8041 |  |  | 75.525 | 14.945 | 30.29 | 30.29 |  |  | 11000 | 20500 | 20500 |  |  | 49.5103 | 9.9021 | 19.8041 | 19.8041 |  |  | 31.8701 | 6.374 | 12.7481 | 12.7481
| 24 | 75.2 | 62.6 | SCR | 70% | 69.99% | 70% | 70% | 70.01% | 70.01% | 75% | 81.98% | 86.01% | 89.99% | 95.03% | 99% | 86.01% | [6 empty] | 18+18+18 | 36 | 18 | 18 | 18 |  |  |  | 39.9611 | 13.3204 | 13.3204 | 13.3204 |  |  | 59.4633 | 19.8211 | 19.8211 | 19.8211 |  |  | 48 | 16 | 16 | 16 |  |  | 39.9611 | 13.3204 | 13.3204 | 13.3204 |  |  | 49.5103 | 16.5034 | 16.5034 | 16.5034 |  |  | 73.7965 | 24.5988 | 24.5988 | 24.5988 |  |  | 16500 | 16500 | 16500 |  |  | 49.5103 | 16.5034 | 16.5034 | 16.5034 |  |  | 31.8701 | 10.6234 | 10.6234 | 10.6234
| 24 | 80.6 | 66.2 | SCR | 70.01% | 70.01% | 70% | 70% | 70.01% | 70% | 70.48% | 72.43% | 74.86% | 86.33% | 99.1% | 99.51% | 74.86% | EXTRAPOLATION | 84.03% |  |  |  |  | 18+18+24 | 36 | 18 | 18 | 24 |  |  |  | 39.9611 | 11.9883 | 11.9883 | 15.9844 |  |  | 64.0944 | 19.8211 | 19.8211 | 24.4522 |  |  | 50 | 15 | 15 | 20 |  |  | 39.9611 | 11.9883 | 11.9883 | 15.9844 |  |  | 49.5103 | 14.8531 | 14.8531 | 19.8041 |  |  | 79.4876 | 24.5988 | 24.5988 | 30.29 |  |  | 15500 | 15500 | 21000 |  |  | 49.5103 | 14.8531 | 14.8531 | 19.8041 |  |  | 31.8701 | 9.561 | 9.561 | 12.7481
| 24 | 89.6 | 73.4 | SCR | 70% | 70% | 69.99% | 69.99% | 69.99% | 76% | 82% | 85.01% | 89.02% | 92% | 95.99% | 100% | 89.02% | [6 empty] | 9+9+9+9 | 36 | 9 | 9 | 9 | 9 |  | 4 | 39.9611 | 9.9903 | 9.9903 | 9.9903 | 9.9903 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 37 | 9.25 | 9.25 | 9.25 | 9.25 |  | 39.9611 | 9.9903 | 9.9903 | 9.9903 | 9.9903 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 49.5103 | 12.3776 | 12.3776 | 12.3776 | 12.3776 |  | 31.8701 | 7.9675 | 7.9675 | 7.9675 | 7.9675
| 30 | 69.8 | 59 | SCR | 69.99% | 69.99% | 70.01% | 70% | 70.01% | 72.65% | 77.54% | 79.04% | 80.9% | 92.08% | 98.05% | 97.71% | 80.9% | INTERPOLATION | 77.5% | 30 | 77.5% |  |  | 9+9+9+12 | 36 | 9 | 9 | 9 | 12 |  |  | 39.9611 | 9.2218 | 9.2218 | 9.2218 | 12.2957 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 39 | 9 | 9 | 9 | 12 |  | 39.9611 | 9.2218 | 9.2218 | 9.2218 | 12.2957 |  | 49.2214 | 11.4255 | 11.4255 | 11.4255 | 14.945 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9500 | 9500 | 9500 | 12500 |  | 49.5103 | 11.4255 | 11.4255 | 11.4255 | 15.2339 |  | 31.8701 | 7.3546 | 7.3546 | 7.3546 | 9.8062
| 30 | 75.2 | 62.6 | SCR | 70.02% | 70.02% | 69.99% | 69.99% | 70% | 75% | 82% | 88% | 90% | 92% | 95.02% | 98% | 90% | [6 empty] | 9+9+9+18 | 36 | 9 | 9 | 9 | 18 |  |  | 39.9611 | 7.9922 | 7.9922 | 7.9922 | 15.9844 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 44 | 9 | 9 | 9 | 17 |  | 39.9611 | 7.9922 | 7.9922 | 7.9922 | 15.9844 |  | 49.5103 | 9.9021 | 9.9021 | 9.9021 | 19.8041 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 9500 | 9500 | 9500 | 17500 |  | 49.5103 | 9.9021 | 9.9021 | 9.9021 | 19.8041 |  | 31.8701 | 6.374 | 6.374 | 6.374 | 12.7481
| 30 | 80.6 | 66.2 | SCR | 70% | 70% | 70% | 69.67% | 70% | 72.56% | 75.89% | 74.42% | 75.94% | 85.43% | 97.62% | 98.53% | 75.94% | EXTRAPOLATION | 84.53% |  |  |  |  | 9+9+9+24 | 36 | 9 | 9 | 9 | 24 |  |  | 39.9611 | 7.052 | 7.052 | 7.052 | 18.8052 |  | 55.8416 | 10.4631 | 10.4631 | 10.4631 | 24.4522 |  | 46 | 8.5 | 8.5 | 8.5 | 20.5 |  | 39.9611 | 7.052 | 7.052 | 7.052 | 18.8052 |  | 49.5103 | 8.7371 | 8.7371 | 8.7371 | 23.299 |  | 66.1581 | 11.956 | 11.956 | 11.956 | 30.29 |  | 9000 | 9000 | 9000 | 21000 |  | 49.5103 | 8.7371 | 8.7371 | 8.7371 | 23.299 |  | 31.8701 | 5.6241 | 5.6241 | 5.6241 | 14.9977
| 30 | 89.6 | 73.4 | SCR | 70.01% | 70.01% | 70.01% | 69.99% | 70% | 74.99% | 82% | 88% | 89.99% | 92% | 95% | 100% | 89.99% | [6 empty] | 9+9+12+12 | 36 | 9 | 9 | 12 | 12 |  |  | 39.9611 | 8.5631 | 8.5631 | 11.4175 | 11.4175 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 42 | 9 | 9 | 12 | 12 |  | 39.9611 | 8.5631 | 8.5631 | 11.4175 | 11.4175 |  | 49.5103 | 10.6094 | 10.6094 | 14.1458 | 14.1458 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 9500 | 9500 | 13000 | 13000 |  | 49.5103 | 10.6094 | 10.6094 | 14.1458 | 14.1458 |  | 31.8701 | 6.8293 | 6.8293 | 9.1058 | 9.1058
| 36 | 69.8 | 59 | SCR | 70% | 70% | 70% | 70% | 71.04% | 72.58% | 76.54% | 79.48% | 82.58% | 87.93% | 95.72% | 97.95% | 82.58% | INTERPOLATION | 79.75% | 36 | 79.75% |  |  | 9+9+12+18 | 36 | 9 | 9 | 12 | 18 |  |  | 39.9611 | 7.4927 | 7.4927 | 9.9903 | 14.9854 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 45 | 9 | 9 | 10.5 | 16.5 |  | 39.9611 | 7.4927 | 7.4927 | 9.9903 | 14.9854 |  | 49.5103 | 9.2832 | 9.2832 | 12.3776 | 18.5664 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 9500 | 9500 | 11500 | 17500 |  | 49.5103 | 9.2832 | 9.2832 | 12.3776 | 18.5664 |  | 31.8701 | 5.9757 | 5.9757 | 7.9675 | 11.9513
| 36 | 75.2 | 62.6 | SCR | 71.49% | 71.48% | 71.49% | 71.49% | 71.5% | 76% | 82.49% | 86.55% | 88.54% | 91.03% | 97.41% | 98.96% | 88.54% | [6 empty] | 9+9+12+24 | 36 | 9 | 9 | 12 | 24 |  |  | 39.9611 | 6.6602 | 6.6602 | 8.8802 | 17.7605 |  | 58.4573 | 10.4631 | 10.4631 | 13.0789 | 24.4522 |  | 48 | 8.5 | 8.5 | 10.5 | 20.5 |  | 39.9611 | 6.6602 | 6.6602 | 8.8802 | 17.7605 |  | 49.5103 | 8.2517 | 8.2517 | 11.0023 | 22.0046 |  | 69.1471 | 11.956 | 11.956 | 14.945 | 30.29 |  | 9000 | 9000 | 11000 | 21000 |  | 49.5103 | 8.2517 | 8.2517 | 11.0023 | 22.0046 |  | 31.8701 | 5.3117 | 5.3117 | 7.0823 | 14.1645
| 36 | 80.6 | 66.2 | SCR | 70% | 70% | 70.01% | 70.01% | 70% | 72.57% | 74.58% | 76.1% | 78.65% | 84.44% | 97.22% | 98.98% | 78.65% | EXTRAPOLATION | 85.23% |  |  |  |  | 9+9+18+18 | 36 | 9 | 9 | 18 | 18 |  |  | 39.9611 | 6.6602 | 6.6602 | 13.3204 | 13.3204 |  | 60.5684 | 10.4631 | 10.4631 | 19.8211 | 19.8211 |  | 48 | 8.5 | 8.5 | 15.5 | 15.5 |  | 39.9611 | 6.6602 | 6.6602 | 13.3204 | 13.3204 |  | 49.5103 | 8.2517 | 8.2517 | 16.5034 | 16.5034 |  | 73.1097 | 11.956 | 11.956 | 24.5988 | 24.5988 |  | 9000 | 9000 | 16000 | 16000 |  | 49.5103 | 8.2517 | 8.2517 | 16.5034 | 16.5034 |  | 31.8701 | 5.3117 | 5.3117 | 10.6234 | 10.6234
| 36 | 89.6 | 73.4 | SCR | 71.93% | 71.92% | 71.92% | 71.93% | 71.92% | 76.44% | 82.48% | 87.04% | 90% | 93.44% | 97.41% | 100% | 90% | [6 empty] | 9+9+18+24 | 36 | 9 | 9 | 18 | 24 |  |  | 39.9611 | 5.9942 | 5.9942 | 11.9883 | 15.9844 |  | 65.1996 | 10.4631 | 10.4631 | 19.8211 | 24.4522 |  | 50.5 | 8 | 8 | 14.5 | 20 |  | 39.9611 | 5.9942 | 5.9942 | 11.9883 | 15.9844 |  | 49.5103 | 7.4266 | 7.4266 | 14.8531 | 19.8041 |  | 78.8009 | 11.956 | 11.956 | 24.5988 | 30.29 |  | 8500 | 8500 | 15000 | 20000 |  | 49.5103 | 7.4266 | 7.4266 | 14.8531 | 19.8041 |  | 31.8701 | 4.7805 | 4.7805 | 9.561 | 12.7481
| 48 | 69.8 | 59 | SCR | 70.02% | 70.01% | 70.01% | 70% | 70% | 73% | 90.71% | 93.04% | 98.1% | 99.13% | 100% | 100% | 98.1% | INTERPOLATION | 78.95% | 48 | 78.95% |  |  | 9+12+12+12 | 36 | 9 | 12 | 12 | 12 |  |  | 39.9611 | 7.9922 | 10.6563 | 10.6563 | 10.6563 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 45 | 9 | 12 | 12 | 12 |  | 39.9611 | 7.9922 | 10.6563 | 10.6563 | 10.6563 |  | 49.5103 | 9.9021 | 13.2028 | 13.2028 | 13.2028 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 9500 | 12500 | 12500 | 12500 |  | 49.5103 | 9.9021 | 13.2028 | 13.2028 | 13.2028 |  | 31.8701 | 6.374 | 8.4987 | 8.4987 | 8.4987
| 48 | 75.2 | 62.6 | SCR | 73% | 73% | 73% | 73% | 73% | 76.99% | 82.99% | 85% | 87% | 90.01% | 100% | 100% | 87% | [6 empty] | 9+12+12+18 | 36 | 9 | 12 | 12 | 18 |  |  | 39.9611 | 7.052 | 9.4026 | 9.4026 | 14.1039 |  | 56.442 | 10.4631 | 13.0789 | 13.0789 | 19.8211 |  | 46 | 9 | 10.5 | 10.5 | 16 |  | 39.9611 | 7.052 | 9.4026 | 9.4026 | 14.1039 |  | 49.5103 | 8.7371 | 11.6495 | 11.6495 | 17.4742 |  | 66.4449 | 11.956 | 14.945 | 14.945 | 24.5988 |  | 9500 | 11500 | 11500 | 16500 |  | 49.5103 | 8.7371 | 11.6495 | 11.6495 | 17.4742 |  | 31.8701 | 5.6241 | 7.4989 | 7.4989 | 11.2483
| 48 | 80.6 | 66.2 | SCR | 72.55% | 72.56% | 72.54% | 73.15% | 72.59% | 72.59% | 73.89% | 75.83% | 77.94% | 92.96% | 98.92% | 100% | 77.94% | EXTRAPOLATION | 87.79% |  |  |  |  | 9+12+12+24 | 36 | 9 | 12 | 12 | 24 |  |  | 39.9611 | 6.3096 | 8.4129 | 8.4129 | 16.8257 |  | 61.0731 | 10.4631 | 13.0789 | 13.0789 | 24.4522 |  | 48.5 | 8.5 | 10 | 10 | 20 |  | 39.9611 | 6.3096 | 8.4129 | 8.4129 | 16.8257 |  | 49.5103 | 7.8174 | 10.4232 | 10.4232 | 20.8465 |  | 72.1361 | 11.956 | 14.945 | 14.945 | 30.29 |  | 9000 | 10500 | 10500 | 20500 |  | 49.5103 | 7.8174 | 10.4232 | 10.4232 | 20.8465 |  | 31.8701 | 5.0321 | 6.7095 | 6.7095 | 13.419
| 48 | 89.6 | 73.4 | SCR | 73.99% | 73.99% | 74.01% | 74% | 74% | 78% | 83.01% | 86.01% | 90% | 94.99% | 100% | 100% | 90% | [6 empty] | 9+12+18+18 | 36 | 9 | 12 | 18 | 18 |  |  | 39.9611 | 6.3096 | 8.4129 | 12.6193 | 12.6193 |  | 63.1842 | 10.4631 | 13.0789 | 19.8211 | 19.8211 |  | 48.5 | 8.5 | 10 | 15 | 15 |  | 39.9611 | 6.3096 | 8.4129 | 12.6193 | 12.6193 |  | 49.5103 | 7.8174 | 10.4232 | 15.6348 | 15.6348 |  | 76.0987 | 11.956 | 14.945 | 24.5988 | 24.5988 |  | 9000 | 10500 | 15500 | 15500 |  | 49.5103 | 7.8174 | 10.4232 | 15.6348 | 15.6348 |  | 31.8701 | 5.0321 | 6.7095 | 10.0643 | 10.0643
| 18 | 69.8 | 59 | Input | 1.375 | 1.41 | 1.455 | 1.495 | 1.54 | 1.57 | 1.6 | 1.75 | 1.915 | 1.45 | 1.505 | 1.43 | [7 empty] | 9+18+18+18 | 36 | 9 | 18 | 18 | 18 |  |  | 39.9611 | 5.7087 | 11.4175 | 11.4175 | 11.4175 |  | 69.9264 | 10.4631 | 19.8211 | 19.8211 | 19.8211 |  | 50 | 8 | 14 | 14 | 14 |  | 39.9611 | 5.7087 | 11.4175 | 11.4175 | 11.4175 |  | 49.5103 | 7.0729 | 14.1458 | 14.1458 | 14.1458 |  | 85.7525 | 11.956 | 24.5988 | 24.5988 | 24.5988 |  | 8500 | 14500 | 14500 | 14500 |  | 49.5103 | 7.0729 | 14.1458 | 14.1458 | 14.1458 |  | 31.8701 | 4.5529 | 9.1058 | 9.1058 | 9.1058
| 18 | 75.2 | 62.6 | Input | 1.415 | 1.46 | 1.505 | 1.545 | 1.59 | 1.62 | 1.65 | 1.8 | 1.965 | 1.5 | 1.54 | 1.35 | [7 empty] | 12+12+12+12 | 36 | 12 | 12 | 12 | 12 |  |  | 39.9611 | 9.9903 | 9.9903 | 9.9903 | 9.9903 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 48 | 12 | 12 | 12 | 12 |  | 39.9611 | 9.9903 | 9.9903 | 9.9903 | 9.9903 |  | 49.5103 | 12.3776 | 12.3776 | 12.3776 | 12.3776 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 12500 | 12500 | 12500 | 12500 |  | 49.5103 | 12.3776 | 12.3776 | 12.3776 | 12.3776 |  | 31.8701 | 7.9675 | 7.9675 | 7.9675 | 7.9675
| 18 | 80.6 | 66.2 | Input | 1.455 | 1.49 | 1.53 | 1.575 | 1.605 | 1.625 | 1.645 | 1.835 | 2.01 | 1.485 | 1.55 | 1.47 | [7 empty] | 12+12+12+18 | 36 | 12 | 12 | 12 | 18 |  |  | 39.9611 | 8.8802 | 8.8802 | 8.8802 | 13.3204 |  | 59.0578 | 13.0789 | 13.0789 | 13.0789 | 19.8211 |  | 49 | 11 | 11 | 11 | 16 |  | 39.9611 | 8.8802 | 8.8802 | 8.8802 | 13.3204 |  | 49.5103 | 11.0023 | 11.0023 | 11.0023 | 16.5034 |  | 69.4339 | 14.945 | 14.945 | 14.945 | 24.5988 |  | 11500 | 11500 | 11500 | 16500 |  | 49.5103 | 11.0023 | 11.0023 | 11.0023 | 16.5034 |  | 31.8701 | 7.0823 | 7.0823 | 7.0823 | 10.6234
| 18 | 89.6 | 73.4 | Input | 1.505 | 1.54 | 1.58 | 1.625 | 1.655 | 1.72 | 1.695 | 1.885 | 2.14 | 1.535 | 1.6 | 1.52 | [7 empty] | 12+12+12+24 | 36 | 12 | 12 | 12 | 24 |  |  | 39.9611 | 7.9922 | 7.9922 | 7.9922 | 15.9844 |  | 63.6889 | 13.0789 | 13.0789 | 13.0789 | 24.4522 |  | 50 | 10 | 10 | 10 | 20 |  | 39.9611 | 7.9922 | 7.9922 | 7.9922 | 15.9844 |  | 49.5103 | 9.9021 | 9.9021 | 9.9021 | 19.8041 |  | 75.1251 | 14.945 | 14.945 | 14.945 | 30.29 |  | 10500 | 10500 | 10500 | 20500 |  | 49.5103 | 9.9021 | 9.9021 | 9.9021 | 19.8041 |  | 31.8701 | 6.374 | 6.374 | 6.374 | 12.7481
| 24 | 69.8 | 59 | Input | 2.1 | 2.15 | 2.16 | 2.18 | 2.2 | 2.215 | 2.235 | 2.27 | 2.505 | 2.395 | 2.53 | 2.59 | [7 empty] | 12+12+18+18 | 36 | 12 | 12 | 18 | 18 |  |  | 39.9611 | 7.9922 | 7.9922 | 11.9883 | 11.9883 |  | 65.8 | 13.0789 | 13.0789 | 19.8211 | 19.8211 |  | 50 | 10 | 10 | 15 | 15 |  | 39.9611 | 7.9922 | 7.9922 | 11.9883 | 11.9883 |  | 49.5103 | 9.9021 | 9.9021 | 14.8531 | 14.8531 |  | 79.0877 | 14.945 | 14.945 | 24.5988 | 24.5988 |  | 10500 | 10500 | 15500 | 15500 |  | 49.5103 | 9.9021 | 9.9021 | 14.8531 | 14.8531 |  | 31.8701 | 6.374 | 6.374 | 9.561 | 9.561
| 24 | 75.2 | 62.6 | Input | 2.14 | 2.19 | 2.2 | 2.22 | 2.24 | 2.255 | 2.275 | 2.31 | 2.545 | 2.435 | 2.6 | 2.63 | [7 empty] | 48K | 48 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
| 24 | 80.6 | 66.2 | Input | 2.155 | 2.2 | 2.24 | 2.34 | 2.865 | 2.415 | 2.46 | 2.735 | 3.035 | 2.485 | 2.58 | 2.685 | [7 empty] | 9+18 | 48 | 9 | 18 |  |  |  | 2 | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 48.49 | 16.1633 | 32.3267 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 54.9371 | 18.3124 | 36.6247 |  |  |  | 23.908 | 8.2601 | 15.6478
| 24 | 89.6 | 73.4 | Input | 2.22 | 2.27 | 2.31 | 2.38 | 2.935 | 2.485 | 2.53 | 2.805 | 3.105 | 2.555 | 2.65 | 2.755 | [7 empty] | 9+24 | 48 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33.5 | 9.5 | 24 |  |  |  | 48.49 | 13.2245 | 35.2655 |  |  |  | 42.246 | 11.956 | 30.29 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 54.9371 | 14.9828 | 39.9543 |  |  |  | 27.564 | 8.2601 | 19.3039
| 30 | 69.8 | 59 | Input | 3.17 | 3.24 | 3.295 | 3.3 | 3.365 | 3.42 | 3.46 | 3.655 | 4.015 | 3.14 | 3.225 | 2.76 | [7 empty] | 12+12 | 48 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 25 | 12.5 | 12.5 |  |  |  | 48.49 | 24.245 | 24.245 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 54.9371 | 27.4685 | 27.4685 |  |  |  | 20.6503 | 10.3252 | 10.3252
| 30 | 75.2 | 62.6 | Input | 3.22 | 3.29 | 3.345 | 3.35 | 3.415 | 3.47 | 3.51 | 3.705 | 4.065 | 3.19 | 3.275 | 2.81 | [7 empty] | 12+18 | 48 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 48.49 | 19.396 | 29.094 |  |  |  | 39.5438 | 14.945 | 24.5988 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 19000 | 54.9371 | 21.9748 | 32.9623 |  |  |  | 25.973 | 10.3252 | 15.6478
| 30 | 80.6 | 66.2 | Input | 3.235 | 3.305 | 3.37 | 3.425 | 3.455 | 3.53 | 3.57 | 3.715 | 4.095 | 3.235 | 3.3 | 2.775 | [7 empty] | 12+24 | 48 | 12 | 24 |  |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 36 | 12 | 24 |  |  |  | 48.49 | 16.1633 | 32.3267 |  |  |  | 45.235 | 14.945 | 30.29 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 12500; Zone 2: 25000 | 54.9371 | 18.3124 | 36.6247 |  |  |  | 29.629 | 10.3252 | 19.3039
| 30 | 89.6 | 73.4 | Input | 3.29 | 3.365 | 3.43 | 3.485 | 3.515 | 3.59 | 3.63 | 3.775 | 4.155 | 3.295 | 3.36 | 2.835 | [7 empty] | 18+18 | 48 | 18 | 18 |  |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 37 | 18.5 | 18.5 |  |  |  | 48.49 | 24.245 | 24.245 |  |  |  | 49.1976 | 24.5988 | 24.5988 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 19000; Zone 2: 19000 | 54.9371 | 27.4685 | 27.4685 |  |  |  | 31.2957 | 15.6478 | 15.6478
| 36 | 69.8 | 59 | Input | 2.73 | 2.79 | 2.86 | 2.9 | 2.94 | 3.01 | 3.06 | 3.425 | 3.83 | 3.72 | 3.8 | 3.445 | [7 empty] | 18+24 | 48 | 18 | 24 |  |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 40 | 17.5 | 22.5 |  |  |  | 48.49 | 20.7814 | 27.7086 |  |  |  | 53.8345 | 23.5445 | 30.29 |  |  |  | 54.8888 | Zone 1: 24.5988; Zone 2: 30.29; Zone 1: 18000; Zone 2: 23000 | 54.9371 | 23.5445 | 31.3926 |  |  |  | 34.9517 | 15.6478 | 19.3039
| 36 | 75.2 | 62.6 | Input | 2.79 | 2.85 | 2.92 | 2.96 | 3 | 3.07 | 3.12 | 3.485 | 3.89 | 3.78 | 3.86 | 3.505 | [7 empty] | 24+24 | 48 | 24 | 24 |  |  |  |  | 48.49 | 24.245 | 24.245 |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 42 | 21 | 21 |  |  |  | 48.49 | 24.245 | 24.245 |  |  |  | 54.9371 | 27.4685 | 27.4685 |  |  |  | 60.58 | Zone 1: 30.29; Zone 2: 30.29; Zone 1: 22000; Zone 2: 22000 | 54.9371 | 27.4685 | 27.4685 |  |  |  | 38.2806 | 19.1403 | 19.1403
| 36 | 80.6 | 66.2 | Input | 2.83 | 2.89 | 2.92 | 2.94 | 2.98 | 3.09 | 3.13 | 3.515 | 3.95 | 3.84 | 3.89 | 3.505 | [7 empty] | 9+9+9 | 48 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 28.5 | 9.5 | 9.5 | 9.5 |  |  | 48.49 | 16.1633 | 16.1633 | 16.1633 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 11000 | 11000 | 11000 |  |  | 54.9371 | 18.3124 | 18.3124 | 18.3124 |  |  | 24.7804 | 8.2601 | 8.2601 | 8.2601
| 36 | 89.6 | 73.4 | Input | 2.89 | 2.955 | 2.985 | 3.005 | 3.045 | 3.155 | 3.195 | 3.58 | 4.015 | 3.905 | 3.955 | 3.57 | [7 empty] | 9+9+12 | 48 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 31 | 9.5 | 9.5 | 12 |  |  | 48.49 | 14.547 | 14.547 | 19.396 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 10500 | 10500 | 13000 |  |  | 54.9371 | 16.4811 | 16.4811 | 21.9748 |  |  | 26.8454 | 8.2601 | 8.2601 | 10.3252
| 48 | 69.8 | 59 | Input | 2.195 | 2.24 | 2.28 | 2.35 | 2.38 | 2.41 | 2.46 | 2.78 | 3.11 | 3.45 | 3.64 | 3.08 | [7 empty] | 9+9+18 | 48 | 9 | 9 | 18 |  |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 37 | 9.5 | 9.5 | 18 |  |  | 48.49 | 12.1225 | 12.1225 | 24.245 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 10000 | 10000 | 19000 |  |  | 54.9371 | 13.7343 | 13.7343 | 27.4685 |  |  | 32.1681 | 8.2601 | 8.2601 | 15.6478
| 48 | 75.2 | 62.6 | Input | 2.26 | 2.31 | 2.35 | 2.42 | 2.45 | 2.48 | 2.53 | 2.85 | 3.18 | 3.52 | 3.71 | 3.15 | [7 empty] | 9+9+24 | 48 | 9 | 9 | 24 |  |  |  | 45.2337 | 10.3907 | 10.3907 | 24.4522 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 40.5 | 9 | 9 | 22.5 |  |  | 48.49 | 10.3907 | 10.3907 | 27.7086 |  |  | 53.8345 | 11.7722 | 11.7722 | 30.29 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 9500 | 9500 | 23500 |  |  | 54.9371 | 11.7722 | 11.7722 | 31.3926 |  |  | 35.7098 | 8.203 | 8.203 | 19.3039
| 48 | 80.6 | 66.2 | Input | 3.28 | 3.35 | 3.42 | 3.5 | 3.55 | 3.66 | 3.95 | 4.4 | 4.87 | 3.845 | 4.05 | 3.555 | [7 empty] | 9+12+12 | 48 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 34.5 | 9.5 | 12.5 | 12.5 |  |  | 48.49 | 13.2245 | 17.6327 | 17.6327 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 10000 | 13000 | 13000 |  |  | 54.9371 | 14.9828 | 19.9771 | 19.9771 |  |  | 28.9105 | 8.2601 | 10.3252 | 10.3252
| 48 | 89.6 | 73.4 | Input | 3.345 | 3.42 | 3.49 | 3.57 | 3.62 | 3.73 | 4.02 | 4.47 | 4.94 | 3.915 | 4.12 | 3.625 | [7 empty] | 9+12+18 | 48 | 9 | 12 | 18 |  |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 39 | 9 | 12 | 18 |  |  | 48.49 | 11.19 | 14.92 | 22.38 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 9500 | 12500 | 19000 |  |  | 54.9371 | 12.6778 | 16.9037 | 25.3556 |  |  | 34.2331 | 8.2601 | 10.3252 | 15.6478
| LEGEND | [22 empty] | 9+12+24 | 48 | 9 | 12 | 24 |  |  |  | 47.0809 | 9.698 | 12.9307 | 24.4522 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 42.5 | 9 | 12 | 21.5 |  |  | 48.49 | 9.698 | 12.9307 | 25.8613 |  |  | 54.9371 | 10.9874 | 14.6499 | 29.2998 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 9500 | 12500 | 22000 |  |  | 54.9371 | 10.9874 | 14.6499 | 29.2998 |  |  | 37.1681 | 7.6561 | 10.2082 | 19.3039
| DB - Dry Bulb | [22 empty] | 9+18+18 | 48 | 9 | 18 | 18 |  |  |  | 48.49 | 9.698 | 19.396 | 19.396 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 45 | 9 | 18 | 18 |  |  | 48.49 | 9.698 | 19.396 | 19.396 |  |  | 54.9371 | 10.9874 | 21.9748 | 21.9748 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 9500 | 18500 | 18500 |  |  | 54.9371 | 10.9874 | 21.9748 | 21.9748 |  |  | 38.2806 | 7.6561 | 15.3122 | 15.3122
| WB - Wet Bulb | [22 empty] | 9+18+24 | 48 | 9 | 18 | 24 |  |  |  | 48.49 | 8.5571 | 17.1141 | 22.8188 |  |  | 54.7364 | 10.4631 | 19.8211 | 24.4522 |  |  | 46 | 8.5 | 16 | 21.5 |  |  | 48.49 | 8.5571 | 17.1141 | 22.8188 |  |  | 54.9371 | 9.6948 | 19.3896 | 25.8528 |  |  | 66.8448 | 11.956 | 24.5988 | 30.29 |  |  | 9500 | 16500 | 22000 |  |  | 54.9371 | 9.6948 | 19.3896 | 25.8528 |  |  | 38.2806 | 6.7554 | 13.5108 | 18.0144
| TC - Total Net Capacity (1000 Btu/hour) | [22 empty] | 9+24+24 | 48 | 9 | 24 | 24 |  |  |  | 48.49 | 7.6563 | 20.4168 | 20.4168 |  |  | 59.3676 | 10.4631 | 24.4522 | 24.4522 |  |  | 48 | 8 | 20 | 20 |  |  | 48.49 | 7.6563 | 20.4168 | 20.4168 |  |  | 54.9371 | 8.6743 | 23.1314 | 23.1314 |  |  | 72.536 | 11.956 | 30.29 | 30.29 |  |  | 8500 | 21000 | 21000 |  |  | 54.9371 | 8.6743 | 23.1314 | 23.1314 |  |  | 38.2806 | 6.0443 | 16.1181 | 16.1181
| SC - Sensible Capacity (1000 Btu/hour) | [22 empty] | 12+12+12 | 48 | 12 | 12 | 12 |  |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 36 | 12 | 12 | 12 |  |  | 48.49 | 16.1633 | 16.1633 | 16.1633 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 13000 | 13000 | 13000 |  |  | 54.9371 | 18.3124 | 18.3124 | 18.3124 |  |  | 30.9755 | 10.3252 | 10.3252 | 10.3252
| Input - Total Power (kW) | [22 empty] | 12+12+18 | 48 | 12 | 12 | 18 |  |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 41 | 12 | 12 | 17 |  |  | 48.49 | 13.8543 | 13.8543 | 20.7814 |  |  | 53.4345 | 14.945 | 14.945 | 23.5445 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12500 | 12500 | 18000 |  |  | 54.9371 | 15.6963 | 15.6963 | 23.5445 |  |  | 36.2982 | 10.3252 | 10.3252 | 15.6478
[24 empty] | 12+12+24 | 48 | 12 | 12 | 24 |  |  |  | 48.49 | 12.1225 | 12.1225 | 24.245 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 44 | 11 | 11 | 22 |  |  | 48.49 | 12.1225 | 12.1225 | 24.245 |  |  | 54.9371 | 13.7343 | 13.7343 | 27.4685 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 11500 | 11500 | 23000 |  |  | 54.9371 | 13.7343 | 13.7343 | 27.4685 |  |  | 38.2806 | 9.5701 | 9.5701 | 19.1403
| HEATING PERFORMANCE DATA | [22 empty] | 12+18+18 | 48 | 12 | 18 | 18 |  |  |  | 48.49 | 12.1225 | 18.1837 | 18.1837 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 44 | 11 | 16.5 | 16.5 |  |  | 48.49 | 12.1225 | 18.1837 | 18.1837 |  |  | 54.9371 | 13.7343 | 20.6014 | 20.6014 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 11500 | 17000 | 17000 |  |  | 54.9371 | 13.7343 | 20.6014 | 20.6014 |  |  | 38.2806 | 9.5701 | 14.3552 | 14.3552
| Model | Heating |  |  |  | Outdoor conditions (DB) | [17 empty] | 12+18+24 | 48 | 12 | 18 | 24 |  |  |  | 48.49 | 10.7756 | 16.1633 | 21.5511 |  |  | 57.3522 | 13.0789 | 19.8211 | 24.4522 |  |  | 48 | 10.5 | 16 | 21.5 |  |  | 48.49 | 10.7756 | 16.1633 | 21.5511 |  |  | 54.9371 | 12.2082 | 18.3124 | 24.4165 |  |  | 69.8338 | 14.945 | 24.5988 | 30.29 |  |  | 11000 | 16000 | 22000 |  |  | 54.9371 | 12.2082 | 18.3124 | 24.4165 |  |  | 38.2806 | 8.5068 | 12.7602 | 17.0136
|  | Indoor Conditions DB | [21 empty] | 12+24+24 | 48 | 12 | 24 | 24 |  |  |  | 48.49 | 9.698 | 19.396 | 19.396 |  |  | 61.9833 | 13.0789 | 24.4522 | 24.4522 |  |  | 50 | 10 | 20 | 20 |  |  | 48.49 | 9.698 | 19.396 | 19.396 |  |  | 54.9371 | 10.9874 | 21.9748 | 21.9748 |  |  | 75.525 | 14.945 | 30.29 | 30.29 |  |  | 11000 | 20500 | 20500 |  |  | 54.9371 | 10.9874 | 21.9748 | 21.9748 |  |  | 38.2806 | 7.6561 | 15.3122 | 15.3122
[5 empty] | -22 | -13 | -4 | 0 | 5 | 17 | 19.4 | 24.8 | 32 | 39.2 | 44.6 | 53.6 |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | CAPACITY |  |  | 18+18+18 | 48 | 18 | 18 | 18 |  |  |  | 48.49 | 16.1633 | 16.1633 | 16.1633 |  |  | 59.4633 | 19.8211 | 19.8211 | 19.8211 |  |  | 48 | 16 | 16 | 16 |  |  | 48.49 | 16.1633 | 16.1633 | 16.1633 |  |  | 54.9371 | 18.3124 | 18.3124 | 18.3124 |  |  | 73.7965 | 24.5988 | 24.5988 | 24.5988 |  |  | 16500 | 16500 | 16500 |  |  | 54.9371 | 18.3124 | 18.3124 | 18.3124 |  |  | 38.2806 | 12.7602 | 12.7602 | 12.7602
| 18 | 59 |  | TC | 7.495 | 9.295 | 11.39 | 12.56 | 14.565 | 18.06 | 18.29 | 19.115 | 19.55 | 20.67 | 24.75 | 26.255 | 24.8169 | INTERPOLATION | 22.1998 | 18 | 22.1998 |  |  | 18+18+24 | 48 | 18 | 18 | 24 |  |  |  | 48.49 | 14.547 | 14.547 | 19.396 |  |  | 64.0944 | 19.8211 | 19.8211 | 24.4522 |  |  | 50 | 15 | 15 | 20 |  |  | 48.49 | 14.547 | 14.547 | 19.396 |  |  | 54.9371 | 16.4811 | 16.4811 | 21.9748 |  |  | 79.4876 | 24.5988 | 24.5988 | 30.29 |  |  | 15500 | 15500 | 21000 |  |  | 54.9371 | 16.4811 | 16.4811 | 21.9748 |  |  | 38.2806 | 11.4842 | 11.4842 | 15.3122
| 18 | 64.4 |  | TC | 7.385 | 9.155 | 11.22 | 12.37 | 14.285 | 17.79 | 18.015 | 18.83 | 19.255 | 20.355 | 24.375 | 25.86 | 24.441 | [6 empty] | 9+9+9+9 | 48 | 9 | 9 | 9 | 9 |  | 4 | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 37 | 9.25 | 9.25 | 9.25 | 9.25 |  | 48.49 | 12.1225 | 12.1225 | 12.1225 | 12.1225 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 54.9371 | 13.7343 | 13.7343 | 13.7343 | 13.7343 |  | 33.0405 | 8.2601 | 8.2601 | 8.2601 | 8.2601
| 18 | 69 |  | TC | 5.415 | 6.35 | 7.355 | 8.135 | 14.195 | 14.205 | 14.71 | 16.855 | 18.395 | 18.855 | 22.28 | 23.38 | 22.3289 | EXTRAPOLATION | 22.4083 |  |  |  |  | 9+9+9+12 | 48 | 9 | 9 | 9 | 12 |  |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 39 | 9 | 9 | 9 | 12 |  | 48.49 | 11.19 | 11.19 | 11.19 | 14.92 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9500 | 9500 | 9500 | 12500 |  | 54.9371 | 12.6778 | 12.6778 | 12.6778 | 16.9037 |  | 35.1056 | 8.2601 | 8.2601 | 8.2601 | 10.3252
| 18 | 71.6 |  | TC | 5.535 | 6.255 | 7.24 | 8.015 | 13.605 | 13.99 | 14.49 | 16.6 | 18.12 | 18.575 | 21.945 | 23.03 | 21.9932 | [6 empty] | 9+9+9+18 | 48 | 9 | 9 | 9 | 18 |  |  | 48.49 | 9.698 | 9.698 | 9.698 | 19.396 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 44 | 9 | 9 | 9 | 17 |  | 48.49 | 9.698 | 9.698 | 9.698 | 19.396 |  | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 21.9748 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 9500 | 9500 | 9500 | 17500 |  | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 21.9748 |  | 38.2806 | 7.6561 | 7.6561 | 7.6561 | 15.3122
| 24 | 59 |  | TC | 14.04 | 17.84 | 20.125 | 22.59 | 24.15 | 25.5 | 25.88 | 28.135 | 30.24 | 32.02 | 36.69 | 40.625 | 36.8649 | INTERPOLATION | 35.9864 | 24 | 35.9864 |  |  | 9+9+9+24 | 48 | 9 | 9 | 9 | 24 |  |  | 48.49 | 8.5571 | 8.5571 | 8.5571 | 22.8188 |  | 55.8416 | 10.4631 | 10.4631 | 10.4631 | 24.4522 |  | 46 | 8.5 | 8.5 | 8.5 | 20.5 |  | 48.49 | 8.5571 | 8.5571 | 8.5571 | 22.8188 |  | 54.9371 | 9.6948 | 9.6948 | 9.6948 | 25.8528 |  | 66.1581 | 11.956 | 11.956 | 11.956 | 30.29 |  | 9000 | 9000 | 9000 | 21000 |  | 54.9371 | 9.6948 | 9.6948 | 9.6948 | 25.8528 |  | 38.2806 | 6.7554 | 6.7554 | 6.7554 | 18.0144
| 24 | 64.4 |  | TC | 13.865 | 17.62 | 19.875 | 22.31 | 23.95 | 25.185 | 25.56 | 27.785 | 29.935 | 31.69 | 36.145 | 40.02 | 36.3172 | [6 empty] | 9+9+12+12 | 48 | 9 | 9 | 12 | 12 |  |  | 46.9392 | 10.3907 | 10.3907 | 13.0789 | 13.0789 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 42 | 9 | 9 | 12 | 12 |  | 48.49 | 10.3907 | 10.3907 | 13.8543 | 13.8543 |  | 53.4345 | 11.7722 | 11.7722 | 14.945 | 14.945 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 9500 | 9500 | 13000 | 13000 |  | 54.9371 | 11.7722 | 11.7722 | 15.6963 | 15.6963 |  | 37.0563 | 8.203 | 8.203 | 10.3252 | 10.3252
| 24 | 69 |  | TC | 13.765 | 17.48 | 19.72 | 22.14 | 23.77 | 24.99 | 25.36 | 27.57 | 29.705 | 31.015 | 35.995 | 40.46 | 36.1934 | EXTRAPOLATION | 35.9133 |  |  |  |  | 9+9+12+18 | 48 | 9 | 9 | 12 | 18 |  |  | 48.49 | 9.0919 | 9.0919 | 12.1225 | 18.1837 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 46 | 9 | 9 | 11 | 17 |  | 48.49 | 9.0919 | 9.0919 | 12.1225 | 18.1837 |  | 54.9371 | 10.3007 | 10.3007 | 13.7343 | 20.6014 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 9500 | 9500 | 11500 | 17500 |  | 54.9371 | 10.3007 | 10.3007 | 13.7343 | 20.6014 |  | 38.2806 | 7.1776 | 7.1776 | 9.5701 | 14.3552
| 24 | 71.6 |  | TC | 13.695 | 17.395 | 19.625 | 22.025 | 23.405 | 24.865 | 25.235 | 27.43 | 29.555 | 30.59 | 35.46 | 39.85 | 35.6551 | [6 empty] | 9+9+12+24 | 48 | 9 | 9 | 12 | 24 |  |  | 48.49 | 8.0817 | 8.0817 | 10.7756 | 21.5511 |  | 58.4573 | 10.4631 | 10.4631 | 13.0789 | 24.4522 |  | 48 | 8.5 | 8.5 | 10.5 | 20.5 |  | 48.49 | 8.0817 | 8.0817 | 10.7756 | 21.5511 |  | 54.9371 | 9.1562 | 9.1562 | 12.2082 | 24.4165 |  | 69.1471 | 11.956 | 11.956 | 14.945 | 30.29 |  | 9000 | 9000 | 11000 | 21000 |  | 54.9371 | 9.1562 | 9.1562 | 12.2082 | 24.4165 |  | 38.2806 | 6.3801 | 6.3801 | 8.5068 | 17.0136
| 30 | 59 |  | TC | 18.545 | 22.4 | 24.37 | 26.675 | 28.605 | 31.575 | 31.86 | 33.255 | 34.93 | 36.86 | 38.23 | 41.63 | 38.3811 | INTERPOLATION | 36.901 | 30 | 36.901 |  |  | 9+9+18+18 | 48 | 9 | 9 | 18 | 18 |  |  | 48.49 | 8.0817 | 8.0817 | 16.1633 | 16.1633 |  | 60.5684 | 10.4631 | 10.4631 | 19.8211 | 19.8211 |  | 48 | 8.5 | 8.5 | 15.5 | 15.5 |  | 48.49 | 8.0817 | 8.0817 | 16.1633 | 16.1633 |  | 54.9371 | 9.1562 | 9.1562 | 18.3124 | 18.3124 |  | 73.1097 | 11.956 | 11.956 | 24.5988 | 24.5988 |  | 9000 | 9000 | 16000 | 16000 |  | 54.9371 | 9.1562 | 9.1562 | 18.3124 | 18.3124 |  | 38.2806 | 6.3801 | 6.3801 | 12.7602 | 12.7602
| 30 | 64.4 |  | TC | 18.295 | 22.09 | 24.03 | 26.305 | 28.165 | 31.115 | 31.395 | 32.765 | 34.425 | 36.325 | 37.655 | 41.005 | 37.8039 | [6 empty] | 9+9+18+24 | 48 | 9 | 9 | 18 | 24 |  |  | 48.49 | 7.2735 | 7.2735 | 14.547 | 19.396 |  | 65.1996 | 10.4631 | 10.4631 | 19.8211 | 24.4522 |  | 50.5 | 8 | 8 | 14.5 | 20 |  | 48.49 | 7.2735 | 7.2735 | 14.547 | 19.396 |  | 54.9371 | 8.2406 | 8.2406 | 16.4811 | 21.9748 |  | 78.8009 | 11.956 | 11.956 | 24.5988 | 30.29 |  | 8500 | 8500 | 15000 | 20000 |  | 54.9371 | 8.2406 | 8.2406 | 16.4811 | 21.9748 |  | 38.2806 | 5.7421 | 5.7421 | 11.4842 | 15.3122
| 30 | 69 |  | TC | 16.595 | 20.52 | 21.915 | 23.87 | 27.1 | 27.5 | 27.955 | 31.66 | 33.75 | 35.855 | 36.98 | 40.02 | 37.1151 | EXTRAPOLATION | 36.8953 |  |  |  |  | 9+12+12+12 | 48 | 9 | 12 | 12 | 12 |  |  | 48.49 | 9.698 | 12.9307 | 12.9307 | 12.9307 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 45 | 9 | 12 | 12 | 12 |  | 48.49 | 9.698 | 12.9307 | 12.9307 | 12.9307 |  | 54.9371 | 10.9874 | 14.6499 | 14.6499 | 14.6499 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 9500 | 12500 | 12500 | 12500 |  | 54.9371 | 10.9874 | 14.6499 | 14.6499 | 14.6499 |  | 38.2806 | 7.6561 | 10.2082 | 10.2082 | 10.2082
| 30 | 71.6 |  | TC | 15.415 | 19.3 | 21.655 | 23.585 | 25.83 | 27.1 | 27.55 | 31.185 | 33.245 | 35.32 | 36.425 | 39.425 | 36.5583 | [6 empty] | 9+12+12+18 | 48 | 9 | 12 | 12 | 18 |  |  | 48.49 | 8.5571 | 11.4094 | 11.4094 | 17.1141 |  | 56.442 | 10.4631 | 13.0789 | 13.0789 | 19.8211 |  | 47 | 9 | 11 | 11 | 16 |  | 48.49 | 8.5571 | 11.4094 | 11.4094 | 17.1141 |  | 54.9371 | 9.6948 | 12.9264 | 12.9264 | 19.3896 |  | 66.4449 | 11.956 | 14.945 | 14.945 | 24.5988 |  | 9500 | 11500 | 11500 | 16500 |  | 54.9371 | 9.6948 | 12.9264 | 12.9264 | 19.3896 |  | 38.2806 | 6.7554 | 9.0072 | 9.0072 | 13.5108
| 36 | 59 |  | TC | 23.435 | 28.205 | 30.28 | 33.065 | 36.065 | 38.655 | 39.265 | 40.485 | 42.4 | 45.04 | 55.94 | 61.83 | 56.2018 | INTERPOLATION | 49.5103 | 36 | 49.5103 |  |  | 9+12+12+24 | 48 | 9 | 12 | 12 | 24 |  |  | 48.49 | 7.6563 | 10.2084 | 10.2084 | 20.4168 |  | 61.0731 | 10.4631 | 13.0789 | 13.0789 | 24.4522 |  | 48.5 | 8.5 | 10 | 10 | 20 |  | 48.49 | 7.6563 | 10.2084 | 10.2084 | 20.4168 |  | 54.9371 | 8.6743 | 11.5657 | 11.5657 | 23.1314 |  | 72.1361 | 11.956 | 14.945 | 14.945 | 30.29 |  | 9000 | 10500 | 10500 | 20500 |  | 54.9371 | 8.6743 | 11.5657 | 11.5657 | 23.1314 |  | 38.2806 | 6.0443 | 8.0591 | 8.0591 | 16.1181
| 36 | 64.4 |  | TC | 23.14 | 27.835 | 29.88 | 32.615 | 35.72 | 38.075 | 38.675 | 39.875 | 41.775 | 44.365 | 55.11 | 60.915 | 55.368 | [6 empty] | 9+12+18+18 | 48 | 9 | 12 | 18 | 18 |  |  | 48.49 | 7.6563 | 10.2084 | 15.3126 | 15.3126 |  | 63.1842 | 10.4631 | 13.0789 | 19.8211 | 19.8211 |  | 48.5 | 8.5 | 10 | 15 | 15 |  | 48.49 | 7.6563 | 10.2084 | 15.3126 | 15.3126 |  | 54.9371 | 8.6743 | 11.5657 | 17.3486 | 17.3486 |  | 76.0987 | 11.956 | 14.945 | 24.5988 | 24.5988 |  | 9000 | 10500 | 15500 | 15500 |  | 54.9371 | 8.6743 | 11.5657 | 17.3486 | 17.3486 |  | 38.2806 | 6.0443 | 8.0591 | 12.0886 | 12.0886
| 36 | 69 |  | TC | 22.66 | 27.245 | 28.57 | 31.26 | 35.61 | 36.81 | 37.14 | 39.13 | 41.71 | 45.71 | 49.725 | 53.495 | 49.8926 | EXTRAPOLATION | 50.045 |  |  |  |  | 9+18+18+18 | 48 | 9 | 18 | 18 | 18 |  |  | 48.49 | 6.9271 | 13.8543 | 13.8543 | 13.8543 |  | 69.9264 | 10.4631 | 19.8211 | 19.8211 | 19.8211 |  | 50 | 8 | 14 | 14 | 14 |  | 48.49 | 6.9271 | 13.8543 | 13.8543 | 13.8543 |  | 54.9371 | 7.8482 | 15.6963 | 15.6963 | 15.6963 |  | 85.7525 | 11.956 | 24.5988 | 24.5988 | 24.5988 |  | 8500 | 14500 | 14500 | 14500 |  | 54.9371 | 7.8482 | 15.6963 | 15.6963 | 15.6963 |  | 38.2806 | 5.4687 | 10.9373 | 10.9373 | 10.9373
| 36 | 71.6 |  | TC | 22.265 | 26.76 | 28.06 | 30.7 | 34.58 | 36.07 | 36.395 | 38.345 | 40.87 | 44.795 | 48.735 | 52.42 | 48.8988 | [6 empty] | 12+12+12+12 | 48 | 12 | 12 | 12 | 12 |  |  | 48.49 | 12.1225 | 12.1225 | 12.1225 | 12.1225 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 48 | 12 | 12 | 12 | 12 |  | 48.49 | 12.1225 | 12.1225 | 12.1225 | 12.1225 |  | 54.9371 | 13.7343 | 13.7343 | 13.7343 | 13.7343 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 12500 | 12500 | 12500 | 12500 |  | 54.9371 | 13.7343 | 13.7343 | 13.7343 | 13.7343 |  | 38.2806 | 9.5701 | 9.5701 | 9.5701 | 9.5701
| 48 | 59 |  | TC | 23.585 | 28.385 | 30.47 | 33.275 | 36.995 | 38.895 | 39.51 | 40.74 | 42.67 | 45.32 | 56.29 | 66.58 | 56.7473 | INTERPOLATION | 54.9371 | 48 | 54.9371 |  |  | 12+12+12+18 | 48 | 12 | 12 | 12 | 18 |  |  | 48.49 | 10.7756 | 10.7756 | 10.7756 | 16.1633 |  | 59.0578 | 13.0789 | 13.0789 | 13.0789 | 19.8211 |  | 49 | 11 | 11 | 11 | 16 |  | 48.49 | 10.7756 | 10.7756 | 10.7756 | 16.1633 |  | 54.9371 | 12.2082 | 12.2082 | 12.2082 | 18.3124 |  | 69.4339 | 14.945 | 14.945 | 14.945 | 24.5988 |  | 11500 | 11500 | 11500 | 16500 |  | 54.9371 | 12.2082 | 12.2082 | 12.2082 | 18.3124 |  | 38.2806 | 8.5068 | 8.5068 | 8.5068 | 12.7602
| 48 | 64.4 |  | TC | 23.325 | 28.06 | 30.12 | 32.88 | 36.555 | 38.38 | 38.985 | 40.195 | 42.11 | 44.72 | 55.55 | 65.575 | 55.9956 | [6 empty] | 12+12+12+24 | 48 | 12 | 12 | 12 | 24 |  |  | 48.49 | 9.698 | 9.698 | 9.698 | 19.396 |  | 63.6889 | 13.0789 | 13.0789 | 13.0789 | 24.4522 |  | 50 | 10 | 10 | 10 | 20 |  | 48.49 | 9.698 | 9.698 | 9.698 | 19.396 |  | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 21.9748 |  | 75.1251 | 14.945 | 14.945 | 14.945 | 30.29 |  | 10500 | 10500 | 10500 | 20500 |  | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 21.9748 |  | 38.2806 | 7.6561 | 7.6561 | 7.6561 | 15.3122
| 48 | 69 |  | TC | 22.955 | 27.6 | 28.945 | 31.665 | 36.235 | 37.29 | 37.625 | 39.64 | 42.25 | 46.305 | 54.93 | 64.68 | 55.3633 | EXTRAPOLATION | 54.8547 |  |  |  |  | 12+12+18+18 | 48 | 12 | 12 | 18 | 18 |  |  | 48.49 | 9.698 | 9.698 | 14.547 | 14.547 |  | 65.8 | 13.0789 | 13.0789 | 19.8211 | 19.8211 |  | 50 | 10 | 10 | 15 | 15 |  | 48.49 | 9.698 | 9.698 | 14.547 | 14.547 |  | 54.9371 | 10.9874 | 10.9874 | 16.4811 | 16.4811 |  | 79.0877 | 14.945 | 14.945 | 24.5988 | 24.5988 |  | 10500 | 10500 | 15500 | 15500 |  | 54.9371 | 10.9874 | 10.9874 | 16.4811 | 16.4811 |  | 38.2806 | 7.6561 | 7.6561 | 11.4842 | 11.4842
| 48 | 71.6 |  | TC | 22.51 | 27.055 | 28.37 | 31.035 | 35.055 | 36.465 | 36.795 | 38.765 | 41.32 | 45.29 | 53.83 | 63.395 | 54.2551 | [6 empty] | 9+9+9+9+9 | 48 | 9 | 9 | 9 | 9 | 9 | 5 | 48.49 | 9.698 | 9.698 | 9.698 | 9.698 | 9.698 | 52.3156 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 45 | 9 | 9 | 9 | 9 | 9 | 48.49 | 9.698 | 9.698 | 9.698 | 9.698 | 9.698 | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 59.7801 | 11.956 | 11.956 | 11.956 | 11.956 | 11.956 | 9500 | 9500 | 9500 | 9500 | 9500 | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 38.2806 | 7.6561 | 7.6561 | 7.6561 | 7.6561 | 7.6561
| 18 | 59 |  | Input | 1.66 | 1.7 | 1.785 | 1.815 | 1.925 | 1.9 | 1.915 | 1.97 | 1.625 | 1.71 | 1.905 | 1.865 | [7 empty] | 9+9+9+9+12 | 48 | 9 | 9 | 9 | 9 | 12 |  | 48.49 | 9.0919 | 9.0919 | 9.0919 | 9.0919 | 12.1225 | 54.9313 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 48 | 9 | 9 | 9 | 9 | 12 | 48.49 | 9.0919 | 9.0919 | 9.0919 | 9.0919 | 12.1225 | 54.9371 | 10.3007 | 10.3007 | 10.3007 | 10.3007 | 13.7343 | 62.7691 | 11.956 | 11.956 | 11.956 | 11.956 | 14.945 | 9500 | 9500 | 9500 | 9500 | 13000 | 54.9371 | 10.3007 | 10.3007 | 10.3007 | 10.3007 | 13.7343 | 38.2806 | 7.1776 | 7.1776 | 7.1776 | 7.1776 | 9.5701
| 18 | 64.4 |  | Input | 1.69 | 1.73 | 1.815 | 1.845 | 1.96 | 1.93 | 1.945 | 2 | 1.655 | 1.74 | 1.935 | 1.895 | [7 empty] | 9+9+9+9+18 | 48 | 9 | 9 | 9 | 9 | 18 |  | 48.49 | 8.0817 | 8.0817 | 8.0817 | 8.0817 | 16.1633 | 61.6736 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 19.8211 | 50 | 8.5 | 8.5 | 8.5 | 8.5 | 16 | 48.49 | 8.0817 | 8.0817 | 8.0817 | 8.0817 | 16.1633 | 54.9371 | 9.1562 | 9.1562 | 9.1562 | 9.1562 | 18.3124 | 72.4229 | 11.956 | 11.956 | 11.956 | 11.956 | 24.5988 | 9000 | 9000 | 9000 | 9000 | 16500 | 54.9371 | 9.1562 | 9.1562 | 9.1562 | 9.1562 | 18.3124 | 38.2806 | 6.3801 | 6.3801 | 6.3801 | 6.3801 | 12.7602
| 18 | 69 |  | Input | 1.435 | 1.465 | 1.5 | 1.51 | 1.96 | 1.655 | 1.695 | 1.82 | 1.83 | 1.91 | 1.975 | 1.78 | [7 empty] | 9+9+9+9+24 | 48 | 9 | 9 | 9 | 9 | 24 |  | 48.49 | 7.2735 | 7.2735 | 7.2735 | 7.2735 | 19.396 | 66.3047 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 24.4522 | 52 | 8 | 8 | 8 | 8 | 20 | 48.49 | 7.2735 | 7.2735 | 7.2735 | 7.2735 | 19.396 | 54.9371 | 8.2406 | 8.2406 | 8.2406 | 8.2406 | 21.9748 | 78.1141 | 11.956 | 11.956 | 11.956 | 11.956 | 30.29 | 8500 | 8500 | 8500 | 8500 | 20500 | 54.9371 | 8.2406 | 8.2406 | 8.2406 | 8.2406 | 21.9748 | 38.2806 | 5.7421 | 5.7421 | 5.7421 | 5.7421 | 15.3122
| 18 | 71.6 |  | Input | 1.465 | 1.495 | 1.53 | 1.54 | 2.03 | 1.685 | 1.725 | 1.85 | 1.86 | 1.94 | 2.005 | 1.81 | [7 empty] | 9+9+9+12+12 | 48 | 9 | 9 | 9 | 12 | 12 |  | 48.49 | 8.5571 | 8.5571 | 8.5571 | 11.4094 | 11.4094 | 57.5471 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 49 | 9 | 9 | 9 | 11 | 11 | 48.49 | 8.5571 | 8.5571 | 8.5571 | 11.4094 | 11.4094 | 54.9371 | 9.6948 | 9.6948 | 9.6948 | 12.9264 | 12.9264 | 65.7581 | 11.956 | 11.956 | 11.956 | 14.945 | 14.945 | 9000 | 9000 | 9000 | 12000 | 12000 | 54.9371 | 9.6948 | 9.6948 | 9.6948 | 12.9264 | 12.9264 | 38.2806 | 6.7554 | 6.7554 | 6.7554 | 9.0072 | 9.0072
| 24 | 59 |  | Input | 2.95 | 3.215 | 3.255 | 3.475 | 3.625 | 2.68 | 2.81 | 2.89 | 2.67 | 2.8 | 2.98 | 2.73 | [7 empty] | 9+9+9+12+18 | 48 | 9 | 9 | 9 | 12 | 18 |  | 48.49 | 7.6563 | 7.6563 | 7.6563 | 10.2084 | 15.3126 | 64.2893 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 19.8211 | 51 | 8 | 8 | 8 | 11 | 16 | 48.49 | 7.6563 | 7.6563 | 7.6563 | 10.2084 | 15.3126 | 54.9371 | 8.6743 | 8.6743 | 8.6743 | 11.5657 | 17.3486 | 75.4119 | 11.956 | 11.956 | 11.956 | 14.945 | 24.5988 | 8500 | 8500 | 8500 | 11500 | 17000 | 54.9371 | 8.6743 | 8.6743 | 8.6743 | 11.5657 | 17.3486 | 38.2806 | 6.0443 | 6.0443 | 6.0443 | 8.0591 | 12.0886
| 24 | 64.4 |  | Input | 3.025 | 3.295 | 3.335 | 3.56 | 3.725 | 2.75 | 2.88 | 2.96 | 2.74 | 2.91 | 3.01 | 2.76 | [7 empty] | 9+9+9+18+18 | 48 | 9 | 9 | 9 | 18 | 18 |  | 48.49 | 6.9271 | 6.9271 | 6.9271 | 13.8543 | 13.8543 | 71.0316 | 10.4631 | 10.4631 | 10.4631 | 19.8211 | 19.8211 | 52.5 | 7.5 | 7.5 | 7.5 | 15 | 15 | 48.49 | 6.9271 | 6.9271 | 6.9271 | 13.8543 | 13.8543 | 54.9371 | 7.8482 | 7.8482 | 7.8482 | 15.6963 | 15.6963 | 85.0657 | 11.956 | 11.956 | 11.956 | 24.5988 | 24.5988 | 8000 | 8000 | 8000 | 15500 | 15500 | 54.9371 | 7.8482 | 7.8482 | 7.8482 | 15.6963 | 15.6963 | 38.2806 | 5.4687 | 5.4687 | 5.4687 | 10.9373 | 10.9373
| 24 | 69 |  | Input | 3.09 | 3.365 | 3.405 | 3.64 | 3.845 | 2.81 | 2.945 | 3.03 | 2.795 | 2.98 | 3.065 | 3.195 | [7 empty] | 9+9+12+12+12 | 48 | 9 | 9 | 12 | 12 | 12 |  | 48.49 | 8.0817 | 8.0817 | 10.7756 | 10.7756 | 10.7756 | 60.1629 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 50 | 8.5 | 8.5 | 11 | 11 | 11 | 48.49 | 8.0817 | 8.0817 | 10.7756 | 10.7756 | 10.7756 | 54.9371 | 9.1562 | 9.1562 | 12.2082 | 12.2082 | 12.2082 | 68.7471 | 11.956 | 11.956 | 14.945 | 14.945 | 14.945 | 9000 | 9000 | 12000 | 12000 | 12000 | 54.9371 | 9.1562 | 9.1562 | 12.2082 | 12.2082 | 12.2082 | 38.2806 | 6.3801 | 6.3801 | 8.5068 | 8.5068 | 8.5068
| 24 | 71.6 |  | Input | 3.165 | 3.445 | 3.485 | 3.725 | 3.855 | 2.87 | 3.01 | 3.1 | 2.86 | 3.035 | 3.095 | 3.225 | [7 empty] | 9+9+12+12+18 | 48 | 9 | 9 | 12 | 12 | 18 |  | 48.49 | 7.2735 | 7.2735 | 9.698 | 9.698 | 14.547 | 66.9051 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 19.8211 | 52 | 8.5 | 8.5 | 10 | 10 | 15 | 48.49 | 7.2735 | 7.2735 | 9.698 | 9.698 | 14.547 | 54.9371 | 8.2406 | 8.2406 | 10.9874 | 10.9874 | 16.4811 | 78.4009 | 11.956 | 11.956 | 14.945 | 14.945 | 24.5988 | 8500 | 8500 | 11000 | 11000 | 16000 | 54.9371 | 8.2406 | 8.2406 | 10.9874 | 10.9874 | 16.4811 | 38.2806 | 5.7421 | 5.7421 | 7.6561 | 7.6561 | 11.4842
| 30 | 59 |  | Input | 3.415 | 3.485 | 3.475 | 3.645 | 3.71 | 3.74 | 3.76 | 3.82 | 3.105 | 3.145 | 3.295 | 3.395 | [7 empty] | 9+12+12+12+12 | 48 | 9 | 12 | 12 | 12 | 12 |  | 48.49 | 7.6563 | 10.2084 | 10.2084 | 10.2084 | 10.2084 | 62.7787 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 50 | 8 | 10.5 | 10.5 | 10.5 | 10.5 | 48.49 | 7.6563 | 10.2084 | 10.2084 | 10.2084 | 10.2084 | 54.9371 | 8.6743 | 11.5657 | 11.5657 | 11.5657 | 11.5657 | 71.7361 | 11.956 | 14.945 | 14.945 | 14.945 | 14.945 | 8500 | 11000 | 11000 | 11000 | 11000 | 54.9371 | 8.6743 | 11.5657 | 11.5657 | 11.5657 | 11.5657 | 38.2806 | 6.0443 | 8.0591 | 8.0591 | 8.0591 | 8.0591
| 30 | 64.4 |  | Input | 3.445 | 3.515 | 3.555 | 3.78 | 3.84 | 3.87 | 3.89 | 3.95 | 3.135 | 3.175 | 3.325 | 3.425 | [7 empty] | 9+12+12+12+18 | 48 | 9 | 12 | 12 | 12 | 18 |  | 48.49 | 6.9271 | 9.2362 | 9.2362 | 9.2362 | 13.8543 | 69.5209 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 19.8211 | 52.5 | 7.5 | 10 | 10 | 10 | 15 | 48.49 | 6.9271 | 9.2362 | 9.2362 | 9.2362 | 13.8543 | 54.9371 | 7.8482 | 10.4642 | 10.4642 | 10.4642 | 15.6963 | 81.3899 | 11.956 | 14.945 | 14.945 | 14.945 | 24.5988 | 8000 | 10500 | 10500 | 10500 | 15500 | 54.9371 | 7.8482 | 10.4642 | 10.4642 | 10.4642 | 15.6963 | 38.2806 | 5.4687 | 7.2915 | 7.2915 | 7.2915 | 10.9373
| 30 | 69 |  | Input | 3.535 | 3.605 | 3.665 | 3.79 | 3.945 | 3.88 | 3.93 | 4.07 | 3.165 | 3.205 | 3.235 | 3.325 | [7 empty] | 12+12+12+12+12 | 48 | 12 | 12 | 12 | 12 | 12 |  | 48.49 | 9.698 | 9.698 | 9.698 | 9.698 | 9.698 | 65.3944 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 52.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 48.49 | 9.698 | 9.698 | 9.698 | 9.698 | 9.698 | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 74.7251 | 14.945 | 14.945 | 14.945 | 14.945 | 14.945 | 11000 | 11000 | 11000 | 11000 | 11000 | 54.9371 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 10.9874 | 38.2806 | 7.6561 | 7.6561 | 7.6561 | 7.6561 | 7.6561
| 30 | 71.6 |  | Input | 3.665 | 3.635 | 3.8 | 3.82 | 3.84 | 3.91 | 3.96 | 4.1 | 3.195 | 3.235 | 3.265 | 3.355
| 36 | 59 |  | Input | 4.945 | 5.06 | 5.21 | 5.24 | 5.275 | 5.15 | 5.17 | 5.25 | 4.595 | 4.765 | 4.935 | 4.595
| 36 | 64.4 |  | Input | 5.005 | 5.12 | 5.27 | 5.3 | 5.35 | 5.21 | 5.23 | 5.31 | 4.655 | 4.825 | 4.995 | 4.655
| 36 | 69 |  | Input | 5.08 | 5.19 | 5.28 | 5.31 | 5.38 | 5.29 | 5.31 | 5.39 | 4.655 | 4.995 | 4.695 | 4.33
| 36 | 71.6 |  | Input | 5.13 | 5.24 | 5.33 | 5.36 | 5.38 | 5.34 | 5.36 | 5.44 | 4.705 | 5.05 | 4.745 | 4.385
| 48 | 59 |  | Input | 4.995 | 5.11 | 5.26 | 5.29 | 5.345 | 5.2 | 5.22 | 5.3 | 4.64 | 4.815 | 4.985 | 4.64
| 48 | 64.4 |  | Input | 5.11 | 5.22 | 5.37 | 5.41 | 5.495 | 5.31 | 5.33 | 5.42 | 4.745 | 4.925 | 5.1 | 4.745
| 48 | 69 |  | Input | 5.14 | 5.25 | 5.34 | 5.37 | 5.445 | 5.35 | 5.37 | 5.455 | 4.715 | 4.665 | 4.745 | 5.08
| 48 | 71.6 |  | Input | 5.19 | 5.3 | 5.39 | 5.42 | 5.46 | 5.4 | 5.42 | 5.505 | 4.765 | 5.11 | 4.795 | 5.13
| 18 | 59 |  | COP | 1.325 | 1.605 | 1.87 | 2.025 | 2.185 | 2.785 | 2.795 | 2.84 | 3.53 | 3.555 | 3.825 | 4.12
| 18 | 64.4 |  | COP | 1.275 | 1.55 | 1.81 | 1.965 | 2.135 | 2.7 | 2.715 | 2.755 | 3.41 | 3.435 | 3.715 | 4
| 18 | 69 |  | COP | 1.11 | 1.27 | 1.44 | 1.58 | 2.125 | 2.52 | 2.545 | 2.715 | 2.945 | 2.89 | 3.305 | 3.83
| 18 | 71.6 |  | COP | 1.11 | 1.225 | 1.39 | 1.53 | 1.965 | 2.435 | 2.465 | 2.635 | 2.86 | 2.81 | 3.21 | 3.715
| 24 | 59 |  | COP | 1.395 | 1.625 | 1.815 | 1.905 | 1.955 | 2.79 | 2.7 | 2.85 | 3.32 | 3.355 | 3.605 | 4.365
| 24 | 64.4 |  | COP | 1.345 | 1.57 | 1.745 | 1.835 | 1.885 | 2.69 | 2.605 | 2.75 | 3.205 | 3.19 | 3.515 | 4.25
| 24 | 69 |  | COP | 1.305 | 1.52 | 1.695 | 1.785 | 1.81 | 2.61 | 2.525 | 2.67 | 3.115 | 3.05 | 3.445 | 3.71
| 24 | 71.6 |  | COP | 1.27 | 1.48 | 1.65 | 1.735 | 1.78 | 2.535 | 2.455 | 2.595 | 3.03 | 2.96 | 3.36 | 3.62
| 30 | 59 |  | COP | 1.59 | 1.885 | 2.055 | 2.14 | 2.26 | 2.475 | 2.485 | 2.555 | 3.295 | 3.435 | 3.4 | 3.59
| 30 | 64.4 |  | COP | 1.56 | 1.845 | 1.98 | 2.04 | 2.15 | 2.36 | 2.365 | 2.435 | 3.22 | 3.355 | 3.32 | 3.51
| 30 | 69 |  | COP | 1.375 | 1.665 | 1.755 | 1.845 | 2.01 | 2.08 | 2.085 | 2.28 | 3.125 | 3.285 | 3.355 | 3.53
| 30 | 71.6 |  | COP | 1.235 | 1.555 | 1.67 | 1.815 | 1.975 | 2.03 | 2.04 | 2.23 | 3.05 | 3.2 | 3.275 | 3.445
| 36 | 59 |  | COP | 1.39 | 1.635 | 1.7 | 1.85 | 2.005 | 2.2 | 2.225 | 2.26 | 2.705 | 2.77 | 3.32 | 3.945
| 36 | 64.4 |  | COP | 1.355 | 1.595 | 1.66 | 1.805 | 1.965 | 2.14 | 2.17 | 2.2 | 2.635 | 2.695 | 3.235 | 3.835
| 36 | 69 |  | COP | 1.31 | 1.54 | 1.585 | 1.725 | 1.94 | 2.04 | 2.05 | 2.13 | 2.625 | 2.68 | 3.105 | 3.62
| 36 | 71.6 |  | COP | 1.27 | 1.495 | 1.545 | 1.68 | 1.885 | 1.98 | 1.99 | 2.065 | 2.55 | 2.6 | 3.01 | 3.505
| 48 | 59 |  | COP | 1.385 | 1.63 | 1.7 | 1.845 | 2.0284 | 2.19 | 2.22 | 2.255 | 2.695 | 2.76 | 3.31 | 4.21
| 48 | 64.4 |  | COP | 1.34 | 1.575 | 1.64 | 1.785 | 1.96 | 2.12 | 2.14 | 2.175 | 2.6 | 2.665 | 3.195 | 4.05
| 48 | 69 |  | COP | 1.31 | 1.54 | 1.59 | 1.73 | 1.945 | 2.04 | 2.05 | 2.13 | 2.63 | 2.91 | 3.39 | 3.735
| 48 | 71.6 |  | COP | 1.27 | 1.495 | 1.545 | 1.68 | 1.8815 | 1.98 | 1.99 | 2.06 | 2.54 | 2.6 | 3.29 | 3.625
LEGEND
DB - Dry Bulb
WB - Wet Bulb
TC - Total Net Capacity (1000 Btu/hour)
Input - Total Power (kW)
COP - W/W

## Ducted (hidden)
Ducted Indoor Units | [24 empty] | NOMINAL COMBINATIONS | [6 empty] | COOLING ESTIMATED CAPACITY CAPPED | [5 empty] | COOLING CAPPED CAPACITY BASED ON INDOOR UNIT | [5 empty] | COOLING ORIGINAL ESTIMATED CAPACITY | [5 empty] | COOLING CALCULATION UNCAPPED | [5 empty] | HEATING ESTIMATED CAPACITY CAPPED | [5 empty] | HEATING CAPPED CAPACITY BASED ON INDOOR UNIT | [5 empty] | HEATING ORIGINAL ESTIMATED CAPACITY |  |  |  |  | HEATING CALCULATION UNCAPPED | [5 empty] | SENSIBLE ESTIMATED CAPACITY BASED ON RATIO
[22 empty] | Variables of indoor |  | Size |  | Size |  |  |  |  | No. of Zones | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) | 0 | 0 | 0 | 0 | Heating Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h) |  |  |  |  | Total Capacity | Cooling Capacity (Btu/h)
[22 empty] | Indoor Unit Sizes | Defined by size/variable 9 | 18K | 18 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[22 empty] | 9 | 1 | 9+9 | 18 | 9 | 9 |  |  |  | 2 | 20.2322 | 10.1161 | 10.1161 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 18 | 9 | 9 |  |  |  | 20.2322 | 10.1161 | 10.1161 |  |  |  | 20.4583 | 10.2291 | 10.2291 |  |  |  | 23.912 | Zone 1: 11.956; Zone 2: 11.956; Zone 1: 9500; Zone 2: 9500 | 20.4583 | 10.2291 | 10.2291 |  |  |  | 14.6946 | 7.3473 | 7.3473
[22 empty] | 12 | 1.3333 | 9+12 | 18 | 9 | 12 |  |  |  |  | 20.2322 | 8.671 | 11.5613 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 19 | 8.5 | 10.5 |  |  |  | 20.2322 | 8.671 | 11.5613 |  |  |  | 20.4583 | 8.7678 | 11.6904 |  |  |  | 26.901 | Zone 1: 11.956; Zone 2: 14.945; Zone 1: 9000; Zone 2: 11000 | 20.4583 | 8.7678 | 11.6904 |  |  |  | 14.6946 | 6.2977 | 8.3969
[22 empty] | 18 | 2 | 12+12 | 18 | 12 | 12 |  |  |  |  | 20.2322 | 10.1161 | 10.1161 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 19 | 9.5 | 9.5 |  |  |  | 20.2322 | 10.1161 | 10.1161 |  |  |  | 20.4583 | 10.2291 | 10.2291 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 10000; Zone 2: 10000 | 20.4583 | 10.2291 | 10.2291 |  |  |  | 14.6946 | 7.3473 | 7.3473
[22 empty] | 24 | 2.6667 | 24K | 24 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[24 empty] | 9+9 | 24 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 19 | 9.5 | 9.5 |  |  |  | 28.9122 | 14.4561 | 14.4561 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 11.956; 10000 Zone 1: 10000; 10000 Zone 2: 10000 | 35.7621 | 17.8811 | 17.8811 |  |  |  | 15.5799 | 7.7899 | 7.7899
[24 empty] | 9+12 | 24 | 9 | 12 |  |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 21.5 | 9.5 | 12 |  |  |  | 28.9122 | 12.391 | 16.5213 |  |  |  | 26.901 | 11.956 | 14.945 |  |  |  | 26.901 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 14.945; 10000 Zone 1: 10000; 10000 Zone 2: 13000 | 35.7621 | 15.3266 | 20.4355 |  |  |  | 17.5274 | 7.7899 | 9.7374
[24 empty] | 9+18 | 24 | 9 | 18 |  |  |  |  | 28.9122 | 9.6374 | 19.2748 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 25 | 8.4 | 16.6 |  |  |  | 28.9122 | 9.6374 | 19.2748 |  |  |  | 35.7621 | 11.9207 | 23.8414 |  |  |  | 36.5548 | 14.945 Zone 1: 11.956; 14.945 Zone 2: 24.5988; 10000 Zone 1: 9000; 10000 Zone 2: 18000 | 35.7621 | 11.9207 | 23.8414 |  |  |  | 21.5256 | 7.1752 | 14.3504
[24 empty] | 12+12 | 24 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 24 | 12 | 12 |  |  |  | 28.9122 | 14.4561 | 14.4561 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | 14.945 Zone 1: 14.945; 14.945 Zone 2: 14.945; 10000 Zone 1: 13000; 10000 Zone 2: 13000 | 35.7621 | 17.8811 | 17.8811 |  |  |  | 19.4748 | 9.7374 | 9.7374
[24 empty] | 12+18 | 24 | 12 | 18 |  |  |  |  | 28.9122 | 11.5649 | 17.3473 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 26 | 10 | 16 |  |  |  | 28.9122 | 11.5649 | 17.3473 |  |  |  | 35.7621 | 14.3048 | 21.4573 |  |  |  | 39.5438 | 14.945 Zone 1: 14.945; 14.945 Zone 2: 24.5988; 10000 Zone 1: 11200; 10000 Zone 2: 16800 | 35.7621 | 14.3048 | 21.4573 |  |  |  | 21.5256 | 8.6102 | 12.9153
[24 empty] | 18+18 | 24 | 18 | 18 |  |  |  |  | 28.9122 | 14.4561 | 14.4561 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 28 | 14 | 14 |  |  |  | 28.9122 | 14.4561 | 14.4561 |  |  |  | 35.7621 | 17.8811 | 17.8811 |  |  |  | 49.1976 | 14.945 Zone 1: 24.5988; 14.945 Zone 2: 24.5988; 10000 Zone 1: 15000; 10000 Zone 2: 15000 | 35.7621 | 17.8811 | 17.8811 |  |  |  | 21.5256 | 10.7628 | 10.7628
[24 empty] | 9+9+9 | 24 | 9 | 9 | 9 |  |  | 3 | 28.9122 | 9.6374 | 9.6374 | 9.6374 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 27 | 9 | 9 | 9 |  |  | 28.9122 | 9.6374 | 9.6374 | 9.6374 |  |  | 35.7621 | 11.9207 | 11.9207 | 11.9207 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 9500 | 9500 | 9500 |  |  | 35.7621 | 11.9207 | 11.9207 | 11.9207 |  |  | 21.5256 | 7.1752 | 7.1752 | 7.1752
[24 empty] | 9+9+12 | 24 | 9 | 9 | 12 |  |  |  | 28.9122 | 8.6737 | 8.6737 | 11.5649 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 29.001 | 8.667 | 8.667 | 11.667 |  |  | 28.9122 | 8.6737 | 8.6737 | 11.5649 |  |  | 35.7621 | 10.7286 | 10.7286 | 14.3048 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 9500 | 9500 | 12000 |  |  | 35.7621 | 10.7286 | 10.7286 | 14.3048 |  |  | 21.5256 | 6.4577 | 6.4577 | 8.6102
[24 empty] | 9+9+18 | 24 | 9 | 9 | 18 |  |  |  | 28.9122 | 7.2281 | 7.2281 | 14.4561 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 29.999 | 8.333 | 8.333 | 13.333 |  |  | 28.9122 | 7.2281 | 7.2281 | 14.4561 |  |  | 35.7621 | 8.9405 | 8.9405 | 17.8811 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 9000 | 9000 | 14000 |  |  | 35.7621 | 8.9405 | 8.9405 | 17.8811 |  |  | 21.5256 | 5.3814 | 5.3814 | 10.7628
[24 empty] | 9+12+12 | 24 | 9 | 12 | 12 |  |  |  | 28.9122 | 7.8852 | 10.5135 | 10.5135 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 28.5 | 8.5 | 10 | 10 |  |  | 28.9122 | 7.8852 | 10.5135 | 10.5135 |  |  | 35.7621 | 9.7533 | 13.0044 | 13.0044 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 8500 | 11500 | 11500 |  |  | 35.7621 | 9.7533 | 13.0044 | 13.0044 |  |  | 21.5256 | 5.8706 | 7.8275 | 7.8275
[24 empty] | 12+12+12 | 24 | 12 | 12 | 12 |  |  |  | 28.9122 | 9.6374 | 9.6374 | 9.6374 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 29.001 | 9.667 | 9.667 | 9.667 |  |  | 28.9122 | 9.6374 | 9.6374 | 9.6374 |  |  | 35.7621 | 11.9207 | 11.9207 | 11.9207 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 10667 | 10667 | 10667 |  |  | 35.7621 | 11.9207 | 11.9207 | 11.9207 |  |  | 21.5256 | 7.1752 | 7.1752 | 7.1752
[24 empty] | 30K | 30 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
[24 empty] | 9+9 | 30 | 9 | 9 |  |  |  | 2 | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20.9262 | 10.4631 | 10.4631 |  |  |  | 20 | 10 | 10 |  |  |  | 36.9733 | 18.4867 | 18.4867 |  |  |  | 23.912 | 11.956 | 11.956 |  |  |  | 23.912 | Zone 1: 11.956; Zone 2: 11.956; Zone 1: 10500; Zone 2: 10500 | 36.672 | 18.336 | 18.336 |  |  |  | 15.6711 | 7.8356 | 7.8356
[24 empty] | 9+12 | 30 | 9 | 12 |  |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 23.542 | 10.4631 | 13.0789 |  |  |  | 21.5 | 9.5 | 12 |  |  |  | 36.9733 | 15.8457 | 21.1276 |  |  |  | 26.901 | 11.956 | 14.945 |  |  |  | 26.901 | Zone 1: 11.956; Zone 2: 14.945; Zone 1: 10000; Zone 2: 13000 | 36.672 | 15.7166 | 20.9554 |  |  |  | 17.63 | 7.8356 | 9.7945
[24 empty] | 9+18 | 30 | 9 | 18 |  |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 36.9733 | 12.3244 | 24.6489 |  |  |  | 36.404 | 11.956 | 24.448 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 36.672 | 12.224 | 24.448 |  |  |  | 22.6791 | 7.8356 | 14.8435
| COOLING PERFORMANCE DATA | [22 empty] | 9+24 | 30 | 9 | 24 |  |  |  |  | 34.5359 | 10.0836 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33 | 9 | 24 |  |  |  | 36.9733 | 10.0836 | 26.8897 |  |  |  | 36.672 | 10.0015 | 26.6705 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 36.672 | 10.0015 | 26.6705 |  |  |  | 25.8631 | 7.5514 | 18.3117
| Model | Cooling |  |  | Outdoor conditions (DB) | [18 empty] | 12+12 | 30 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 24 | 12 | 12 |  |  |  | 36.9733 | 18.4867 | 18.4867 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 36.672 | 18.336 | 18.336 |  |  |  | 19.5889 | 9.7945 | 9.7945
|  | Indoor Conditions DB | [21 empty] | 12+18 | 30 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 36.9733 | 14.7893 | 22.184 |  |  |  | 36.672 | 14.6688 | 22.0032 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 18000 | 36.672 | 14.6688 | 22.0032 |  |  |  | 24.638 | 9.7945 | 14.8435
|  | DB | WB |  | -13 | -4 | 0 | 5 | 17 | 47 | 77 | 86 | 95 | 104 | 113 | 122.0001 |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | CAPACITY |  |  | 12+24 | 30 | 12 | 24 |  |  |  |  | 36.7767 | 12.3244 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 34 | 11 | 23 |  |  |  | 36.9733 | 12.3244 | 24.6489 |  |  |  | 36.672 | 12.224 | 24.448 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 12000; Zone 2: 24000 | 36.672 | 12.224 | 24.448 |  |  |  | 27.5411 | 9.2295 | 18.3117
| 18 | 69.8 | 59 | TC | 18.3 | 18.65 | 18.43 | 18.75 | 18.88 | 19.12 | 20.26 | 18.47 | 16.53 | 11.28 | 10.64 | 9.86 | 16.53 | INTERPOLATION | 20.2322 | 18 | 20.2322 |  |  | 18+18 | 30 | 18 | 18 |  |  |  |  | 36.9733 | 18.4867 | 18.4867 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 33 | 16.5 | 16.5 |  |  |  | 36.9733 | 18.4867 | 18.4867 |  |  |  | 36.672 | 18.336 | 18.336 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 17000; Zone 2: 17000 | 36.672 | 18.336 | 18.336 |  |  |  | 27.6884 | 13.8442 | 13.8442
| 18 | 75.2 | 62.6 | TC | 19.76 | 20.14 | 19.9 | 20.25 | 20.39 | 20.65 | 21.88 | 19.95 | 17.85 | 12.18 | 11.49 | 10.13 | 17.85 | [6 empty] | 9+9+9 | 30 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 27.999 | 9.333 | 9.333 | 9.333 |  |  | 36.9733 | 12.3244 | 12.3244 | 12.3244 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 9667 | 9667 | 9667 |  |  | 36.672 | 12.224 | 12.224 | 12.224 |  |  | 23.5067 | 7.8356 | 7.8356 | 7.8356
| 18 | 80.6 | 66.2 | TC | 21.14 | 21.54 | 21.61 | 21.69 | 21.86 | 22.06 | 23.06 | 21.85 | 20.53 | 13.72 | 11.56 | 10.61 | 20.53 | EXTRAPOLATION | 19.6908 |  |  |  |  | 9+9+12 | 30 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 30 | 9 | 9 | 12 |  |  | 36.9733 | 11.092 | 11.092 | 14.7893 |  |  | 36.672 | 11.0016 | 11.0016 | 14.6688 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 9500 | 9500 | 12500 |  |  | 36.672 | 11.0016 | 11.0016 | 14.6688 |  |  | 25.4656 | 7.8356 | 7.8356 | 9.7945
| 18 | 89.6 | 73.4 | TC | 23.04 | 23.48 | 23.55 | 23.64 | 23.83 | 24.05 | 25.14 | 23.82 | 22.38 | 14.95 | 12.6 | 11.56 | 22.38 | [6 empty] | 9+9+18 | 30 | 9 | 9 | 18 |  |  |  | 36.9733 | 9.2433 | 9.2433 | 18.4867 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 33 | 8.5 | 8.5 | 16 |  |  | 36.9733 | 9.2433 | 9.2433 | 18.4867 |  |  | 36.672 | 9.168 | 9.168 | 18.336 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 8500 | 8500 | 17000 |  |  | 36.672 | 9.168 | 9.168 | 18.336 |  |  | 27.6884 | 6.9221 | 6.9221 | 13.8442
| 24 | 69.8 | 59 | TC | 27.01 | 27.53 | 27.42 | 27.46 | 27.23 | 27.56 | 27.05 | 25.22 | 22.79 | 18.48 | 16.18 | 14.26 | 22.79 | INTERPOLATION | 28.9122 | 24 | 28.9122 |  |  | 9+9+24 | 30 | 9 | 9 | 24 |  |  |  | 36.9733 | 7.9229 | 7.9229 | 21.1276 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 35 | 7.5 | 7.5 | 20 |  |  | 36.9733 | 7.9229 | 7.9229 | 21.1276 |  |  | 36.672 | 7.8583 | 7.8583 | 20.9554 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 8500 | 8500 | 21000 |  |  | 36.672 | 7.8583 | 7.8583 | 20.9554 |  |  | 27.6884 | 5.9332 | 5.9332 | 15.822
| 24 | 75.2 | 62.6 | TC | 29.17 | 29.73 | 29.61 | 29.66 | 29.41 | 29.76 | 29.21 | 27.24 | 24.61 | 19.96 | 17.47 | 15.4 | 24.61 | [6 empty] | 9+12+12 | 30 | 9 | 12 | 12 |  |  |  | 36.2414 | 10.0836 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 31.5 | 8.5 | 11.5 | 11.5 |  |  | 36.9733 | 10.0836 | 13.4448 | 13.4448 |  |  | 36.672 | 10.0015 | 13.3353 | 13.3353 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 9000 | 12000 | 12000 |  |  | 36.672 | 10.0015 | 13.3353 | 13.3353 |  |  | 27.1403 | 7.5514 | 9.7945 | 9.7945
| 24 | 80.6 | 66.2 | TC | 32.9 | 33.53 | 33.43 | 33.22 | 33.18 | 33.42 | 33.4 | 31.64 | 29.45 | 22.61 | 20.56 | 18.47 | 29.45 | EXTRAPOLATION | 27.649 |  |  |  |  | 9+12+18 | 30 | 9 | 12 | 18 |  |  |  | 36.9733 | 8.5323 | 11.3764 | 17.0646 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 34 | 8 | 11 | 15 |  |  | 36.9733 | 8.5323 | 11.3764 | 17.0646 |  |  | 36.672 | 8.4628 | 11.2837 | 16.9255 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 8500 | 11500 | 16000 |  |  | 36.672 | 8.4628 | 11.2837 | 16.9255 |  |  | 27.6884 | 6.3896 | 8.5195 | 12.7793
| 24 | 89.6 | 73.4 | TC | 35.21 | 35.88 | 35.77 | 35.55 | 35.5 | 35.76 | 35.74 | 33.85 | 31.51 | 24.19 | 22 | 19.76 | 31.51 | [6 empty] | 9+12+24 | 30 | 9 | 12 | 24 |  |  |  | 36.9733 | 7.3947 | 9.8596 | 19.7191 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 36 | 7 | 9 | 20 |  |  | 36.9733 | 7.3947 | 9.8596 | 19.7191 |  |  | 36.672 | 7.3344 | 9.7792 | 19.5584 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 8500 | 9500 | 21000 |  |  | 36.672 | 7.3344 | 9.7792 | 19.5584 |  |  | 27.6884 | 5.5377 | 7.3836 | 14.7672
| 30 | 69.8 | 59 | TC | 34.76 | 35.43 | 35.18 | 35.62 | 36.15 | 36.2 | 36.96 | 35.27 | 33.22 | 24.93 | 22.56 | 20.15 | 33.22 | INTERPOLATION | 36.9733 | 30 | 36.9733 |  |  | 9+18+18 | 30 | 9 | 18 | 18 |  |  |  | 36.9733 | 7.3947 | 14.7893 | 14.7893 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 36 | 8 | 14 | 14 |  |  | 36.9733 | 7.3947 | 14.7893 | 14.7893 |  |  | 36.672 | 7.3344 | 14.6688 | 14.6688 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 8500 | 14500 | 14500 |  |  | 36.672 | 7.3344 | 14.6688 | 14.6688 |  |  | 27.6884 | 5.5377 | 11.0754 | 11.0754
| 30 | 75.2 | 62.6 | TC | 35.8 | 36.49 | 36.24 | 36.69 | 37.23 | 37.29 | 38.44 | 38.09 | 35.88 | 26.92 | 24.36 | 21.76 | 35.88 | [6 empty] | 12+12+12 | 30 | 12 | 12 | 12 |  |  |  | 36.9733 | 12.3244 | 12.3244 | 12.3244 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 33.999 | 11.333 | 11.333 | 11.333 |  |  | 36.9733 | 12.3244 | 12.3244 | 12.3244 |  |  | 36.672 | 12.224 | 12.224 | 12.224 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 12000 | 12000 | 12000 |  |  | 36.672 | 12.224 | 12.224 | 12.224 |  |  | 27.6884 | 9.2295 | 9.2295 | 9.2295
| 30 | 80.6 | 66.2 | TC | 39.77 | 40.53 | 40.42 | 41.2 | 41.08 | 40.62 | 40.12 | 38.91 | 37.11 | 29.31 | 27.14 | 23.53 | 37.11 | EXTRAPOLATION | 36.9738 |  |  |  |  | 12+12+18 | 30 | 12 | 12 | 18 |  |  |  | 36.9733 | 10.5638 | 10.5638 | 15.8457 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 36 | 11 | 11 | 14 |  |  | 36.9733 | 10.5638 | 10.5638 | 15.8457 |  |  | 36.672 | 10.4777 | 10.4777 | 15.7166 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12000 | 12000 | 15000 |  |  | 36.672 | 10.4777 | 10.4777 | 15.7166 |  |  | 27.6884 | 7.911 | 7.911 | 11.8665
| 30 | 89.6 | 73.4 | TC | 42.95 | 43.77 | 43.65 | 44.49 | 44.37 | 43.87 | 43.33 | 42.02 | 40.08 | 31.65 | 29.31 | 25.41 | 40.08 | [6 empty] | 12+18+18 | 30 | 12 | 18 | 18 |  |  |  | 36.9733 | 9.2433 | 13.865 | 13.865 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 35.999 | 9.333 | 13.333 | 13.333 |  |  | 36.9733 | 9.2433 | 13.865 | 13.865 |  |  | 36.672 | 9.168 | 13.752 | 13.752 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 10000 | 14500 | 14500 |  |  | 36.672 | 9.168 | 13.752 | 13.752 |  |  | 27.6884 | 6.9221 | 10.3832 | 10.3832
| 36 | 69.8 | 59 | TC | 35.88 | 36.57 | 36.15 | 36.81 | 37.18 | 38.15 | 38.59 | 34.8 | 32.05 | 26.27 | 24.15 | 22.01 | 32.05 | INTERPOLATION | 38.9656 | 36 | 38.9656 |  |  | 12+12+24 | 30 | 12 | 12 | 24 |  |  |  | 36.9733 | 9.2433 | 9.2433 | 18.4867 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 36 | 8 | 8 | 20 |  |  | 36.9733 | 9.2433 | 9.2433 | 18.4867 |  |  | 36.672 | 9.168 | 9.168 | 18.336 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 9000 | 9000 | 21000 |  |  | 36.672 | 9.168 | 9.168 | 18.336 |  |  | 27.6884 | 6.9221 | 6.9221 | 13.8442
| 36 | 75.2 | 62.6 | TC | 38.76 | 39.5 | 39.04 | 39.75 | 40.15 | 41.2 | 41.68 | 37.58 | 34.61 | 28.37 | 26.08 | 23.77 | 34.61 | [6 empty] | 9+9+9+9 | 30 | 9 | 9 | 9 | 9 |  | 4 | 36.9733 | 9.2433 | 9.2433 | 9.2433 | 9.2433 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 36 | 9 | 9 | 9 | 9 |  | 36.9733 | 9.2433 | 9.2433 | 9.2433 | 9.2433 |  | 36.672 | 9.168 | 9.168 | 9.168 | 9.168 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 36.672 | 9.168 | 9.168 | 9.168 | 9.168 |  | 27.6884 | 6.9221 | 6.9221 | 6.9221 | 6.9221
| 36 | 80.6 | 66.2 | TC | 40.78 | 41.56 | 41.25 | 42.05 | 42.42 | 42.88 | 43.75 | 41.65 | 39.51 | 32.8 | 30.41 | 25.87 | 39.51 | EXTRAPOLATION | 37.5108 |  |  |  |  | 9+9+9+12 | 30 | 9 | 9 | 9 | 12 |  |  | 36.9733 | 8.5323 | 8.5323 | 8.5323 | 11.3764 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 36.5 | 8.5 | 8.5 | 8.5 | 11 |  | 36.9733 | 8.5323 | 8.5323 | 8.5323 | 11.3764 |  | 36.672 | 8.4628 | 8.4628 | 8.4628 | 11.2837 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9000 | 9000 | 9000 | 12000 |  | 36.672 | 8.4628 | 8.4628 | 8.4628 | 11.2837 |  | 27.6884 | 6.3896 | 6.3896 | 6.3896 | 8.5195
| 36 | 89.6 | 73.4 | TC | 42.82 | 43.64 | 43.31 | 44.15 | 44.54 | 45.02 | 45.94 | 43.73 | 41.49 | 34.44 | 31.93 | 27.19 | 41.49 | [6 empty] | 9+9+9+18 | 30 | 9 | 9 | 9 | 18 |  |  | 36.9733 | 7.3947 | 7.3947 | 7.3947 | 14.7893 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 37 | 8 | 8 | 8 | 13 |  | 36.9733 | 7.3947 | 7.3947 | 7.3947 | 14.7893 |  | 36.672 | 7.3344 | 7.3344 | 7.3344 | 14.6688 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 8500 | 8500 | 8500 | 14000 |  | 36.672 | 7.3344 | 7.3344 | 7.3344 | 14.6688 |  | 27.6884 | 5.5377 | 5.5377 | 5.5377 | 11.0754
| 48 | 69.8 | 59 | TC | 39.49 | 40.25 | 40.41 | 40.87 | 40.14 | 40.97 | 40.25 | 38.41 | 35.24 | 31.42 | 27.98 | 25.48 | 35.24 | INTERPOLATION | 45.3756 | 48 | 45.3756 |  |  | 9+9+12+12 | 30 | 9 | 9 | 12 | 12 |  |  | 36.9733 | 7.9229 | 7.9229 | 10.5638 | 10.5638 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 37 | 8 | 8 | 10.5 | 10.5 |  | 36.9733 | 7.9229 | 7.9229 | 10.5638 | 10.5638 |  | 36.672 | 7.8583 | 7.8583 | 10.4777 | 10.4777 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 8500 | 8500 | 11000 | 11000 |  | 36.672 | 7.8583 | 7.8583 | 10.4777 | 10.4777 |  | 27.6884 | 5.9332 | 5.9332 | 7.911 | 7.911
| 48 | 75.2 | 62.6 | TC | 42.65 | 43.47 | 43.64 | 44.14 | 43.35 | 44.25 | 43.47 | 41.48 | 38.06 | 33.93 | 30.22 | 27.52 | 38.06 | [6 empty] | 9+9+12+18 | 30 | 9 | 9 | 12 | 18 |  |  | 36.9733 | 6.9325 | 6.9325 | 9.2433 | 13.865 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 38 | 7.5 | 7.5 | 9 | 14 |  | 36.9733 | 6.9325 | 6.9325 | 9.2433 | 13.865 |  | 36.672 | 6.876 | 6.876 | 9.168 | 13.752 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 8000 | 8000 | 9500 | 14500 |  | 36.672 | 6.876 | 6.876 | 9.168 | 13.752 |  | 27.6884 | 5.1916 | 5.1916 | 6.9221 | 10.3832
| 48 | 80.6 | 66.2 | TC | 51.77 | 52.76 | 52.93 | 52.85 | 52.41 | 52.56 | 52.55 | 49.63 | 46.29 | 38.92 | 36.56 | 32.12 | 46.29 | EXTRAPOLATION | 42.9118 |  |  |  |  | 9+12+12+12 | 30 | 9 | 12 | 12 | 12 |  |  | 36.9733 | 7.3947 | 9.8596 | 9.8596 | 9.8596 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 37 | 7 | 10 | 10 | 10 |  | 36.9733 | 7.3947 | 9.8596 | 9.8596 | 9.8596 |  | 36.672 | 7.3344 | 9.7792 | 9.7792 | 9.7792 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 8000 | 10500 | 10500 | 10500 |  | 36.672 | 7.3344 | 9.7792 | 9.7792 | 9.7792 |  | 27.6884 | 5.5377 | 7.3836 | 7.3836 | 7.3836
| 48 | 89.6 | 73.4 | TC | 54.36 | 55.4 | 55.58 | 55.49 | 55.03 | 55.19 | 55.18 | 52.11 | 48.6 | 40.87 | 38.39 | 33.76 | 48.6 | [6 empty] | 12+12+12+12 | 30 | 12 | 12 | 12 | 12 |  |  | 36.9733 | 9.2433 | 9.2433 | 9.2433 | 9.2433 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 38 | 9.5 | 9.5 | 9.5 | 9.5 |  | 36.9733 | 9.2433 | 9.2433 | 9.2433 | 9.2433 |  | 36.672 | 9.168 | 9.168 | 9.168 | 9.168 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 10000 | 10000 | 10000 | 10000 |  | 36.672 | 9.168 | 9.168 | 9.168 | 9.168 |  | 27.6884 | 6.9221 | 6.9221 | 6.9221 | 6.9221
| 18 | 69.8 | 59 | SC | 12.81 | 13.06 | 12.9 | 13.13 | 13.22 | 13.38 | 15.17 | 14.04 | 13.1 | 10.91 | 10.24 | 9.73 | [7 empty] | 36K | 36 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
| 18 | 75.2 | 62.6 | SC | 13.83 | 14.1 | 14.33 | 14.99 | 15.29 | 15.69 | 17.07 | 15.76 | 14.64 | 10.84 | 10.92 | 9.93 | [7 empty] | 9+18 | 36 | 9 | 18 |  |  |  | 2 | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 38.9656 | 12.9885 | 25.977 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 48.7003 | 16.2334 | 32.4668 |  |  |  | 22.3112 | 7.7085 | 14.6028
| 18 | 80.6 | 66.2 | SC | 14.8 | 15.08 | 15.13 | 15.18 | 15.3 | 15.44 | 16.14 | 15.3 | 14.67 | 12.11 | 11.18 | 10.49 | [7 empty] | 9+24 | 36 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33.5 | 9.5 | 24 |  |  |  | 38.9656 | 10.627 | 28.3386 |  |  |  | 42.246 | 11.956 | 30.29 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 48.7003 | 13.2819 | 35.4184 |  |  |  | 25.7231 | 7.7085 | 18.0146
| 18 | 89.6 | 73.4 | SC | 16.58 | 16.9 | 17.2 | 17.5 | 17.87 | 17.55 | 20.61 | 20.01 | 19.24 | 14.06 | 12.1 | 11.33 | [7 empty] | 12+12 | 36 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 25 | 12.5 | 12.5 |  |  |  | 38.9656 | 19.4828 | 19.4828 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 48.7003 | 24.3501 | 24.3501 |  |  |  | 19.2712 | 9.6356 | 9.6356
| 24 | 69.8 | 59 | SC | 18.91 | 19.27 | 19.19 | 19.22 | 19.06 | 19.29 | 20.83 | 19.93 | 18.92 | 16.82 | 15.86 | 14.16 | [7 empty] | 12+18 | 36 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 38.9656 | 15.5862 | 23.3793 |  |  |  | 39.5438 | 14.945 | 24.5988 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 19000 | 48.7003 | 19.4801 | 29.2202 |  |  |  | 24.2383 | 9.6356 | 14.6028
| 24 | 75.2 | 62.6 | SC | 20.42 | 20.81 | 20.73 | 20.76 | 20.59 | 20.84 | 21.91 | 22.33 | 21.17 | 17.96 | 16.6 | 15.25 | [7 empty] | 12+24 | 36 | 12 | 24 |  |  |  |  | 37.4407 | 12.9885 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 36 | 12 | 24 |  |  |  | 38.9656 | 12.9885 | 25.977 |  |  |  | 45.235 | 14.945 | 30.29 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 48.7003 | 16.2334 | 32.4668 |  |  |  | 27.5836 | 9.569 | 18.0146
| 24 | 80.6 | 66.2 | SC | 23.03 | 23.47 | 23.4 | 23.25 | 23.23 | 23.39 | 23.04 | 22.47 | 21.5 | 18.76 | 20.28 | 18.38 | [7 empty] | 18+18 | 36 | 18 | 18 |  |  |  |  | 38.9656 | 19.4828 | 19.4828 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 37 | 18.5 | 18.5 |  |  |  | 38.9656 | 19.4828 | 19.4828 |  |  |  | 48.7003 | 24.3501 | 24.3501 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 19000; Zone 2: 19000 | 48.7003 | 24.3501 | 24.3501 |  |  |  | 28.707 | 14.3535 | 14.3535
| 24 | 89.6 | 73.4 | SC | 24.64 | 25.11 | 25.04 | 24.88 | 24.85 | 27.18 | 29.31 | 28.78 | 28.05 | 22.26 | 21.12 | 19.76 | [7 empty] | 18+24 | 36 | 18 | 24 |  |  |  |  | 38.9656 | 16.6995 | 22.266 |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 40 | 17.5 | 22.5 |  |  |  | 38.9656 | 16.6995 | 22.266 |  |  |  | 48.7003 | 20.8715 | 27.8287 |  |  |  | 54.8888 | Zone 1: 24.5988; Zone 2: 30.29; Zone 1: 18000; Zone 2: 23000 | 48.7003 | 20.8715 | 27.8287 |  |  |  | 28.707 | 12.303 | 16.404
| 30 | 69.8 | 59 | SC | 24.33 | 24.8 | 24.63 | 24.93 | 25.31 | 25.34 | 27.94 | 27.17 | 26.27 | 22.53 | 21.98 | 19.49 | [7 empty] | 24+24 | 36 | 24 | 24 |  |  |  |  | 38.9656 | 19.4828 | 19.4828 |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 42 | 21 | 21 |  |  |  | 38.9656 | 19.4828 | 19.4828 |  |  |  | 48.7003 | 24.3501 | 24.3501 |  |  |  | 60.58 | Zone 1: 30.29; Zone 2: 30.29; Zone 1: 22000; Zone 2: 22000 | 48.7003 | 24.3501 | 24.3501 |  |  |  | 28.707 | 14.3535 | 14.3535
| 30 | 75.2 | 62.6 | SC | 25.07 | 25.55 | 25.36 | 25.68 | 26.06 | 27.96 | 31.52 | 33.52 | 32.29 | 24.77 | 23.15 | 21.33 | [7 empty] | 9+9+9 | 36 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 28.5 | 9.5 | 9.5 | 9.5 |  |  | 38.9656 | 12.9885 | 12.9885 | 12.9885 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 11000 | 11000 | 11000 |  |  | 48.7003 | 16.2334 | 16.2334 | 16.2334 |  |  | 23.1254 | 7.7085 | 7.7085 | 7.7085
| 30 | 80.6 | 66.2 | SC | 27.84 | 28.37 | 28.29 | 28.56 | 28.76 | 28.43 | 30.33 | 27.74 | 27.09 | 24.22 | 26.06 | 23.06 | [7 empty] | 9+9+12 | 36 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 31 | 9.5 | 9.5 | 12 |  |  | 38.9656 | 11.6897 | 11.6897 | 15.5862 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 10500 | 10500 | 13000 |  |  | 48.7003 | 14.6101 | 14.6101 | 19.4801 |  |  | 25.0525 | 7.7085 | 7.7085 | 9.6356
| 30 | 89.6 | 73.4 | SC | 30.06 | 30.64 | 30.56 | 31.14 | 31.06 | 32.9 | 35.53 | 36.98 | 36.07 | 29.12 | 27.85 | 25.41 | [7 empty] | 9+9+18 | 36 | 9 | 9 | 18 |  |  |  | 38.9656 | 9.7414 | 9.7414 | 19.4828 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 37 | 9.5 | 9.5 | 18 |  |  | 38.9656 | 9.7414 | 9.7414 | 19.4828 |  |  | 48.2622 | 11.956 | 11.956 | 24.3501 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 10000 | 10000 | 19000 |  |  | 48.7003 | 12.1751 | 12.1751 | 24.3501 |  |  | 28.707 | 7.1767 | 7.1767 | 14.3535
| 36 | 69.8 | 59 | SC | 25.12 | 25.6 | 25.31 | 25.77 | 26.03 | 26.71 | 28.94 | 26.73 | 25.64 | 23.09 | 24.07 | 22.01 | [7 empty] | 9+9+24 | 36 | 9 | 9 | 24 |  |  |  | 38.9656 | 8.3498 | 8.3498 | 22.266 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 40.5 | 9 | 9 | 22.5 |  |  | 38.9656 | 8.3498 | 8.3498 | 22.266 |  |  | 48.7003 | 10.4358 | 10.4358 | 27.8287 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 9500 | 9500 | 23500 |  |  | 48.7003 | 10.4358 | 10.4358 | 27.8287 |  |  | 28.707 | 6.1515 | 6.1515 | 16.404
| 36 | 75.2 | 62.6 | SC | 28.29 | 28.83 | 28.5 | 29.02 | 29.31 | 31.73 | 34.59 | 31.95 | 30.11 | 25.53 | 26.08 | 23.77 | [7 empty] | 9+12+12 | 36 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 34.5 | 9.5 | 12.5 | 12.5 |  |  | 38.9656 | 10.627 | 14.1693 | 14.1693 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 10000 | 12500 | 12500 |  |  | 48.7003 | 13.2819 | 17.7092 | 17.7092 |  |  | 26.9796 | 7.7085 | 9.6356 | 9.6356
| 36 | 80.6 | 66.2 | SC | 28.54 | 29.09 | 28.88 | 29.44 | 29.69 | 30.02 | 31.06 | 29.98 | 28.45 | 25.78 | 30.28 | 25.87 | [7 empty] | 9+12+18 | 36 | 9 | 12 | 18 |  |  |  | 38.9656 | 8.9921 | 11.9894 | 17.9841 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 39 | 9 | 12 | 18 |  |  | 38.9656 | 8.9921 | 11.9894 | 17.9841 |  |  | 48.6606 | 11.2385 | 14.945 | 22.477 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 9500 | 12500 | 18000 |  |  | 48.7003 | 11.2385 | 14.9847 | 22.477 |  |  | 28.707 | 6.6247 | 8.8329 | 13.2494
| 36 | 89.6 | 73.4 | SC | 31.68 | 32.29 | 32.05 | 32.67 | 32.96 | 35.12 | 38.13 | 37.61 | 37.34 | 32.72 | 31.93 | 27.19 | [7 empty] | 9+12+24 | 36 | 9 | 12 | 24 |  |  |  | 38.9656 | 7.7931 | 10.3908 | 20.7816 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 42.5 | 9 | 12 | 21.5 |  |  | 38.9656 | 7.7931 | 10.3908 | 20.7816 |  |  | 48.7003 | 9.7401 | 12.9867 | 25.9735 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 9500 | 12500 | 22000 |  |  | 48.7003 | 9.7401 | 12.9867 | 25.9735 |  |  | 28.707 | 5.7414 | 7.6552 | 15.3104
| 48 | 69.8 | 59 | SC | 27.65 | 28.18 | 28.29 | 28.61 | 28.1 | 29.91 | 36.89 | 35.46 | 34.61 | 30.86 | 27.98 | 25.48 | [7 empty] | 9+18+18 | 36 | 9 | 18 | 18 |  |  |  | 38.9656 | 7.7931 | 15.5862 | 15.5862 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 45 | 9 | 18 | 18 |  |  | 38.9656 | 7.7931 | 15.5862 | 15.5862 |  |  | 48.7003 | 9.7401 | 19.4801 | 19.4801 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 9500 | 18500 | 18500 |  |  | 48.7003 | 9.7401 | 19.4801 | 19.4801 |  |  | 28.707 | 5.7414 | 11.4828 | 11.4828
| 48 | 75.2 | 62.6 | SC | 31.13 | 31.73 | 31.86 | 32.22 | 31.65 | 34.07 | 36.08 | 35.26 | 33.11 | 30.54 | 30.22 | 27.52 | [7 empty] | 9+18+24 | 36 | 9 | 18 | 24 |  |  |  | 38.9656 | 6.8763 | 13.7525 | 18.3367 |  |  | 54.7364 | 10.4631 | 19.8211 | 24.4522 |  |  | 46 | 8.5 | 16 | 21.5 |  |  | 38.9656 | 6.8763 | 13.7525 | 18.3367 |  |  | 48.7003 | 8.5942 | 17.1883 | 22.9178 |  |  | 66.8448 | 11.956 | 24.5988 | 30.29 |  |  | 9000 | 17000 | 22000 |  |  | 48.7003 | 8.5942 | 17.1883 | 22.9178 |  |  | 28.707 | 5.0659 | 10.1319 | 13.5092
| 48 | 80.6 | 66.2 | SC | 36.24 | 36.93 | 37.05 | 37 | 36.69 | 36.79 | 37.31 | 36.23 | 34.72 | 36.3 | 35.75 | 32.12 | [7 empty] | 9+24+24 | 36 | 9 | 24 | 24 |  |  |  | 38.9656 | 6.1525 | 16.4065 | 16.4065 |  |  | 59.3676 | 10.4631 | 24.4522 | 24.4522 |  |  | 48 | 8 | 20 | 20 |  |  | 38.9656 | 6.1525 | 16.4065 | 16.4065 |  |  | 48.7003 | 7.6895 | 20.5054 | 20.5054 |  |  | 72.536 | 11.956 | 30.29 | 30.29 |  |  | 8500 | 21000 | 21000 |  |  | 48.7003 | 7.6895 | 20.5054 | 20.5054 |  |  | 28.707 | 4.5327 | 12.0872 | 12.0872
| 48 | 89.6 | 73.4 | SC | 40.22 | 40.99 | 41.13 | 41.06 | 40.72 | 43.05 | 45.8 | 44.82 | 43.74 | 38.82 | 38.39 | 33.76 | [7 empty] | 12+12+12 | 36 | 12 | 12 | 12 |  |  |  | 38.9656 | 12.9885 | 12.9885 | 12.9885 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 36 | 12 | 12 | 12 |  |  | 38.9656 | 12.9885 | 12.9885 | 12.9885 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 13000 | 13000 | 13000 |  |  | 48.7003 | 16.2334 | 16.2334 | 16.2334 |  |  | 28.707 | 9.569 | 9.569 | 9.569
| 18 | 69.8 | 59 | SCR | 70% | 70.03% | 69.99% | 70.03% | 70.02% | 69.98% | 74.88% | 76.02% | 79.25% | 96.72% | 96.24% | 98.68% | 79.25% | INTERPOLATION | 72.63% | 18 | 72.63% |  |  | 12+12+18 | 36 | 12 | 12 | 18 |  |  |  | 38.9656 | 11.133 | 11.133 | 16.6995 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 41 | 12 | 12 | 17 |  |  | 38.9656 | 11.133 | 11.133 | 16.6995 |  |  | 48.7003 | 13.9144 | 13.9144 | 20.8715 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12500 | 12500 | 18000 |  |  | 48.7003 | 13.9144 | 13.9144 | 20.8715 |  |  | 28.707 | 8.202 | 8.202 | 12.303
| 18 | 75.2 | 62.6 | SCR | 69.99% | 70.01% | 72.01% | 74.02% | 74.99% | 75.98% | 78.02% | 79% | 82.02% | 89% | 95.04% | 98.03% | 82.02% | [6 empty] | 12+12+24 | 36 | 12 | 12 | 24 |  |  |  | 38.9656 | 9.7414 | 9.7414 | 19.4828 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 44 | 11 | 11 | 22 |  |  | 38.9656 | 9.7414 | 9.7414 | 19.4828 |  |  | 48.7003 | 12.1751 | 12.1751 | 24.3501 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 11500 | 11500 | 23000 |  |  | 48.7003 | 12.1751 | 12.1751 | 24.3501 |  |  | 28.707 | 7.1767 | 7.1767 | 14.3535
| 18 | 80.6 | 66.2 | SCR | 70.01% | 70.01% | 70.01% | 69.99% | 69.99% | 69.99% | 69.99% | 70.02% | 71.46% | 88.27% | 96.71% | 98.87% | 71.46% | EXTRAPOLATION | 79.95% |  |  |  |  | 12+18+18 | 36 | 12 | 18 | 18 |  |  |  | 38.9656 | 9.7414 | 14.6121 | 14.6121 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 44 | 11 | 16.5 | 16.5 |  |  | 38.9656 | 9.7414 | 14.6121 | 14.6121 |  |  | 48.7003 | 12.1751 | 18.2626 | 18.2626 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 11500 | 17000 | 17000 |  |  | 48.7003 | 12.1751 | 18.2626 | 18.2626 |  |  | 28.707 | 7.1767 | 10.7651 | 10.7651
| 18 | 89.6 | 73.4 | SCR | 71.96% | 71.98% | 73.04% | 74.03% | 74.99% | 72.97% | 81.98% | 84.01% | 85.97% | 94.05% | 96.03% | 98.01% | 85.97% | [6 empty] | 12+18+24 | 36 | 12 | 18 | 24 |  |  |  | 38.9656 | 8.659 | 12.9885 | 17.318 |  |  | 57.3522 | 13.0789 | 19.8211 | 24.4522 |  |  | 47.5 | 10.5 | 15.5 | 21.5 |  |  | 38.9656 | 8.659 | 12.9885 | 17.318 |  |  | 48.7003 | 10.8223 | 16.2334 | 21.6446 |  |  | 69.8338 | 14.945 | 24.5988 | 30.29 |  |  | 11000 | 16000 | 22000 |  |  | 48.7003 | 10.8223 | 16.2334 | 21.6446 |  |  | 28.707 | 6.3793 | 9.569 | 12.7587
| 24 | 69.8 | 59 | SCR | 70.01% | 70% | 69.99% | 69.99% | 70% | 69.99% | 77.01% | 79.02% | 83.02% | 91.02% | 98.02% | 99.3% | 83.02% | INTERPOLATION | 74.45% | 24 | 74.45% |  |  | 12+24+24 | 36 | 12 | 24 | 24 |  |  |  | 38.9656 | 7.7931 | 15.5862 | 15.5862 |  |  | 61.9833 | 13.0789 | 24.4522 | 24.4522 |  |  | 50 | 10 | 20 | 20 |  |  | 38.9656 | 7.7931 | 15.5862 | 15.5862 |  |  | 48.7003 | 9.7401 | 19.4801 | 19.4801 |  |  | 75.525 | 14.945 | 30.29 | 30.29 |  |  | 11000 | 20500 | 20500 |  |  | 48.7003 | 9.7401 | 19.4801 | 19.4801 |  |  | 28.707 | 5.7414 | 11.4828 | 11.4828
| 24 | 75.2 | 62.6 | SCR | 70% | 70% | 70.01% | 69.99% | 70.01% | 70.03% | 75.01% | 81.98% | 86.02% | 89.98% | 95.02% | 99.03% | 86.02% | [6 empty] | 18+18+18 | 36 | 18 | 18 | 18 |  |  |  | 38.9656 | 12.9885 | 12.9885 | 12.9885 |  |  | 59.4633 | 19.8211 | 19.8211 | 19.8211 |  |  | 48 | 16 | 16 | 16 |  |  | 38.9656 | 12.9885 | 12.9885 | 12.9885 |  |  | 48.7003 | 16.2334 | 16.2334 | 16.2334 |  |  | 73.7965 | 24.5988 | 24.5988 | 24.5988 |  |  | 16500 | 16500 | 16500 |  |  | 48.7003 | 16.2334 | 16.2334 | 16.2334 |  |  | 28.707 | 9.569 | 9.569 | 9.569
| 24 | 80.6 | 66.2 | SCR | 70% | 70% | 70% | 69.99% | 70.01% | 69.99% | 68.98% | 71.02% | 73.01% | 82.97% | 98.64% | 99.51% | 73.01% | EXTRAPOLATION | 82.97% |  |  |  |  | 18+18+24 | 36 | 18 | 18 | 24 |  |  |  | 38.9656 | 11.6897 | 11.6897 | 15.5862 |  |  | 64.0944 | 19.8211 | 19.8211 | 24.4522 |  |  | 50 | 15 | 15 | 20 |  |  | 38.9656 | 11.6897 | 11.6897 | 15.5862 |  |  | 48.7003 | 14.6101 | 14.6101 | 19.4801 |  |  | 79.4876 | 24.5988 | 24.5988 | 30.29 |  |  | 15500 | 15500 | 21000 |  |  | 48.7003 | 14.6101 | 14.6101 | 19.4801 |  |  | 28.707 | 8.6121 | 8.6121 | 11.4828
| 24 | 89.6 | 73.4 | SCR | 69.98% | 69.98% | 70% | 69.99% | 70% | 76.01% | 82.01% | 85.02% | 89.02% | 92.02% | 96% | 100% | 89.02% | [6 empty] | 9+9+9+9 | 36 | 9 | 9 | 9 | 9 |  | 4 | 38.9656 | 9.7414 | 9.7414 | 9.7414 | 9.7414 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 37 | 9.25 | 9.25 | 9.25 | 9.25 |  | 38.9656 | 9.7414 | 9.7414 | 9.7414 | 9.7414 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 48.7003 | 12.1751 | 12.1751 | 12.1751 | 12.1751 |  | 28.707 | 7.1767 | 7.1767 | 7.1767 | 7.1767
| 30 | 69.8 | 59 | SCR | 69.99% | 70% | 70.01% | 69.99% | 70.01% | 70% | 75.6% | 77.03% | 79.08% | 90.37% | 97.43% | 96.72% | 79.08% | INTERPOLATION | 74.89% | 30 | 74.89% |  |  | 9+9+9+12 | 36 | 9 | 9 | 9 | 12 |  |  | 38.9656 | 8.9921 | 8.9921 | 8.9921 | 11.9894 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 39 | 9 | 9 | 9 | 12 |  | 38.9656 | 8.9921 | 8.9921 | 8.9921 | 11.9894 |  | 48.6606 | 11.2385 | 11.2385 | 11.2385 | 14.945 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9500 | 9500 | 9500 | 12500 |  | 48.7003 | 11.2385 | 11.2385 | 11.2385 | 14.9847 |  | 28.707 | 6.6247 | 6.6247 | 6.6247 | 8.8329
| 30 | 75.2 | 62.6 | SCR | 70.03% | 70.02% | 69.98% | 69.99% | 70% | 74.98% | 82% | 88% | 89.99% | 92.01% | 95.03% | 98.02% | 89.99% | [6 empty] | 9+9+9+18 | 36 | 9 | 9 | 9 | 18 |  |  | 38.9656 | 7.7931 | 7.7931 | 7.7931 | 15.5862 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 44 | 9 | 9 | 9 | 17 |  | 38.9656 | 7.7931 | 7.7931 | 7.7931 | 15.5862 |  | 48.7003 | 9.7401 | 9.7401 | 9.7401 | 19.4801 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 9500 | 9500 | 9500 | 17500 |  | 48.7003 | 9.7401 | 9.7401 | 9.7401 | 19.4801 |  | 28.707 | 5.7414 | 5.7414 | 5.7414 | 11.4828
| 30 | 80.6 | 66.2 | SCR | 70% | 70% | 69.99% | 69.32% | 70.01% | 69.99% | 75.6% | 71.29% | 73% | 82.63% | 96.02% | 98% | 73% | EXTRAPOLATION | 83.4% |  |  |  |  | 9+9+9+24 | 36 | 9 | 9 | 9 | 24 |  |  | 38.9656 | 6.8763 | 6.8763 | 6.8763 | 18.3367 |  | 55.8416 | 10.4631 | 10.4631 | 10.4631 | 24.4522 |  | 46 | 8.5 | 8.5 | 8.5 | 20.5 |  | 38.9656 | 6.8763 | 6.8763 | 6.8763 | 18.3367 |  | 48.7003 | 8.5942 | 8.5942 | 8.5942 | 22.9178 |  | 66.1581 | 11.956 | 11.956 | 11.956 | 30.29 |  | 9000 | 9000 | 9000 | 21000 |  | 48.7003 | 8.5942 | 8.5942 | 8.5942 | 22.9178 |  | 28.707 | 5.0659 | 5.0659 | 5.0659 | 13.5092
| 30 | 89.6 | 73.4 | SCR | 69.99% | 70% | 70.01% | 69.99% | 70% | 74.99% | 82% | 88.01% | 90% | 92.01% | 95.02% | 100% | 90% | [6 empty] | 9+9+12+12 | 36 | 9 | 9 | 12 | 12 |  |  | 38.9656 | 8.3498 | 8.3498 | 11.133 | 11.133 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 42 | 9 | 9 | 12 | 12 |  | 38.9656 | 8.3498 | 8.3498 | 11.133 | 11.133 |  | 48.7003 | 10.4358 | 10.4358 | 13.9144 | 13.9144 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 9500 | 9500 | 13000 | 13000 |  | 48.7003 | 10.4358 | 10.4358 | 13.9144 | 13.9144 |  | 28.707 | 6.1515 | 6.1515 | 8.202 | 8.202
| 36 | 69.8 | 59 | SCR | 70.01% | 70% | 70.01% | 70.01% | 70.01% | 70.01% | 74.99% | 76.81% | 80% | 87.89% | 99.67% | 100% | 80% | INTERPOLATION | 73.67% | 36 | 73.67% |  |  | 9+9+12+18 | 36 | 9 | 9 | 12 | 18 |  |  | 38.9656 | 7.306 | 7.306 | 9.7414 | 14.6121 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 45 | 9 | 9 | 10.5 | 16.5 |  | 38.9656 | 7.306 | 7.306 | 9.7414 | 14.6121 |  | 48.7003 | 9.1313 | 9.1313 | 12.1751 | 18.2626 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 9500 | 9500 | 11500 | 17500 |  | 48.7003 | 9.1313 | 9.1313 | 12.1751 | 18.2626 |  | 28.707 | 5.3826 | 5.3826 | 7.1767 | 10.7651
| 36 | 75.2 | 62.6 | SCR | 72.99% | 72.99% | 73% | 73.01% | 73% | 77.01% | 82.99% | 85.02% | 87% | 89.99% | 100% | 100% | 87% | [6 empty] | 9+9+12+24 | 36 | 9 | 9 | 12 | 24 |  |  | 38.9656 | 6.4943 | 6.4943 | 8.659 | 17.318 |  | 58.4573 | 10.4631 | 10.4631 | 13.0789 | 24.4522 |  | 48 | 8.5 | 8.5 | 10.5 | 20.5 |  | 38.9656 | 6.4943 | 6.4943 | 8.659 | 17.318 |  | 48.7003 | 8.1167 | 8.1167 | 10.8223 | 21.6446 |  | 69.1471 | 11.956 | 11.956 | 14.945 | 30.29 |  | 9000 | 9000 | 11000 | 21000 |  | 48.7003 | 8.1167 | 8.1167 | 10.8223 | 21.6446 |  | 28.707 | 4.7845 | 4.7845 | 6.3793 | 12.7587
| 36 | 80.6 | 66.2 | SCR | 69.99% | 70% | 70.01% | 70.01% | 69.99% | 70.01% | 70.99% | 71.98% | 72.01% | 78.6% | 99.57% | 100% | 72.01% | EXTRAPOLATION | 82.63% |  |  |  |  | 9+9+18+18 | 36 | 9 | 9 | 18 | 18 |  |  | 38.9656 | 6.4943 | 6.4943 | 12.9885 | 12.9885 |  | 60.5684 | 10.4631 | 10.4631 | 19.8211 | 19.8211 |  | 48 | 8.5 | 8.5 | 15.5 | 15.5 |  | 38.9656 | 6.4943 | 6.4943 | 12.9885 | 12.9885 |  | 48.7003 | 8.1167 | 8.1167 | 16.2334 | 16.2334 |  | 73.1097 | 11.956 | 11.956 | 24.5988 | 24.5988 |  | 9000 | 9000 | 16000 | 16000 |  | 48.7003 | 8.1167 | 8.1167 | 16.2334 | 16.2334 |  | 28.707 | 4.7845 | 4.7845 | 9.569 | 9.569
| 36 | 89.6 | 73.4 | SCR | 73.98% | 73.99% | 74% | 74% | 74% | 78.01% | 83% | 86.01% | 90% | 95.01% | 100% | 100% | 90% | [6 empty] | 9+9+18+24 | 36 | 9 | 9 | 18 | 24 |  |  | 38.9656 | 5.8448 | 5.8448 | 11.6897 | 15.5862 |  | 65.1996 | 10.4631 | 10.4631 | 19.8211 | 24.4522 |  | 50.5 | 8 | 8 | 14.5 | 20 |  | 38.9656 | 5.8448 | 5.8448 | 11.6897 | 15.5862 |  | 48.7003 | 7.305 | 7.305 | 14.6101 | 19.4801 |  | 78.8009 | 11.956 | 11.956 | 24.5988 | 30.29 |  | 8500 | 8500 | 15000 | 20000 |  | 48.7003 | 7.305 | 7.305 | 14.6101 | 19.4801 |  | 28.707 | 4.306 | 4.306 | 8.6121 | 11.4828
| 48 | 69.8 | 59 | SCR | 70.02% | 70.01% | 70.01% | 70% | 70% | 73% | 91.65% | 92.32% | 98.21% | 98.22% | 100% | 100% | 98.21% | INTERPOLATION | 76.34% | 48 | 76.34% |  |  | 9+12+12+12 | 36 | 9 | 12 | 12 | 12 |  |  | 38.9656 | 7.7931 | 10.3908 | 10.3908 | 10.3908 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 45 | 9 | 12 | 12 | 12 |  | 38.9656 | 7.7931 | 10.3908 | 10.3908 | 10.3908 |  | 48.7003 | 9.7401 | 12.9867 | 12.9867 | 12.9867 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 9500 | 12500 | 12500 | 12500 |  | 48.7003 | 9.7401 | 12.9867 | 12.9867 | 12.9867 |  | 28.707 | 5.7414 | 7.6552 | 7.6552 | 7.6552
| 48 | 75.2 | 62.6 | SCR | 72.99% | 72.99% | 73.01% | 73% | 73.01% | 76.99% | 83% | 85% | 86.99% | 90.01% | 100% | 100% | 86.99% | [6 empty] | 9+12+12+18 | 36 | 9 | 12 | 12 | 18 |  |  | 38.9656 | 6.8763 | 9.1684 | 9.1684 | 13.7525 |  | 56.442 | 10.4631 | 13.0789 | 13.0789 | 19.8211 |  | 46 | 9 | 10.5 | 10.5 | 16 |  | 38.9656 | 6.8763 | 9.1684 | 9.1684 | 13.7525 |  | 48.7003 | 8.5942 | 11.4589 | 11.4589 | 17.1883 |  | 66.4449 | 11.956 | 14.945 | 14.945 | 24.5988 |  | 9500 | 11500 | 11500 | 16500 |  | 48.7003 | 8.5942 | 11.4589 | 11.4589 | 17.1883 |  | 28.707 | 5.0659 | 6.7546 | 6.7546 | 10.1319
| 48 | 80.6 | 66.2 | SCR | 70% | 70% | 70% | 70.01% | 70.01% | 70% | 71% | 73% | 75.01% | 93.27% | 97.78% | 100% | 75.01% | EXTRAPOLATION | 87.05% |  |  |  |  | 9+12+12+24 | 36 | 9 | 12 | 12 | 24 |  |  | 38.9656 | 6.1525 | 8.2033 | 8.2033 | 16.4065 |  | 61.0731 | 10.4631 | 13.0789 | 13.0789 | 24.4522 |  | 48.5 | 8.5 | 10 | 10 | 20 |  | 38.9656 | 6.1525 | 8.2033 | 8.2033 | 16.4065 |  | 48.7003 | 7.6895 | 10.2527 | 10.2527 | 20.5054 |  | 72.1361 | 11.956 | 14.945 | 14.945 | 30.29 |  | 9000 | 10500 | 10500 | 20500 |  | 48.7003 | 7.6895 | 10.2527 | 10.2527 | 20.5054 |  | 28.707 | 4.5327 | 6.0436 | 6.0436 | 12.0872
| 48 | 89.6 | 73.4 | SCR | 73.99% | 73.99% | 74% | 74% | 74% | 78% | 83% | 86.01% | 90% | 94.98% | 100% | 100% | 90% | [6 empty] | 9+12+18+18 | 36 | 9 | 12 | 18 | 18 |  |  | 38.9656 | 6.1525 | 8.2033 | 12.3049 | 12.3049 |  | 63.1842 | 10.4631 | 13.0789 | 19.8211 | 19.8211 |  | 48.5 | 8.5 | 10 | 15 | 15 |  | 38.9656 | 6.1525 | 8.2033 | 12.3049 | 12.3049 |  | 48.7003 | 7.6895 | 10.2527 | 15.379 | 15.379 |  | 76.0987 | 11.956 | 14.945 | 24.5988 | 24.5988 |  | 9000 | 10500 | 15500 | 15500 |  | 48.7003 | 7.6895 | 10.2527 | 15.379 | 15.379 |  | 28.707 | 4.5327 | 6.0436 | 9.0654 | 9.0654
| 18 | 69.8 | 59 | Input | 1.38 | 1.41 | 1.43 | 1.46 | 1.51 | 1.54 | 1.57 | 1.71 | 1.87 | 1.43 | 1.49 | 1.54 | [7 empty] | 9+18+18+18 | 36 | 9 | 18 | 18 | 18 |  |  | 38.9656 | 5.5665 | 11.133 | 11.133 | 11.133 |  | 69.9264 | 10.4631 | 19.8211 | 19.8211 | 19.8211 |  | 50 | 8 | 14 | 14 | 14 |  | 38.9656 | 5.5665 | 11.133 | 11.133 | 11.133 |  | 48.7003 | 6.9572 | 13.9144 | 13.9144 | 13.9144 |  | 85.7525 | 11.956 | 24.5988 | 24.5988 | 24.5988 |  | 8500 | 14500 | 14500 | 14500 |  | 48.7003 | 6.9572 | 13.9144 | 13.9144 | 13.9144 |  | 28.707 | 4.101 | 8.202 | 8.202 | 8.202
| 18 | 75.2 | 62.6 | Input | 1.43 | 1.46 | 1.48 | 1.51 | 1.56 | 1.59 | 1.62 | 1.76 | 1.92 | 1.5 | 1.54 | 1.35 | [7 empty] | 12+12+12+12 | 36 | 12 | 12 | 12 | 12 |  |  | 38.9656 | 9.7414 | 9.7414 | 9.7414 | 9.7414 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 48 | 12 | 12 | 12 | 12 |  | 38.9656 | 9.7414 | 9.7414 | 9.7414 | 9.7414 |  | 48.7003 | 12.1751 | 12.1751 | 12.1751 | 12.1751 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 12500 | 12500 | 12500 | 12500 |  | 48.7003 | 12.1751 | 12.1751 | 12.1751 | 12.1751 |  | 28.707 | 7.1767 | 7.1767 | 7.1767 | 7.1767
| 18 | 80.6 | 66.2 | Input | 1.5 | 1.53 | 1.55 | 1.57 | 1.59 | 1.6 | 1.61 | 1.79 | 1.97 | 1.45 | 1.53 | 1.58 | [7 empty] | 12+12+12+18 | 36 | 12 | 12 | 12 | 18 |  |  | 38.9656 | 8.659 | 8.659 | 8.659 | 12.9885 |  | 59.0578 | 13.0789 | 13.0789 | 13.0789 | 19.8211 |  | 49 | 11 | 11 | 11 | 16 |  | 38.9656 | 8.659 | 8.659 | 8.659 | 12.9885 |  | 48.7003 | 10.8223 | 10.8223 | 10.8223 | 16.2334 |  | 69.4339 | 14.945 | 14.945 | 14.945 | 24.5988 |  | 11500 | 11500 | 11500 | 16500 |  | 48.7003 | 10.8223 | 10.8223 | 10.8223 | 16.2334 |  | 28.707 | 6.3793 | 6.3793 | 6.3793 | 9.569
| 18 | 89.6 | 73.4 | Input | 1.55 | 1.58 | 1.6 | 1.62 | 1.64 | 1.72 | 1.66 | 1.84 | 2.14 | 1.5 | 1.58 | 1.63 | [7 empty] | 12+12+12+24 | 36 | 12 | 12 | 12 | 24 |  |  | 38.9656 | 7.7931 | 7.7931 | 7.7931 | 15.5862 |  | 63.6889 | 13.0789 | 13.0789 | 13.0789 | 24.4522 |  | 50 | 10 | 10 | 10 | 20 |  | 38.9656 | 7.7931 | 7.7931 | 7.7931 | 15.5862 |  | 48.7003 | 9.7401 | 9.7401 | 9.7401 | 19.4801 |  | 75.1251 | 14.945 | 14.945 | 14.945 | 30.29 |  | 10500 | 10500 | 10500 | 20500 |  | 48.7003 | 9.7401 | 9.7401 | 9.7401 | 19.4801 |  | 28.707 | 5.7414 | 5.7414 | 5.7414 | 11.4828
| 24 | 69.8 | 59 | Input | 1.94 | 1.98 | 2.01 | 2.02 | 2.04 | 2.05 | 2.06 | 2.28 | 2.51 | 2.4 | 2.48 | 2.56 | [7 empty] | 12+12+18+18 | 36 | 12 | 12 | 18 | 18 |  |  | 38.9656 | 7.7931 | 7.7931 | 11.6897 | 11.6897 |  | 65.8 | 13.0789 | 13.0789 | 19.8211 | 19.8211 |  | 50 | 10 | 10 | 15 | 15 |  | 38.9656 | 7.7931 | 7.7931 | 11.6897 | 11.6897 |  | 48.7003 | 9.7401 | 9.7401 | 14.6101 | 14.6101 |  | 79.0877 | 14.945 | 14.945 | 24.5988 | 24.5988 |  | 10500 | 10500 | 15500 | 15500 |  | 48.7003 | 9.7401 | 9.7401 | 14.6101 | 14.6101 |  | 28.707 | 5.7414 | 5.7414 | 8.6121 | 8.6121
| 24 | 75.2 | 62.6 | Input | 1.98 | 2.02 | 2.05 | 2.06 | 2.08 | 2.09 | 2.1 | 2.32 | 2.55 | 2.44 | 2.6 | 2.6 | [7 empty] | 48K | 48 | [7 empty] | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5
| 24 | 80.6 | 66.2 | Input | 2.11 | 2.15 | 2.2 | 2.34 | 3.38 | 2.42 | 2.45 | 2.72 | 3.03 | 2.49 | 2.54 | 2.63 | [7 empty] | 9+18 | 48 | 9 | 18 |  |  |  | 2 | 30.2842 | 10.4631 | 19.8211 |  |  |  | 30.2842 | 10.4631 | 19.8211 |  |  |  | 27.5 | 9.5 | 18 |  |  |  | 45.3756 | 15.1252 | 30.2504 |  |  |  | 36.5548 | 11.956 | 24.5988 |  |  |  | 36.5548 | Zone 1: 11.956; Zone 2: 24.5988; Zone 1: 10000; Zone 2: 18000 | 54.0378 | 18.0126 | 36.0252 |  |  |  | 23.1182 | 7.9873 | 15.1309
| 24 | 89.6 | 73.4 | Input | 2.18 | 2.22 | 2.27 | 2.38 | 3.45 | 2.49 | 2.52 | 2.79 | 3.1 | 2.56 | 2.61 | 2.7 | [7 empty] | 9+24 | 48 | 9 | 24 |  |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 34.9153 | 10.4631 | 24.4522 |  |  |  | 33.5 | 9.5 | 24 |  |  |  | 45.3756 | 12.3752 | 33.0004 |  |  |  | 42.246 | 11.956 | 30.29 |  |  |  | 42.246 | Zone 1: 11.956; Zone 2: 30.29; Zone 1: 10000; Zone 2: 25000 | 54.0378 | 14.7376 | 39.3002 |  |  |  | 26.6535 | 7.9873 | 18.6662
| 30 | 69.8 | 59 | Input | 3.26 | 3.32 | 3.41 | 3.48 | 3.52 | 3.6 | 3.64 | 3.69 | 4.04 | 3.15 | 3.2 | 2.86 | [7 empty] | 12+12 | 48 | 12 | 12 |  |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 26.1578 | 13.0789 | 13.0789 |  |  |  | 25 | 12.5 | 12.5 |  |  |  | 45.3756 | 22.6878 | 22.6878 |  |  |  | 29.8901 | 14.945 | 14.945 |  |  |  | 29.8901 | Zone 1: 14.945; Zone 2: 14.945; Zone 1: 13000; Zone 2: 13000 | 54.0378 | 27.0189 | 27.0189 |  |  |  | 19.9682 | 9.9841 | 9.9841
| 30 | 75.2 | 62.6 | Input | 3.31 | 3.37 | 3.46 | 3.53 | 3.57 | 3.65 | 3.69 | 3.74 | 4.09 | 3.2 | 3.25 | 2.91 | [7 empty] | 12+18 | 48 | 12 | 18 |  |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 32.9 | 13.0789 | 19.8211 |  |  |  | 30 | 12 | 18 |  |  |  | 45.3756 | 18.1502 | 27.2253 |  |  |  | 39.5438 | 14.945 | 24.5988 |  |  |  | 39.5438 | Zone 1: 14.945; Zone 2: 24.5988; Zone 1: 13000; Zone 2: 19000 | 54.0378 | 21.6151 | 32.4227 |  |  |  | 25.115 | 9.9841 | 15.1309
| 30 | 80.6 | 66.2 | Input | 3.34 | 3.4 | 3.49 | 3.56 | 3.6 | 3.68 | 3.72 | 3.76 | 4.14 | 3.26 | 3.29 | 2.79 | [7 empty] | 12+24 | 48 | 12 | 24 |  |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 37.5311 | 13.0789 | 24.4522 |  |  |  | 36 | 12 | 24 |  |  |  | 45.3756 | 15.1252 | 30.2504 |  |  |  | 45.235 | 14.945 | 30.29 |  |  |  | 45.235 | Zone 1: 14.945; Zone 2: 30.29; Zone 1: 12500; Zone 2: 25000 | 54.0378 | 18.0126 | 36.0252 |  |  |  | 28.6503 | 9.9841 | 18.6662
| 30 | 89.6 | 73.4 | Input | 3.39 | 3.46 | 3.55 | 3.62 | 3.66 | 3.74 | 3.78 | 3.82 | 4.2 | 3.32 | 3.35 | 2.85 | [7 empty] | 18+18 | 48 | 18 | 18 |  |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 39.6422 | 19.8211 | 19.8211 |  |  |  | 37 | 18.5 | 18.5 |  |  |  | 45.3756 | 22.6878 | 22.6878 |  |  |  | 49.1976 | 24.5988 | 24.5988 |  |  |  | 49.1976 | Zone 1: 24.5988; Zone 2: 24.5988; Zone 1: 19000; Zone 2: 19000 | 54.0378 | 27.0189 | 27.0189 |  |  |  | 30.2619 | 15.1309 | 15.1309
| 36 | 69.8 | 59 | Input | 2.77 | 2.82 | 2.89 | 2.93 | 2.97 | 3.04 | 3.09 | 3.46 | 3.87 | 3.76 | 3.84 | 3.48 | [7 empty] | 18+24 | 48 | 18 | 24 |  |  |  |  | 43.8989 | 19.4467 | 24.4522 |  |  |  | 44.2733 | 19.8211 | 24.4522 |  |  |  | 40 | 17.5 | 22.5 |  |  |  | 45.3756 | 19.4467 | 25.9289 |  |  |  | 53.449 | 23.159 | 30.29 |  |  |  | 54.8888 | Zone 1: 24.5988; Zone 2: 30.29; Zone 1: 18000; Zone 2: 23000 | 54.0378 | 23.159 | 30.8787 |  |  |  | 33.5113 | 14.8451 | 18.6662
| 36 | 75.2 | 62.6 | Input | 2.84 | 2.89 | 2.96 | 3 | 3.04 | 3.11 | 3.16 | 3.53 | 3.94 | 3.83 | 3.91 | 3.55 | [7 empty] | 24+24 | 48 | 24 | 24 |  |  |  |  | 45.3756 | 22.6878 | 22.6878 |  |  |  | 48.9044 | 24.4522 | 24.4522 |  |  |  | 42 | 21 | 21 |  |  |  | 45.3756 | 22.6878 | 22.6878 |  |  |  | 54.0378 | 27.0189 | 27.0189 |  |  |  | 60.58 | Zone 1: 30.29; Zone 2: 30.29; Zone 1: 22000; Zone 2: 22000 | 54.0378 | 27.0189 | 27.0189 |  |  |  | 34.6386 | 17.3193 | 17.3193
| 36 | 80.6 | 66.2 | Input | 2.87 | 2.92 | 2.95 | 2.97 | 3.01 | 3.12 | 3.16 | 3.55 | 3.99 | 3.88 | 3.93 | 3.54 | [7 empty] | 9+9+9 | 48 | 9 | 9 | 9 |  |  | 3 | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 31.3893 | 10.4631 | 10.4631 | 10.4631 |  |  | 28.5 | 9.5 | 9.5 | 9.5 |  |  | 45.3756 | 15.1252 | 15.1252 | 15.1252 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 35.8681 | 11.956 | 11.956 | 11.956 |  |  | 11000 | 11000 | 11000 |  |  | 54.0378 | 18.0126 | 18.0126 | 18.0126 |  |  | 23.9618 | 7.9873 | 7.9873 | 7.9873
| 36 | 89.6 | 73.4 | Input | 2.93 | 2.99 | 3.02 | 3.04 | 3.08 | 3.19 | 3.23 | 3.62 | 4.06 | 3.95 | 4 | 3.61 | [7 empty] | 9+9+12 | 48 | 9 | 9 | 12 |  |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 34.0051 | 10.4631 | 10.4631 | 13.0789 |  |  | 31 | 9.5 | 9.5 | 12 |  |  | 45.3756 | 13.6127 | 13.6127 | 18.1502 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 38.8571 | 11.956 | 11.956 | 14.945 |  |  | 10500 | 10500 | 13000 |  |  | 54.0378 | 16.2113 | 16.2113 | 21.6151 |  |  | 25.9586 | 7.9873 | 7.9873 | 9.9841
| 48 | 69.8 | 59 | Input | 2.2 | 2.24 | 2.28 | 2.35 | 2.38 | 2.41 | 2.46 | 2.78 | 3.11 | 3.45 | 3.64 | 3.08 | [7 empty] | 9+9+18 | 48 | 9 | 9 | 18 |  |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 40.7473 | 10.4631 | 10.4631 | 19.8211 |  |  | 37 | 9.5 | 9.5 | 18 |  |  | 45.3756 | 11.3439 | 11.3439 | 22.6878 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 48.5109 | 11.956 | 11.956 | 24.5988 |  |  | 10000 | 10000 | 19000 |  |  | 54.0378 | 13.5094 | 13.5094 | 27.0189 |  |  | 31.1055 | 7.9873 | 7.9873 | 15.1309
| 48 | 75.2 | 62.6 | Input | 2.27 | 2.31 | 2.35 | 2.42 | 2.45 | 2.48 | 2.53 | 2.85 | 3.18 | 3.52 | 3.71 | 3.15 | [7 empty] | 9+9+24 | 48 | 9 | 9 | 24 |  |  |  | 43.8989 | 9.7233 | 9.7233 | 24.4522 |  |  | 45.3784 | 10.4631 | 10.4631 | 24.4522 |  |  | 40.5 | 9 | 9 | 22.5 |  |  | 45.3756 | 9.7233 | 9.7233 | 25.9289 |  |  | 53.449 | 11.5795 | 11.5795 | 30.29 |  |  | 54.202 | 11.956 | 11.956 | 30.29 |  |  | 9500 | 9500 | 23500 |  |  | 54.0378 | 11.5795 | 11.5795 | 30.8787 |  |  | 33.5113 | 7.4225 | 7.4225 | 18.6662
| 48 | 80.6 | 66.2 | Input | 3.57 | 3.64 | 3.69 | 3.75 | 3.81 | 3.86 | 3.96 | 4.44 | 4.94 | 3.9 | 4.12 | 3.68 | [7 empty] | 9+12+12 | 48 | 9 | 12 | 12 |  |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 36.6209 | 10.4631 | 13.0789 | 13.0789 |  |  | 34.5 | 9.5 | 12.5 | 12.5 |  |  | 45.3756 | 12.3752 | 16.5002 | 16.5002 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 41.8461 | 11.956 | 14.945 | 14.945 |  |  | 10000 | 13000 | 13000 |  |  | 54.0378 | 14.7376 | 19.6501 | 19.6501 |  |  | 27.9555 | 7.9873 | 9.9841 | 9.9841
| 48 | 89.6 | 73.4 | Input | 3.64 | 3.71 | 3.76 | 3.82 | 3.88 | 3.93 | 4.03 | 4.51 | 5.01 | 3.97 | 4.19 | 3.75 | [7 empty] | 9+12+18 | 48 | 9 | 12 | 18 |  |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 43.3631 | 10.4631 | 13.0789 | 19.8211 |  |  | 39 | 9 | 12 | 18 |  |  | 45.3756 | 10.4713 | 13.9617 | 20.9426 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 51.4999 | 11.956 | 14.945 | 24.5988 |  |  | 9500 | 12500 | 19000 |  |  | 54.0378 | 12.4703 | 16.627 | 24.9405 |  |  | 33.1023 | 7.9873 | 9.9841 | 15.1309
| LEGEND | [22 empty] | 9+12+24 | 48 | 9 | 12 | 24 |  |  |  | 45.3756 | 9.0751 | 12.1001 | 24.2003 |  |  | 47.9942 | 10.4631 | 13.0789 | 24.4522 |  |  | 42.5 | 9 | 12 | 21.5 |  |  | 45.3756 | 9.0751 | 12.1001 | 24.2003 |  |  | 54.0378 | 10.8076 | 14.4101 | 28.8201 |  |  | 57.191 | 11.956 | 14.945 | 30.29 |  |  | 9500 | 12500 | 22000 |  |  | 54.0378 | 10.8076 | 14.4101 | 28.8201 |  |  | 34.6386 | 6.9277 | 9.2369 | 18.4739
| DB - Dry Bulb | [22 empty] | 9+18+18 | 48 | 9 | 18 | 18 |  |  |  | 45.3756 | 9.0751 | 18.1502 | 18.1502 |  |  | 50.1053 | 10.4631 | 19.8211 | 19.8211 |  |  | 45 | 9 | 18 | 18 |  |  | 45.3756 | 9.0751 | 18.1502 | 18.1502 |  |  | 54.0378 | 10.8076 | 21.6151 | 21.6151 |  |  | 61.1537 | 11.956 | 24.5988 | 24.5988 |  |  | 9500 | 18500 | 18500 |  |  | 54.0378 | 10.8076 | 21.6151 | 21.6151 |  |  | 34.6386 | 6.9277 | 13.8554 | 13.8554
| WB - Wet Bulb | [22 empty] | 9+18+24 | 48 | 9 | 18 | 24 |  |  |  | 45.3756 | 8.0075 | 16.0149 | 21.3532 |  |  | 54.7364 | 10.4631 | 19.8211 | 24.4522 |  |  | 46 | 8.5 | 16 | 21.5 |  |  | 45.3756 | 8.0075 | 16.0149 | 21.3532 |  |  | 54.0378 | 9.5361 | 19.0722 | 25.4295 |  |  | 66.8448 | 11.956 | 24.5988 | 30.29 |  |  | 9500 | 16500 | 22000 |  |  | 54.0378 | 9.5361 | 19.0722 | 25.4295 |  |  | 34.6386 | 6.1127 | 12.2254 | 16.3005
| TC - Total Net Capacity (1000 Btu/hour) | [22 empty] | 9+24+24 | 48 | 9 | 24 | 24 |  |  |  | 45.3756 | 7.1646 | 19.1055 | 19.1055 |  |  | 59.3676 | 10.4631 | 24.4522 | 24.4522 |  |  | 48 | 8 | 20 | 20 |  |  | 45.3756 | 7.1646 | 19.1055 | 19.1055 |  |  | 54.0378 | 8.5323 | 22.7527 | 22.7527 |  |  | 72.536 | 11.956 | 30.29 | 30.29 |  |  | 8500 | 21000 | 21000 |  |  | 54.0378 | 8.5323 | 22.7527 | 22.7527 |  |  | 34.6386 | 5.4692 | 14.5847 | 14.5847
| SC - Sensible Capacity (1000 Btu/hour) | [22 empty] | 12+12+12 | 48 | 12 | 12 | 12 |  |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 39.2367 | 13.0789 | 13.0789 | 13.0789 |  |  | 36 | 12 | 12 | 12 |  |  | 45.3756 | 15.1252 | 15.1252 | 15.1252 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 44.8351 | 14.945 | 14.945 | 14.945 |  |  | 13000 | 13000 | 13000 |  |  | 54.0378 | 18.0126 | 18.0126 | 18.0126 |  |  | 29.9523 | 9.9841 | 9.9841 | 9.9841
| Input - Total Power (kW) | [22 empty] | 12+12+18 | 48 | 12 | 12 | 18 |  |  |  | 45.3756 | 12.9644 | 12.9644 | 19.4467 |  |  | 45.9789 | 13.0789 | 13.0789 | 19.8211 |  |  | 41 | 12 | 12 | 17 |  |  | 45.3756 | 12.9644 | 12.9644 | 19.4467 |  |  | 53.0491 | 14.945 | 14.945 | 23.159 |  |  | 54.4889 | 14.945 | 14.945 | 24.5988 |  |  | 12500 | 12500 | 18000 |  |  | 54.0378 | 15.4394 | 15.4394 | 23.159 |  |  | 34.6386 | 9.8967 | 9.8967 | 14.8451
[24 empty] | 12+12+24 | 48 | 12 | 12 | 24 |  |  |  | 45.3756 | 11.3439 | 11.3439 | 22.6878 |  |  | 50.61 | 13.0789 | 13.0789 | 24.4522 |  |  | 44 | 11 | 11 | 22 |  |  | 45.3756 | 11.3439 | 11.3439 | 22.6878 |  |  | 54.0378 | 13.5094 | 13.5094 | 27.0189 |  |  | 60.1801 | 14.945 | 14.945 | 30.29 |  |  | 11500 | 11500 | 23000 |  |  | 54.0378 | 13.5094 | 13.5094 | 27.0189 |  |  | 34.6386 | 8.6596 | 8.6596 | 17.3193
| HEATING PERFORMANCE DATA | [22 empty] | 12+18+18 | 48 | 12 | 18 | 18 |  |  |  | 45.3756 | 11.3439 | 17.0158 | 17.0158 |  |  | 52.7211 | 13.0789 | 19.8211 | 19.8211 |  |  | 44 | 11 | 16.5 | 16.5 |  |  | 45.3756 | 11.3439 | 17.0158 | 17.0158 |  |  | 54.0378 | 13.5094 | 20.2642 | 20.2642 |  |  | 64.1427 | 14.945 | 24.5988 | 24.5988 |  |  | 11500 | 17000 | 17000 |  |  | 54.0378 | 13.5094 | 20.2642 | 20.2642 |  |  | 34.6386 | 8.6596 | 12.9895 | 12.9895
| Model | Heating |  |  |  | Outdoor conditions (DB) | [17 empty] | 12+18+24 | 48 | 12 | 18 | 24 |  |  |  | 45.3756 | 10.0835 | 15.1252 | 20.1669 |  |  | 57.3522 | 13.0789 | 19.8211 | 24.4522 |  |  | 48 | 10.5 | 16 | 21.5 |  |  | 45.3756 | 10.0835 | 15.1252 | 20.1669 |  |  | 54.0378 | 12.0084 | 18.0126 | 24.0168 |  |  | 69.8338 | 14.945 | 24.5988 | 30.29 |  |  | 11000 | 16000 | 22000 |  |  | 54.0378 | 12.0084 | 18.0126 | 24.0168 |  |  | 34.6386 | 7.6975 | 11.5462 | 15.3949
|  | Indoor Conditions DB | [21 empty] | 12+24+24 | 48 | 12 | 24 | 24 |  |  |  | 45.3756 | 9.0751 | 18.1502 | 18.1502 |  |  | 61.9833 | 13.0789 | 24.4522 | 24.4522 |  |  | 50 | 10 | 20 | 20 |  |  | 45.3756 | 9.0751 | 18.1502 | 18.1502 |  |  | 54.0378 | 10.8076 | 21.6151 | 21.6151 |  |  | 75.525 | 14.945 | 30.29 | 30.29 |  |  | 11000 | 20500 | 20500 |  |  | 54.0378 | 10.8076 | 21.6151 | 21.6151 |  |  | 34.6386 | 6.9277 | 13.8554 | 13.8554
[5 empty] | -22 | -13 | -4 | 0 | 5 | 17 | 19.4 | 24.8 | 32 | 39.2 | 44.6 | 53.6 |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | CAPACITY |  |  | 18+18+18 | 48 | 18 | 18 | 18 |  |  |  | 45.3756 | 15.1252 | 15.1252 | 15.1252 |  |  | 59.4633 | 19.8211 | 19.8211 | 19.8211 |  |  | 48 | 16 | 16 | 16 |  |  | 45.3756 | 15.1252 | 15.1252 | 15.1252 |  |  | 54.0378 | 18.0126 | 18.0126 | 18.0126 |  |  | 73.7965 | 24.5988 | 24.5988 | 24.5988 |  |  | 16500 | 16500 | 16500 |  |  | 54.0378 | 18.0126 | 18.0126 | 18.0126 |  |  | 34.6386 | 11.5462 | 11.5462 | 11.5462
| 18 | 59 |  | TC | 7.25 | 9.05 | 11.18 | 12.58 | 14.73 | 16.91 | 17.12 | 17.64 | 18.36 | 19.67 | 23.68 | 25.16 | 23.7458 | INTERPOLATION | 20.4583 | 18 | 20.4583 |  |  | 18+18+24 | 48 | 18 | 18 | 24 |  |  |  | 45.3756 | 13.6127 | 13.6127 | 18.1502 |  |  | 64.0944 | 19.8211 | 19.8211 | 24.4522 |  |  | 50 | 15 | 15 | 20 |  |  | 45.3756 | 13.6127 | 13.6127 | 18.1502 |  |  | 54.0378 | 16.2113 | 16.2113 | 21.6151 |  |  | 79.4876 | 24.5988 | 24.5988 | 30.29 |  |  | 15500 | 15500 | 21000 |  |  | 54.0378 | 16.2113 | 16.2113 | 21.6151 |  |  | 34.6386 | 10.3916 | 10.3916 | 13.8554
| 18 | 64.4 |  | TC | 7.14 | 8.91 | 11.01 | 12.39 | 14.56 | 16.66 | 16.86 | 17.38 | 18.08 | 19.37 | 23.32 | 24.78 | 23.3849 | [6 empty] | 9+9+9+9 | 48 | 9 | 9 | 9 | 9 |  | 4 | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 41.8524 | 10.4631 | 10.4631 | 10.4631 | 10.4631 |  | 37 | 9.25 | 9.25 | 9.25 | 9.25 |  | 45.3756 | 11.3439 | 11.3439 | 11.3439 | 11.3439 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 47.8241 | 11.956 | 11.956 | 11.956 | 11.956 |  | 9500 | 9500 | 9500 | 9500 |  | 54.0378 | 13.5094 | 13.5094 | 13.5094 | 13.5094 |  | 31.9491 | 7.9873 | 7.9873 | 7.9873 | 7.9873
| 18 | 69 |  | TC | 5.31 | 6.16 | 7.02 | 8.13 | 14.4 | 13.39 | 13.48 | 16.58 | 17.86 | 18.05 | 20.6 | 20.09 | 20.5773 | EXTRAPOLATION | 20.7579 |  |  |  |  | 9+9+9+12 | 48 | 9 | 9 | 9 | 12 |  |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 44.4682 | 10.4631 | 10.4631 | 10.4631 | 13.0789 |  | 39 | 9 | 9 | 9 | 12 |  | 45.3756 | 10.4713 | 10.4713 | 10.4713 | 13.9617 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 50.8131 | 11.956 | 11.956 | 11.956 | 14.945 |  | 9500 | 9500 | 9500 | 12500 |  | 54.0378 | 12.4703 | 12.4703 | 12.4703 | 16.627 |  | 33.9459 | 7.9873 | 7.9873 | 7.9873 | 9.9841
| 18 | 71.6 |  | TC | 5.23 | 6.07 | 6.91 | 8.01 | 13.56 | 13.19 | 13.28 | 16.33 | 17.59 | 17.78 | 20.29 | 19.79 | 20.2678 | [6 empty] | 9+9+9+18 | 48 | 9 | 9 | 9 | 18 |  |  | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 18.1502 |  | 51.2104 | 10.4631 | 10.4631 | 10.4631 | 19.8211 |  | 44 | 9 | 9 | 9 | 17 |  | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 18.1502 |  | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 21.6151 |  | 60.4669 | 11.956 | 11.956 | 11.956 | 24.5988 |  | 9500 | 9500 | 9500 | 17500 |  | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 21.6151 |  | 34.6386 | 6.9277 | 6.9277 | 6.9277 | 13.8554
| 24 | 59 |  | TC | 13.95 | 17.73 | 20 | 22.45 | 23.85 | 25.34 | 25.72 | 27.96 | 30.05 | 31.82 | 36.46 | 40.37 | 36.6338 | INTERPOLATION | 35.7621 | 24 | 35.7621 |  |  | 9+9+9+24 | 48 | 9 | 9 | 9 | 24 |  |  | 45.3756 | 8.0075 | 8.0075 | 8.0075 | 21.3532 |  | 55.8416 | 10.4631 | 10.4631 | 10.4631 | 24.4522 |  | 46 | 8.5 | 8.5 | 8.5 | 20.5 |  | 45.3756 | 8.0075 | 8.0075 | 8.0075 | 21.3532 |  | 54.0378 | 9.5361 | 9.5361 | 9.5361 | 25.4295 |  | 66.1581 | 11.956 | 11.956 | 11.956 | 30.29 |  | 9000 | 9000 | 9000 | 21000 |  | 54.0378 | 9.5361 | 9.5361 | 9.5361 | 25.4295 |  | 34.6386 | 6.1127 | 6.1127 | 6.1127 | 16.3005
| 24 | 64.4 |  | TC | 13.78 | 17.51 | 19.75 | 22.17 | 23.55 | 25.03 | 25.4 | 27.61 | 29.75 | 31.49 | 35.92 | 39.77 | 36.0911 | [6 empty] | 9+9+12+12 | 48 | 9 | 9 | 12 | 12 |  |  | 45.3756 | 9.7233 | 9.7233 | 12.9644 | 12.9644 |  | 47.084 | 10.4631 | 10.4631 | 13.0789 | 13.0789 |  | 42 | 9 | 9 | 12 | 12 |  | 45.3756 | 9.7233 | 9.7233 | 12.9644 | 12.9644 |  | 53.0491 | 11.5795 | 11.5795 | 14.945 | 14.945 |  | 53.8021 | 11.956 | 11.956 | 14.945 | 14.945 |  | 9500 | 9500 | 13000 | 13000 |  | 54.0378 | 11.5795 | 11.5795 | 15.4394 | 15.4394 |  | 34.6386 | 7.4225 | 7.4225 | 9.8967 | 9.8967
| 24 | 69 |  | TC | 13.68 | 17.37 | 19.6 | 22 | 23.37 | 24.83 | 25.2 | 27.4 | 29.52 | 30.82 | 35.77 | 40.21 | 35.9673 | EXTRAPOLATION | 35.6899 |  |  |  |  | 9+9+12+18 | 48 | 9 | 9 | 12 | 18 |  |  | 45.3756 | 8.5079 | 8.5079 | 11.3439 | 17.0158 |  | 53.8262 | 10.4631 | 10.4631 | 13.0789 | 19.8211 |  | 46 | 9 | 9 | 11 | 17 |  | 45.3756 | 8.5079 | 8.5079 | 11.3439 | 17.0158 |  | 54.0378 | 10.1321 | 10.1321 | 13.5094 | 20.2642 |  | 63.4559 | 11.956 | 11.956 | 14.945 | 24.5988 |  | 9500 | 9500 | 11500 | 17500 |  | 54.0378 | 10.1321 | 10.1321 | 13.5094 | 20.2642 |  | 34.6386 | 6.4947 | 6.4947 | 8.6596 | 12.9895
| 24 | 71.6 |  | TC | 13.61 | 17.29 | 19.5 | 21.89 | 23.26 | 24.71 | 25.08 | 27.26 | 29.37 | 30.4 | 35.24 | 39.6 | 35.4338 | [6 empty] | 9+9+12+24 | 48 | 9 | 9 | 12 | 24 |  |  | 45.3756 | 7.5626 | 7.5626 | 10.0835 | 20.1669 |  | 58.4573 | 10.4631 | 10.4631 | 13.0789 | 24.4522 |  | 48 | 8.5 | 8.5 | 10.5 | 20.5 |  | 45.3756 | 7.5626 | 7.5626 | 10.0835 | 20.1669 |  | 54.0378 | 9.0063 | 9.0063 | 12.0084 | 24.0168 |  | 69.1471 | 11.956 | 11.956 | 14.945 | 30.29 |  | 9000 | 9000 | 11000 | 21000 |  | 54.0378 | 9.0063 | 9.0063 | 12.0084 | 24.0168 |  | 34.6386 | 5.7731 | 5.7731 | 7.6975 | 15.3949
| 30 | 59 |  | TC | 18.43 | 22.26 | 24.22 | 26.51 | 27.98 | 31.38 | 31.66 | 33.05 | 34.71 | 36.63 | 37.99 | 41.37 | 38.1402 | INTERPOLATION | 36.672 | 30 | 36.672 |  |  | 9+9+18+18 | 48 | 9 | 9 | 18 | 18 |  |  | 45.3756 | 7.5626 | 7.5626 | 15.1252 | 15.1252 |  | 60.5684 | 10.4631 | 10.4631 | 19.8211 | 19.8211 |  | 48 | 8.5 | 8.5 | 15.5 | 15.5 |  | 45.3756 | 7.5626 | 7.5626 | 15.1252 | 15.1252 |  | 54.0378 | 9.0063 | 9.0063 | 18.0126 | 18.0126 |  | 73.1097 | 11.956 | 11.956 | 24.5988 | 24.5988 |  | 9000 | 9000 | 16000 | 16000 |  | 54.0378 | 9.0063 | 9.0063 | 18.0126 | 18.0126 |  | 34.6386 | 5.7731 | 5.7731 | 11.5462 | 11.5462
| 30 | 64.4 |  | TC | 18.18 | 21.95 | 23.88 | 26.14 | 27.59 | 30.92 | 31.2 | 32.56 | 34.21 | 36.1 | 37.42 | 40.75 | 37.568 | [6 empty] | 9+9+18+24 | 48 | 9 | 9 | 18 | 24 |  |  | 45.3756 | 6.8063 | 6.8063 | 13.6127 | 18.1502 |  | 65.1996 | 10.4631 | 10.4631 | 19.8211 | 24.4522 |  | 50.5 | 8 | 8 | 14.5 | 20 |  | 45.3756 | 6.8063 | 6.8063 | 13.6127 | 18.1502 |  | 54.0378 | 8.1057 | 8.1057 | 16.2113 | 21.6151 |  | 78.8009 | 11.956 | 11.956 | 24.5988 | 30.29 |  | 8500 | 8500 | 15000 | 20000 |  | 54.0378 | 8.1057 | 8.1057 | 16.2113 | 21.6151 |  | 34.6386 | 5.1958 | 5.1958 | 10.3916 | 13.8554
| 30 | 69 |  | TC | 16.49 | 20.39 | 21.78 | 23.72 | 25.98 | 27.33 | 27.78 | 31.46 | 33.54 | 35.63 | 36.75 | 39.77 | 36.8842 | EXTRAPOLATION | 36.6666 |  |  |  |  | 9+12+12+12 | 48 | 9 | 12 | 12 | 12 |  |  | 45.3756 | 9.0751 | 12.1001 | 12.1001 | 12.1001 |  | 49.6998 | 10.4631 | 13.0789 | 13.0789 | 13.0789 |  | 45 | 9 | 12 | 12 | 12 |  | 45.3756 | 9.0751 | 12.1001 | 12.1001 | 12.1001 |  | 54.0378 | 10.8076 | 14.4101 | 14.4101 | 14.4101 |  | 56.7911 | 11.956 | 14.945 | 14.945 | 14.945 |  | 9500 | 12500 | 12500 | 12500 |  | 54.0378 | 10.8076 | 14.4101 | 14.4101 | 14.4101 |  | 34.6386 | 6.9277 | 9.2369 | 9.2369 | 9.2369
| 30 | 71.6 |  | TC | 15.32 | 19.18 | 21.52 | 23.44 | 25.67 | 26.93 | 27.38 | 30.99 | 33.04 | 35.1 | 36.2 | 39.18 | 36.3324 | [6 empty] | 9+12+12+18 | 48 | 9 | 12 | 12 | 18 |  |  | 45.3756 | 8.0075 | 10.6766 | 10.6766 | 16.0149 |  | 56.442 | 10.4631 | 13.0789 | 13.0789 | 19.8211 |  | 47 | 9 | 11 | 11 | 16 |  | 45.3756 | 8.0075 | 10.6766 | 10.6766 | 16.0149 |  | 54.0378 | 9.5361 | 12.7148 | 12.7148 | 19.0722 |  | 66.4449 | 11.956 | 14.945 | 14.945 | 24.5988 |  | 9500 | 11500 | 11500 | 16500 |  | 54.0378 | 9.5361 | 12.7148 | 12.7148 | 19.0722 |  | 34.6386 | 6.1127 | 8.1502 | 8.1502 | 12.2254
| 36 | 59 |  | TC | 23.05 | 27.74 | 29.78 | 32.52 | 35.47 | 38.02 | 38.62 | 39.82 | 41.7 | 44.3 | 55.02 | 60.81 | 55.2773 | INTERPOLATION | 48.7003 | 36 | 48.7003 |  |  | 9+12+12+24 | 48 | 9 | 12 | 12 | 24 |  |  | 45.3756 | 7.1646 | 9.5527 | 9.5527 | 19.1055 |  | 61.0731 | 10.4631 | 13.0789 | 13.0789 | 24.4522 |  | 48.5 | 8.5 | 10 | 10 | 20 |  | 45.3756 | 7.1646 | 9.5527 | 9.5527 | 19.1055 |  | 54.0378 | 8.5323 | 11.3764 | 11.3764 | 22.7527 |  | 72.1361 | 11.956 | 14.945 | 14.945 | 30.29 |  | 9000 | 10500 | 10500 | 20500 |  | 54.0378 | 8.5323 | 11.3764 | 11.3764 | 22.7527 |  | 34.6386 | 5.4692 | 7.2923 | 7.2923 | 14.5847
| 36 | 64.4 |  | TC | 22.76 | 27.38 | 29.39 | 32.08 | 35.29 | 37.45 | 38.04 | 39.22 | 41.09 | 43.64 | 54.21 | 59.92 | 54.4638 | [6 empty] | 9+12+18+18 | 48 | 9 | 12 | 18 | 18 |  |  | 45.3756 | 7.1646 | 9.5527 | 14.3291 | 14.3291 |  | 63.1842 | 10.4631 | 13.0789 | 19.8211 | 19.8211 |  | 48.5 | 8.5 | 10 | 15 | 15 |  | 45.3756 | 7.1646 | 9.5527 | 14.3291 | 14.3291 |  | 54.0378 | 8.5323 | 11.3764 | 17.0646 | 17.0646 |  | 76.0987 | 11.956 | 14.945 | 24.5988 | 24.5988 |  | 9000 | 10500 | 15500 | 15500 |  | 54.0378 | 8.5323 | 11.3764 | 17.0646 | 17.0646 |  | 34.6386 | 5.4692 | 7.2923 | 10.9385 | 10.9385
| 36 | 69 |  | TC | 22.29 | 26.8 | 28.1 | 30.75 | 35.14 | 36.21 | 36.53 | 38.49 | 41.03 | 44.96 | 48.91 | 52.62 | 49.0749 | EXTRAPOLATION | 49.2273 |  |  |  |  | 9+18+18+18 | 48 | 9 | 18 | 18 | 18 |  |  | 45.3756 | 6.4822 | 12.9644 | 12.9644 | 12.9644 |  | 69.9264 | 10.4631 | 19.8211 | 19.8211 | 19.8211 |  | 50 | 8 | 14 | 14 | 14 |  | 45.3756 | 6.4822 | 12.9644 | 12.9644 | 12.9644 |  | 54.0378 | 7.7197 | 15.4394 | 15.4394 | 15.4394 |  | 85.7525 | 11.956 | 24.5988 | 24.5988 | 24.5988 |  | 8500 | 14500 | 14500 | 14500 |  | 54.0378 | 7.7197 | 15.4394 | 15.4394 | 15.4394 |  | 34.6386 | 4.9484 | 9.8967 | 9.8967 | 9.8967
| 36 | 71.6 |  | TC | 21.9 | 26.32 | 27.6 | 30.2 | 34.52 | 35.48 | 35.8 | 37.72 | 40.2 | 44.06 | 47.94 | 51.56 | 48.1009 | [6 empty] | 12+12+12+12 | 48 | 12 | 12 | 12 | 12 |  |  | 45.3756 | 11.3439 | 11.3439 | 11.3439 | 11.3439 |  | 52.3156 | 13.0789 | 13.0789 | 13.0789 | 13.0789 |  | 48 | 12 | 12 | 12 | 12 |  | 45.3756 | 11.3439 | 11.3439 | 11.3439 | 11.3439 |  | 54.0378 | 13.5094 | 13.5094 | 13.5094 | 13.5094 |  | 59.7801 | 14.945 | 14.945 | 14.945 | 14.945 |  | 12500 | 12500 | 12500 | 12500 |  | 54.0378 | 13.5094 | 13.5094 | 13.5094 | 13.5094 |  | 34.6386 | 8.6596 | 8.6596 | 8.6596 | 8.6596
| 48 | 59 |  | TC | 23.2 | 27.92 | 29.97 | 32.73 | 36.7 | 38.26 | 38.86 | 40.07 | 41.97 | 44.58 | 55.37 | 65.49 | 55.8198 | INTERPOLATION | 54.0378 | 48 | 54.0378 |  |  | 12+12+12+18 | 48 | 12 | 12 | 12 | 18 |  |  | 45.3756 | 10.0835 | 10.0835 | 10.0835 | 15.1252 |  | 59.0578 | 13.0789 | 13.0789 | 13.0789 | 19.8211 |  | 49 | 11 | 11 | 11 | 16 |  | 45.3756 | 10.0835 | 10.0835 | 10.0835 | 15.1252 |  | 54.0378 | 12.0084 | 12.0084 | 12.0084 | 18.0126 |  | 69.4339 | 14.945 | 14.945 | 14.945 | 24.5988 |  | 11500 | 11500 | 11500 | 16500 |  | 54.0378 | 12.0084 | 12.0084 | 12.0084 | 18.0126 |  | 34.6386 | 7.6975 | 7.6975 | 7.6975 | 11.5462
| 48 | 64.4 |  | TC | 22.94 | 27.6 | 29.63 | 32.34 | 36.27 | 37.75 | 38.35 | 39.54 | 41.42 | 43.99 | 54.64 | 64.5 | 55.0782 | [6 empty] | 12+12+12+24 | 48 | 12 | 12 | 12 | 24 |  |  | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 18.1502 |  | 63.6889 | 13.0789 | 13.0789 | 13.0789 | 24.4522 |  | 50 | 10 | 10 | 10 | 20 |  | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 18.1502 |  | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 21.6151 |  | 75.1251 | 14.945 | 14.945 | 14.945 | 30.29 |  | 10500 | 10500 | 10500 | 20500 |  | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 21.6151 |  | 34.6386 | 6.9277 | 6.9277 | 6.9277 | 13.8554
| 48 | 69 |  | TC | 22.58 | 27.15 | 28.47 | 31.15 | 36.13 | 36.68 | 37.01 | 38.99 | 41.56 | 45.55 | 54.03 | 63.62 | 54.4562 | EXTRAPOLATION | 53.9568 |  |  |  |  | 12+12+18+18 | 48 | 12 | 12 | 18 | 18 |  |  | 45.3756 | 9.0751 | 9.0751 | 13.6127 | 13.6127 |  | 65.8 | 13.0789 | 13.0789 | 19.8211 | 19.8211 |  | 50 | 10 | 10 | 15 | 15 |  | 45.3756 | 9.0751 | 9.0751 | 13.6127 | 13.6127 |  | 54.0378 | 10.8076 | 10.8076 | 16.2113 | 16.2113 |  | 79.0877 | 14.945 | 14.945 | 24.5988 | 24.5988 |  | 10500 | 10500 | 15500 | 15500 |  | 54.0378 | 10.8076 | 10.8076 | 16.2113 | 16.2113 |  | 34.6386 | 6.9277 | 6.9277 | 10.3916 | 10.3916
| 48 | 71.6 |  | TC | 22.14 | 26.61 | 27.91 | 30.53 | 35.09 | 35.87 | 36.19 | 38.13 | 40.64 | 44.55 | 52.95 | 62.36 | 53.3682 | [6 empty] | 9+9+9+9+9 | 48 | 9 | 9 | 9 | 9 | 9 | 5 | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 52.3156 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 45 | 9 | 9 | 9 | 9 | 9 | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 59.7801 | 11.956 | 11.956 | 11.956 | 11.956 | 11.956 | 9500 | 9500 | 9500 | 9500 | 9500 | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 34.6386 | 6.9277 | 6.9277 | 6.9277 | 6.9277 | 6.9277
| 18 | 59 |  | Input | 1.65 | 1.69 | 1.81 | 1.83 | 1.98 | 1.87 | 1.88 | 1.93 | 1.65 | 1.76 | 2.02 | 1.86 | [7 empty] | 9+9+9+9+12 | 48 | 9 | 9 | 9 | 9 | 12 |  | 45.3756 | 8.5079 | 8.5079 | 8.5079 | 8.5079 | 11.3439 | 54.9313 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 48 | 9 | 9 | 9 | 9 | 12 | 45.3756 | 8.5079 | 8.5079 | 8.5079 | 8.5079 | 11.3439 | 54.0378 | 10.1321 | 10.1321 | 10.1321 | 10.1321 | 13.5094 | 62.7691 | 11.956 | 11.956 | 11.956 | 11.956 | 14.945 | 9500 | 9500 | 9500 | 9500 | 13000 | 54.0378 | 10.1321 | 10.1321 | 10.1321 | 10.1321 | 13.5094 | 34.6386 | 6.4947 | 6.4947 | 6.4947 | 6.4947 | 8.6596
| 18 | 64.4 |  | Input | 1.68 | 1.72 | 1.84 | 1.86 | 2.02 | 1.9 | 1.91 | 1.96 | 1.68 | 1.79 | 2.05 | 1.89 | [7 empty] | 9+9+9+9+18 | 48 | 9 | 9 | 9 | 9 | 18 |  | 45.3756 | 7.5626 | 7.5626 | 7.5626 | 7.5626 | 15.1252 | 61.6736 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 19.8211 | 50 | 8.5 | 8.5 | 8.5 | 8.5 | 16 | 45.3756 | 7.5626 | 7.5626 | 7.5626 | 7.5626 | 15.1252 | 54.0378 | 9.0063 | 9.0063 | 9.0063 | 9.0063 | 18.0126 | 72.4229 | 11.956 | 11.956 | 11.956 | 11.956 | 24.5988 | 9000 | 9000 | 9000 | 9000 | 16500 | 54.0378 | 9.0063 | 9.0063 | 9.0063 | 9.0063 | 18.0126 | 34.6386 | 5.7731 | 5.7731 | 5.7731 | 5.7731 | 11.5462
| 18 | 69 |  | Input | 1.46 | 1.49 | 1.54 | 1.55 | 2.01 | 1.68 | 1.71 | 1.88 | 1.86 | 1.94 | 2 | 1.59 | [7 empty] | 9+9+9+9+24 | 48 | 9 | 9 | 9 | 9 | 24 |  | 45.3756 | 6.8063 | 6.8063 | 6.8063 | 6.8063 | 18.1502 | 66.3047 | 10.4631 | 10.4631 | 10.4631 | 10.4631 | 24.4522 | 52 | 8 | 8 | 8 | 8 | 20 | 45.3756 | 6.8063 | 6.8063 | 6.8063 | 6.8063 | 18.1502 | 54.0378 | 8.1057 | 8.1057 | 8.1057 | 8.1057 | 21.6151 | 78.1141 | 11.956 | 11.956 | 11.956 | 11.956 | 30.29 | 8500 | 8500 | 8500 | 8500 | 20500 | 54.0378 | 8.1057 | 8.1057 | 8.1057 | 8.1057 | 21.6151 | 34.6386 | 5.1958 | 5.1958 | 5.1958 | 5.1958 | 13.8554
| 18 | 71.6 |  | Input | 1.49 | 1.52 | 1.57 | 1.58 | 2.05 | 1.71 | 1.74 | 1.91 | 1.89 | 1.97 | 2.03 | 1.62 | [7 empty] | 9+9+9+12+12 | 48 | 9 | 9 | 9 | 12 | 12 |  | 45.3756 | 8.0075 | 8.0075 | 8.0075 | 10.6766 | 10.6766 | 57.5471 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 49 | 9 | 9 | 9 | 11 | 11 | 45.3756 | 8.0075 | 8.0075 | 8.0075 | 10.6766 | 10.6766 | 54.0378 | 9.5361 | 9.5361 | 9.5361 | 12.7148 | 12.7148 | 65.7581 | 11.956 | 11.956 | 11.956 | 14.945 | 14.945 | 9000 | 9000 | 9000 | 12000 | 12000 | 54.0378 | 9.5361 | 9.5361 | 9.5361 | 12.7148 | 12.7148 | 34.6386 | 6.1127 | 6.1127 | 6.1127 | 8.1502 | 8.1502
| 24 | 59 |  | Input | 2.97 | 3.24 | 3.28 | 3.5 | 3.62 | 2.7 | 2.83 | 2.91 | 2.69 | 2.82 | 3 | 2.75 | [7 empty] | 9+9+9+12+18 | 48 | 9 | 9 | 9 | 12 | 18 |  | 45.3756 | 7.1646 | 7.1646 | 7.1646 | 9.5527 | 14.3291 | 64.2893 | 10.4631 | 10.4631 | 10.4631 | 13.0789 | 19.8211 | 51 | 8 | 8 | 8 | 11 | 16 | 45.3756 | 7.1646 | 7.1646 | 7.1646 | 9.5527 | 14.3291 | 54.0378 | 8.5323 | 8.5323 | 8.5323 | 11.3764 | 17.0646 | 75.4119 | 11.956 | 11.956 | 11.956 | 14.945 | 24.5988 | 8500 | 8500 | 8500 | 11500 | 17000 | 54.0378 | 8.5323 | 8.5323 | 8.5323 | 11.3764 | 17.0646 | 34.6386 | 5.4692 | 5.4692 | 5.4692 | 7.2923 | 10.9385
| 24 | 64.4 |  | Input | 3.05 | 3.32 | 3.36 | 3.59 | 3.71 | 2.77 | 2.9 | 2.98 | 2.76 | 2.93 | 3.03 | 2.78 | [7 empty] | 9+9+9+18+18 | 48 | 9 | 9 | 9 | 18 | 18 |  | 45.3756 | 6.4822 | 6.4822 | 6.4822 | 12.9644 | 12.9644 | 71.0316 | 10.4631 | 10.4631 | 10.4631 | 19.8211 | 19.8211 | 52.5 | 7.5 | 7.5 | 7.5 | 15 | 15 | 45.3756 | 6.4822 | 6.4822 | 6.4822 | 12.9644 | 12.9644 | 54.0378 | 7.7197 | 7.7197 | 7.7197 | 15.4394 | 15.4394 | 85.0657 | 11.956 | 11.956 | 11.956 | 24.5988 | 24.5988 | 8000 | 8000 | 8000 | 15500 | 15500 | 54.0378 | 7.7197 | 7.7197 | 7.7197 | 15.4394 | 15.4394 | 34.6386 | 4.9484 | 4.9484 | 4.9484 | 9.8967 | 9.8967
| 24 | 69 |  | Input | 3.11 | 3.39 | 3.43 | 3.67 | 3.79 | 2.83 | 2.97 | 3.05 | 2.82 | 3 | 3.09 | 3.22 | [7 empty] | 9+9+12+12+12 | 48 | 9 | 9 | 12 | 12 | 12 |  | 45.3756 | 7.5626 | 7.5626 | 10.0835 | 10.0835 | 10.0835 | 60.1629 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 50 | 8.5 | 8.5 | 11 | 11 | 11 | 45.3756 | 7.5626 | 7.5626 | 10.0835 | 10.0835 | 10.0835 | 54.0378 | 9.0063 | 9.0063 | 12.0084 | 12.0084 | 12.0084 | 68.7471 | 11.956 | 11.956 | 14.945 | 14.945 | 14.945 | 9000 | 9000 | 12000 | 12000 | 12000 | 54.0378 | 9.0063 | 9.0063 | 12.0084 | 12.0084 | 12.0084 | 34.6386 | 5.7731 | 5.7731 | 7.6975 | 7.6975 | 7.6975
| 24 | 71.6 |  | Input | 3.19 | 3.47 | 3.51 | 3.75 | 3.88 | 2.89 | 3.03 | 3.12 | 2.88 | 3.06 | 3.12 | 3.25 | [7 empty] | 9+9+12+12+18 | 48 | 9 | 9 | 12 | 12 | 18 |  | 45.3756 | 6.8063 | 6.8063 | 9.0751 | 9.0751 | 13.6127 | 66.9051 | 10.4631 | 10.4631 | 13.0789 | 13.0789 | 19.8211 | 52 | 8.5 | 8.5 | 10 | 10 | 15 | 45.3756 | 6.8063 | 6.8063 | 9.0751 | 9.0751 | 13.6127 | 54.0378 | 8.1057 | 8.1057 | 10.8076 | 10.8076 | 16.2113 | 78.4009 | 11.956 | 11.956 | 14.945 | 14.945 | 24.5988 | 8500 | 8500 | 11000 | 11000 | 16000 | 54.0378 | 8.1057 | 8.1057 | 10.8076 | 10.8076 | 16.2113 | 34.6386 | 5.1958 | 5.1958 | 6.9277 | 6.9277 | 10.3916
| 30 | 59 |  | Input | 3.44 | 3.51 | 3.5 | 3.67 | 3.68 | 3.77 | 3.79 | 3.85 | 3.13 | 3.17 | 3.32 | 3.42 | [7 empty] | 9+12+12+12+12 | 48 | 9 | 12 | 12 | 12 | 12 |  | 45.3756 | 7.1646 | 9.5527 | 9.5527 | 9.5527 | 9.5527 | 62.7787 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 50 | 8 | 10.5 | 10.5 | 10.5 | 10.5 | 45.3756 | 7.1646 | 9.5527 | 9.5527 | 9.5527 | 9.5527 | 54.0378 | 8.5323 | 11.3764 | 11.3764 | 11.3764 | 11.3764 | 71.7361 | 11.956 | 14.945 | 14.945 | 14.945 | 14.945 | 8500 | 11000 | 11000 | 11000 | 11000 | 54.0378 | 8.5323 | 11.3764 | 11.3764 | 11.3764 | 11.3764 | 34.6386 | 5.4692 | 7.2923 | 7.2923 | 7.2923 | 7.2923
| 30 | 64.4 |  | Input | 3.47 | 3.54 | 3.58 | 3.81 | 3.82 | 3.9 | 3.92 | 3.98 | 3.16 | 3.2 | 3.35 | 3.45 | [7 empty] | 9+12+12+12+18 | 48 | 9 | 12 | 12 | 12 | 18 |  | 45.3756 | 6.4822 | 8.643 | 8.643 | 8.643 | 12.9644 | 69.5209 | 10.4631 | 13.0789 | 13.0789 | 13.0789 | 19.8211 | 52.5 | 7.5 | 10 | 10 | 10 | 15 | 45.3756 | 6.4822 | 8.643 | 8.643 | 8.643 | 12.9644 | 54.0378 | 7.7197 | 10.2929 | 10.2929 | 10.2929 | 15.4394 | 81.3899 | 11.956 | 14.945 | 14.945 | 14.945 | 24.5988 | 8000 | 10500 | 10500 | 10500 | 15500 | 54.0378 | 7.7197 | 10.2929 | 10.2929 | 10.2929 | 15.4394 | 34.6386 | 4.9484 | 6.5978 | 6.5978 | 6.5978 | 9.8967
| 30 | 69 |  | Input | 3.56 | 3.63 | 3.69 | 3.82 | 3.84 | 3.91 | 3.96 | 4.1 | 3.19 | 3.23 | 3.26 | 3.35 | [7 empty] | 12+12+12+12+12 | 48 | 12 | 12 | 12 | 12 | 12 |  | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 65.3944 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 13.0789 | 52.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 45.3756 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 9.0751 | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 74.7251 | 14.945 | 14.945 | 14.945 | 14.945 | 14.945 | 11000 | 11000 | 11000 | 11000 | 11000 | 54.0378 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 10.8076 | 34.6386 | 6.9277 | 6.9277 | 6.9277 | 6.9277 | 6.9277
| 30 | 71.6 |  | Input | 3.69 | 3.66 | 3.83 | 3.85 | 3.87 | 3.94 | 3.99 | 4.13 | 3.22 | 3.26 | 3.29 | 3.38
| 36 | 59 |  | Input | 4.98 | 5.1 | 5.25 | 5.28 | 5.31 | 5.19 | 5.21 | 5.29 | 4.63 | 4.8 | 4.97 | 4.63
| 36 | 64.4 |  | Input | 5.04 | 5.16 | 5.31 | 5.34 | 5.37 | 5.25 | 5.27 | 5.35 | 4.69 | 4.86 | 5.03 | 4.69
| 36 | 69 |  | Input | 5.12 | 5.23 | 5.32 | 5.35 | 5.37 | 5.33 | 5.35 | 5.43 | 4.69 | 5.03 | 4.73 | 4.36
| 36 | 71.6 |  | Input | 5.17 | 5.28 | 5.37 | 5.4 | 5.42 | 5.38 | 5.4 | 5.48 | 4.74 | 5.09 | 4.78 | 4.42
| 48 | 59 |  | Input | 5.03 | 5.15 | 5.3 | 5.33 | 5.36 | 5.24 | 5.26 | 5.34 | 4.67 | 4.85 | 5.02 | 4.67
| 48 | 64.4 |  | Input | 5.15 | 5.26 | 5.41 | 5.45 | 5.48 | 5.35 | 5.37 | 5.46 | 4.78 | 4.96 | 5.14 | 4.78
| 48 | 69 |  | Input | 5.18 | 5.29 | 5.38 | 5.41 | 5.5 | 5.39 | 5.41 | 5.5 | 4.75 | 4.7 | 4.78 | 5.12
| 48 | 71.6 |  | Input | 5.23 | 5.34 | 5.43 | 5.46 | 5.52 | 5.44 | 5.46 | 5.55 | 4.8 | 5.15 | 4.83 | 5.17
| 18 | 59 |  | COP | 1.29 | 1.57 | 1.81 | 2.01 | 2.18 | 2.65 | 2.67 | 2.68 | 3.26 | 3.28 | 3.44 | 3.96
| 18 | 64.4 |  | COP | 1.24 | 1.52 | 1.75 | 1.95 | 2.11 | 2.57 | 2.59 | 2.6 | 3.15 | 3.17 | 3.33 | 3.84
| 18 | 69 |  | COP | 1.07 | 1.21 | 1.34 | 1.54 | 2.1 | 2.34 | 2.31 | 2.58 | 2.81 | 2.73 | 3.02 | 3.7
| 18 | 71.6 |  | COP | 1.03 | 1.17 | 1.29 | 1.49 | 1.94 | 2.26 | 2.24 | 2.51 | 2.73 | 2.65 | 2.93 | 3.58
| 24 | 59 |  | COP | 1.38 | 1.6 | 1.79 | 1.88 | 1.93 | 2.75 | 2.66 | 2.81 | 3.27 | 3.31 | 3.56 | 4.3
| 24 | 64.4 |  | COP | 1.33 | 1.55 | 1.72 | 1.81 | 1.86 | 2.65 | 2.57 | 2.71 | 3.16 | 3.15 | 3.47 | 4.19
| 24 | 69 |  | COP | 1.29 | 1.5 | 1.67 | 1.76 | 1.81 | 2.57 | 2.49 | 2.63 | 3.07 | 3.01 | 3.4 | 3.66
| 24 | 71.6 |  | COP | 1.25 | 1.46 | 1.63 | 1.71 | 1.76 | 2.5 | 2.42 | 2.56 | 2.99 | 2.92 | 3.31 | 3.57
| 30 | 59 |  | COP | 1.57 | 1.86 | 2.03 | 2.11 | 2.23 | 2.44 | 2.45 | 2.52 | 3.25 | 3.39 | 3.35 | 3.54
| 30 | 64.4 |  | COP | 1.54 | 1.82 | 1.95 | 2.01 | 2.12 | 2.33 | 2.33 | 2.4 | 3.18 | 3.31 | 3.27 | 3.46
| 30 | 69 |  | COP | 1.36 | 1.64 | 1.73 | 1.82 | 1.98 | 2.05 | 2.06 | 2.25 | 3.08 | 3.24 | 3.31 | 3.48
| 30 | 71.6 |  | COP | 1.22 | 1.53 | 1.65 | 1.79 | 1.95 | 2 | 2.01 | 2.2 | 3.01 | 3.16 | 3.23 | 3.4
| 36 | 59 |  | COP | 1.36 | 1.6 | 1.66 | 1.81 | 1.96 | 2.15 | 2.17 | 2.21 | 2.64 | 2.7 | 3.24 | 3.85
| 36 | 64.4 |  | COP | 1.32 | 1.56 | 1.62 | 1.76 | 1.93 | 2.09 | 2.12 | 2.15 | 2.57 | 2.63 | 3.16 | 3.74
| 36 | 69 |  | COP | 1.28 | 1.5 | 1.55 | 1.68 | 1.92 | 1.99 | 2 | 2.08 | 2.56 | 2.62 | 3.03 | 3.53
| 36 | 71.6 |  | COP | 1.24 | 1.46 | 1.51 | 1.64 | 1.87 | 1.93 | 1.94 | 2.02 | 2.49 | 2.54 | 2.94 | 3.42
| 48 | 59 |  | COP | 1.35 | 1.59 | 1.66 | 1.8 | 0.30092 | 2.14 | 2.17 | 2.2 | 2.63 | 2.69 | 3.23 | 4.11
| 48 | 64.4 |  | COP | 1.31 | 1.54 | 1.6 | 1.74 | 1.94 | 2.07 | 2.09 | 2.12 | 2.54 | 2.6 | 3.12 | 3.95
| 48 | 69 |  | COP | 1.28 | 1.5 | 1.55 | 1.69 | 1.93 | 1.99 | 2 | 2.08 | 2.57 | 2.84 | 3.31 | 3.65
| 48 | 71.6 |  | COP | 1.24 | 1.46 | 1.51 | 1.64 | 0.2946 | 1.93 | 1.94 | 2.01 | 2.48 | 2.54 | 3.21 | 3.54
LEGEND
DB - Dry Bulb
WB - Wet Bulb
TC - Total Net Capacity (1000 Btu/hour)
Input - Total Power (kW)
COP - W/W

## Cap based on indoor unit SZ (hidden)
Perfomances based on the 40MAQ high wall with the 38MA*R at 95F for Cooling and 47F for Heating. The size 9 has been reduced 20% from the size 12 for calculation purposes. Other types of indoor units would have a similar capacity at this temperatures, therefore these caps would apply to all the indoor unit types
High wall 40MAQ
| Model | Cooling |  |  | Outdoor conditions (DB)
|  | Indoor Conditions DB |  |  | 95F (35C)
|  | DB | WB |  |  |  | INTERPOLATION OR EXTRAPOLATION | SIZE | SELECTION OF INTERPOLATION OR EXTRAPOLATION
| 9 | 69.8 | 59 | TC | 9.256 |  | 10.4631 | 9 | 10.4631
| 9 | 75.2 | 62.6 | TC | 9.624
| 9 | 80.6 | 66.2 | TC | 10.568 |  | 10.2409
| 9 | 89.6 | 73.4 | TC | 11.056
| 12 | 69.8 | 59 | TC | 11.57 |  | 13.0789 | 12 | 13.0789
| 12 | 75.2 | 62.6 | TC | 12.03
| 12 | 80.6 | 66.2 | TC | 13.21 |  | 12.8011
| 12 | 89.6 | 73.4 | TC | 13.82
| 18 | 69.8 | 59 | TC | 17.46 |  | 19.8211 | 18 | 19.8211
| 18 | 75.2 | 62.6 | TC | 18.71
| 18 | 80.6 | 66.2 | TC | 19.96 |  | 19.2392
| 18 | 89.6 | 73.4 | TC | 20.17
| 24 | 69.8 | 59 | TC | 25.86 |  | 24.4522 | 24 | 24.4522
| 24 | 75.2 | 62.6 | TC | 28.07
| 24 | 80.6 | 66.2 | TC | 24 |  | 26.0518
| 24 | 89.6 | 73.4 | TC | 26.4
| 9 | 69.8 | 59 | SC | 7.8676 |  | 9.619 | 9 | 9.619
| 9 | 75.2 | 62.6 | SC | 8.1804
| 9 | 80.6 | 66.2 | SC | 9.7988 |  | 9.1472
| 9 | 89.6 | 73.4 | SC | 10.1388
| 12 | 69.8 | 59 | SC | 9.8345 |  | 12.0237 | 12 | 12.0237
| 12 | 75.2 | 62.6 | SC | 10.2255
| 12 | 80.6 | 66.2 | SC | 12.2485 |  | 11.434
| 12 | 89.6 | 73.4 | SC | 12.6735
| 18 | 69.8 | 59 | SC | 15.3648 |  | 17.62 | 18 | 17.62
| 18 | 75.2 | 62.6 | SC | 16.4648
| 18 | 80.6 | 66.2 | SC | 17.7644 |  | 17.0451
| 18 | 89.6 | 73.4 | SC | 17.9513
| 24 | 69.8 | 59 | SC | 19.395 |  | 17.7322 | 24 | 17.7322
| 24 | 75.2 | 62.6 | SC | 15.59
| 24 | 80.6 | 66.2 | SC | 18 |  | 18.2836
| 24 | 89.6 | 73.4 | SC | 19.8
| Model | Heating | [14 empty] | Outdoor conditions (DB)
|  | Indoor Conditions DB |  |  | -22 | -13 | -4 | 0 | 5 | 17 | 19.4 | 24.8 | 32 | 39.2 | 44.6 | 53.6 | 47
[18 empty] | INTERPOLATION OR EXTRAPOLATION | SIZE | SELECTION OF INTERPOLATION OR EXTRAPOLATION
| 9 | 59 |  | TC | 6.01 | 9.22 | 10.02 | 11.2 | 12.37 | 15.03 | 15.26 | 15.52 | 14.21 | 15.29 | 15.82 | 17.32 | 12.976 | 11.956 | 9 | 11.956
| 9 | 64.4 |  | TC | 5.41 | 9.12 | 9.82 | 11.02 | 12.19 | 14.305 | 14.755 | 14.89 | 14.11 | 14.925 | 15.4 | 16.445 | 12.5429
| 9 | 69 |  | TC | 5.31 | 9.02 | 9.65 | 10.85 | 12.01 | 13.58 | 14.25 | 14.26 | 14.01 | 14.56 | 14.98 | 15.57 | 12.1099 | 11.9432
| 9 | 71.6 |  | TC | 5.22 | 8.88 | 9.42 | 10.65 | 11.51 | 13.08 | 13.75 | 13.76 | 13.51 | 14.06 | 14.48 | 15.07 | 11.7099
| 12 | 59 |  | TC | 6.01 | 9.22 | 10.2 | 11.02 | 12.37 | 15.03 | 15.26 | 15.52 | 14.21 | 15.29 | 15.82 | 17.32 | 16.22 | 14.945 | 12 | 14.945
| 12 | 64.4 |  | TC | 5.41 | 9.12 | 10.02 | 10.98 | 12.19 | 14.305 | 14.755 | 14.89 | 14.11 | 14.925 | 15.4 | 16.445 | 15.6787
| 12 | 69 |  | TC | 5.31 | 9.02 | 9.82 | 11.81 | 12.01 | 13.58 | 14.25 | 14.26 | 14.01 | 14.56 | 14.98 | 15.57 | 15.1373 | 14.929
| 12 | 71.6 |  | TC | 5.22 | 8.88 | 9.62 | 11.74 | 12 | 13.08 | 13.75 | 13.76 | 13.51 | 14.06 | 14.48 | 15.07 | 14.6373
| 18 | 59 |  | TC | 11.99 | 16.82 | 17.26 | 18.02 | 18.82 | 23.32 | 23.55 | 23.71 | 23.91 | 24.14 | 24.32 | 26.88 | 25.0027 | 24.5988 | 18 | 24.5988
| 18 | 64.4 |  | TC | 12.12 | 16.67 | 17.11 | 17.98 | 18.67 | 23.17 | 23.4 | 23.56 | 23.76 | 23.99 | 24.17 | 26.73 | 24.8527
| 18 | 69 |  | TC | 12.42 | 16.52 | 17.01 | 18.01 | 18.52 | 23.02 | 23.25 | 23.41 | 23.61 | 23.84 | 24.02 | 26.58 | 24.7027 | 24.58
| 18 | 71.6 |  | TC | 11.19 | 16.25 | 16.87 | 17.98 | 18.25 | 22.75 | 22.98 | 23.14 | 23.34 | 23.57 | 23.75 | 26.31 | 24.4327
| 24 | 59 |  | TC | 15.2 | 16.66 | 22.54 | 24.56 | 25.24 | 26.02 | 26.85 | 27.56 | 27.87 | 28.89 | 29.79 | 31.92 | 30.358 | 30.29 | 24 | 30.29
| 24 | 64.4 |  | TC | 15.13 | 16.59 | 22.32 | 24.32 | 24.1 | 25.783 | 26.05 | 26.59 | 27.58 | 28.51 | 29.75 | 31.85 | 30.31
| 24 | 69 |  | TC | 15.05 | 16.52 | 21.02 | 24 | 24.03 | 25.713 | 25.98 | 26.52 | 27.51 | 28.44 | 29.68 | 31.78 | 30.24 | 30.3104
| 24 | 71.6 |  | TC | 13.46 | 16.65 | 20.05 | 24.02 | 24.16 | 25.843 | 26.11 | 26.65 | 27.64 | 28.57 | 29.81 | 31.91 | 30.37

## Altitude Correction (hidden)
High altitude correction factor |  |  |  | file:///\\cusiif05.carrier.utc.com\Secured\Marketing\DLS-VRF\Software\Carrier%20TCB%20Software%20Issues\Old-DNU\855%20MGR%20Caps%20Cosolidated\855%20MGR%20Caps%2011-6-18update\Altitude%20function%20of%20ST.pptx
Altitude |  | Toshiba
meter | feet | Indoor | Outdoor
0 | 0 | 1 | 1
305 | 1000 | 0.99 | 0.99
610 | 2000 | 0.98 | 0.98
914 | 3000 | 0.97 | 0.98
1219 | 4000 | 0.96 | 0.97
1524 | 5000 | 0.95 | 0.96
1829 | 6000 | 0.94 | 0.95
2134 | 7000 | 0.92 | 0.94
2438 | 8000 | 0.9 | 0.94
2743 | 9000 | 0.86 | 0.93
3048 | 10000 | 0.82 | 0.92
Capacity correction (Indoor) = Indoor capacity X correction factor
Capacity correction (Outdoor) = Outdoor capacity X correction factor
Altitude De-rate Table
Altitude(feet) | Indoor | Outdoor | Total
0 | 1 | 1 | 1
1000 | 0.99 | 0.99 | 0.9801
2000 | 0.98 | 0.98 | 0.9604
3000 | 0.97 | 0.98 | 0.9506
4000 | 0.96 | 0.97 | 0.9312
5000 | 0.95 | 0.96 | 0.912
6000 | 0.94 | 0.95 | 0.893
7000 | 0.92 | 0.94 | 0.8648
8000 | 0.9 | 0.94 | 0.846
9000 | 0.86 | 0.93 | 0.7998
10000 | 0.82 | 0.92 | 0.7544

## Piping Correction (hidden)
NOTE
Light commercial
| Capacity | Max.Length(m) | Max.Height(m)
| 12K | 25 | 10
| 18K | 30 | 20
| 24K | 50 | 25
| 30K | 50 | 25
| 36K | 65 | 30
| 42K | 65 | 30
| 48K | 65 | 30
| 55K/60K | 65 | 30
Piping Length Derate Tables
| Minimum Length | Maximum Length | Cooling Derate | Heating Derate
| 0 | 16.4 | 1 | 1
| 16.4 | 49.2 | 0.972 | 0.987
| 49.2 | 82 | 0.945 | 0.975
| 82 | 114.8 | 0.917 | 0.962
| 114.8 | 164.1 | 0.876 | 0.943
| 164.1 | 328 | 0.876 | 0.943
[10 empty] | Piping to furthest FCU | 45
Size
| 12 | Feet | 9.8424 | 16.404 | 32.808 | 65.616 | 82.02
| 12 | Meters | 3 | 5 | 10 | 20 | 25
| 12 | Cooling | 1 | 1 | 0.9875 | 0.9625 | 0.95
| 12 | Heating | 1 | 1 | 0.9925 | 0.9775 | 0.97
| 18 | Feet | 9.8424 | 16.404 | 32.808 | 65.616 | 98.424
| 18 | Meters | 3 | 5 | 10 | 20 | 30
| 18 | Cooling | 1 | 1 | 0.98375 | 0.95125 | 0.935
| 18 | Heating | 1 | 1 | 0.994 | 0.982 | 0.976
| 24 | Feet | 9.8424 | 16.404 | 32.808 | 65.616 | 98.424 | 131.232 | 164.04
| 24 | Meters | 3 | 5 | 10 | 20 | 30 | 40 | 50
| 24 | Cooling | 1 | 1 | 0.98944 | 0.96833 | 0.94722 | 0.92611 | 0.905
| 24 | Heating | 1 | 1 | 0.99667 | 0.99 | 0.98333 | 0.97667 | 0.97
| 36 | Feet | 9.8424 | 16.404 | 49.212 | 82.02 | 114.828 | 164.04 | 213.252
| 36 | Meters | 3 | 5 | 15 | 25 | 35 | 50 | 65
| 36 | Cooling | 1 | 1 | 0.97233 | 0.94467 | 0.917 | 0.8755 | 0.834 |  | 0.97589
| 36 | Heating | 1 | 1 | 0.98733 | 0.97467 | 0.962 | 0.943 | 0.924 |  | 0.98896
| 42 | Feet | 9.8424 | 16.404 | 49.212 | 82.02 | 114.828 | 164.04 | 213.252
| 42 | Meters | 3 | 5 | 15 | 25 | 35 | 50 | 65
| 42 | Cooling | 1 | 1 | 0.971 | 0.942 | 0.913 | 0.8695 | 0.826
| 42 | Heating | 1 | 1 | 0.98667 | 0.97333 | 0.96 | 0.94 | 0.92
| 48 | Feet | 9.8424 | 16.404 | 49.212 | 82.02 | 114.828 | 164.04 | 213.252
| 48 | Meters | 3 | 5 | 15 | 25 | 35 | 50 | 65
| 48 | Cooling | 1 | 1 | 0.97067 | 0.94133 | 0.912 | 0.868 | 0.824
| 48 | Heating | 1 | 1 | 0.98517 | 0.97033 | 0.9555 | 0.93325 | 0.911
Note on A1: Matthew Morris: Please just derate based on piping length only, not height. But please also capture these maximum lengths. Also, please capture/cap max heights in adjacent tab.