## 38MURA-01SB
Outdoor Unit Single Zone Heat Pump System
38MURAQ
Job Data: |  |  | Location: |  |  |  | Carrier #:
Tag #: | [6 empty] | Date:
[5 empty] | Outdoor Model # |  | Size |  | STANDARD FEATURES • Variable Speed (Inverter) • Factory installed Base Pan Heater • Factory installed Crankcase Heater • Low Voltage Controls • 24V Interface Pre-Installed • Traditional Unitary Line Set Sizes • Standard Heat and High Heat Options • Auto-Restart function • Condenser High Temp Protection • Quiet operation • Anti-corrosive fin coating LIMITED WARRANTY* • 10 year limited to original purchaser on compressor and parts upon timely registration, otherwise 5 years *For residential applications. See warranty for full details.
[5 empty] | 38MURAQ18AA3 |  | 1.5T
[5 empty] | 38MURAQ18AB3 |  | 1.5T - HH
[5 empty] | 38MURAQ24AA3 |  | 2T
[5 empty] | 38MURAQ24AB3 |  | 2T - HH
[5 empty] | 38MURAQ30AA3 |  | 2.5T
[5 empty] | 38MURAQ30AB3 |  | 2.5T - HH
[5 empty] | 38MURAQ36AA3 |  | 3T
[5 empty] | 38MURAQ36AB3 |  | 3T - HH
[5 empty] | 38MURAQ48AA3 |  | 4T
[5 empty] | 38MURAQ48AB3 |  | 4T - HH
[5 empty] | 38MURAQ60AA3 |  | 5T
[5 empty] | 38MURAQ60AB3 -Coming Soon |  | 5T - HH
Combination Selection
| NOTE: Images for illustration purposes only. Actual models may be slightly different. |  |  |  | Outdoor Unit | 2.5T
[5 empty] | Indoor Category | Air Handler
Specifications
Outdoor - Heat Pump (Standard Heat)
System | Outdoor Size |  | 1.5T | 2T | 2.5T | 3T | 4T | 5T
Electrical | Voltage, Phase, Cycle | V/Ph/Hz | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60
| MCA | A. | 16 | 19 | 20 | 24 | 34 | 34
| Recommended Fuse Size | A. | 20 | 20 | 25 | 25 | 35 | 35
| MOPA - Fuse Rating | A. | 20 | 30 | 35 | 40 | 50 | 60
| Short Circuit Current Rating (SCCR) | kA | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Operating Range | Cooling Outdoor DB Min - Max | °F(°C) | 5~130 (-15~55) | 5~130 (-15~55) | 5~130 (-15~55) | 5~130 (-15~55) | 5~130 (-15~55) | 5~130 (-15~55)
| Heating Outdoor DB Min - Max | °F(°C) | -5~86 (-15~30) | -5~86 (-15~30) | -5~86 (-15~30) | -5~86 (-15~30) | -5~86 (-15~30) | -5~86 (-15~30)
Piping | Total Piping Length | ft (m) | 98 (30) | 164 (50) | 164 (50) | 213 (65) | 213 (65) | 213 (65)
| Piping Lift* | ft (m) | 65 (20) | 82 (25) | 82 (25) | 98 (30) | 98 (30) | 98 (30)
| Pipe Connection Size - Liquid | in (mm) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52)
| Pipe Connection Size - Suction | in (mm) | 3/4 (19) | 3/4 (19) | 3/4 (19) | 3/4 (19) | 3/4 (19) | 7/8 (22)
Refrigerant | Refrigerant Type |  | R410A | R410A | R410A | R410A | R410A | R410A
| Charge | lbs (kg) | 3.53 (1.6) | 4.63 (2.1) | 6.72 (3.05) | 8.16 (3.7) | 10.4 (4.7) | 10.8 (4.9)
| Add'l Refrigerant (between Std & Max Piping Lngths) | Oz/ft (g/m) | 0.69 (65) | 0.69 (65) | 0.69 (65) | 0.69 (65) | 0.69 (65) | 0.69 (65)
| Metering Device |  | EEV | EEV | EEV | EEV | EEV | EEV
Outdoor Coil | Face Area | Sq. Ft. | 5 | 5.9 | 8.18 | 8.14 | 13.53 | 13.36
| No. Rows |  | 2 | 2 | 2.6 | 3 | 2 | 3
| Fins per inch |  | 20 | 20 | 18 | 18 | 18 | 18
| Circuits |  | 4 | 6 | 6 | 6 | 8 | 14
Compressor | Type |  | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter
| Model |  | KSN140D21UFZ | KTM240D57UMT | KTF250D22UMT | KTF250D22UMT | KTQ420D1UMU | KTQ420D1UMU
| Oil Type |  | VG74 | VG74 | VG74 | VG74 | VG74 | VG74
| Oil Charge | Fl. Oz. | 14.9 | 22.7 | 22.7 | 22.7 | 47.3 | 47.3
| Rated Current | RLA | 9 | 14 | 16 | 17.6 | 24 | 24.6
Airflow & Sound | Airflow | CFM | 1450 | 1765 | 3000 | 2235 | 4500 | 4412
| Sound Pressure | dB(A) | 54 | 60 | 62 | 61 | 59 | 61
* Condensing unit above or below indoor unit
Outdoor - Heat Pump (High Heat)
System | Outdoor Size |  | 1.5T - HH | 2T - HH | 2.5T - HH | 3T - HH | 4T - HH | 5T - HH
Electrical | Voltage, Phase, Cycle | V/Ph/Hz | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60 | 208/230-1-60
| MCA | A. | 16 | 20.5 | 23 | 41 | 42
| Recommended Fuse Size | A. | 20 | 25 | 25 | 45 | 45
| MOCP - Fuse Rating | A. | 20 | 35 | 35 | 50 | 50
| Short Circuit Current Rating (SCCR) | kA | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Operating Range | Cooling Outdoor DB Min - Max | °F(°C) | -22~130 (-30~55) | -22~130 (-30~55) | -22~130 (-30~55) | -22~130 (-30~55) | -22~130 (-30~55) | -22~130 (-30~55)
| Heating Outdoor DB Min - Max | °F(°C) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30) | -22~86 (-30~30)
Piping | Total Piping Length | ft (m) | 98 (30) | 164 (50) | 164 (50) | 213 (65) | 213 (65)
| Piping Lift* | ft (m) | 65 (20) | 82 (25) | 82 (25) | 98 (30) | 98 (30)
| Pipe Connection Size - Liquid | in (mm) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52) | 3/8 (9.52)
| Pipe Connection Size - Suction | in (mm) | 3/4 (19) | 3/4 (19) | 3/4 (19) | 3/4 (19) | 3/4 (19)
Refrigerant | Refrigerant Type |  | R410A | R410A | R410A | R410A | R410A
| Charge | lbs (kg) | 5.07 (2.3) | 6.39 (2.9) | 8.38 (3.8) | 10.36 (4.7) | 10.58 (4.8)
| Add'l Refrigerant (between Std & Max Piping Lngths) | Oz/ft (g/m) | 0.69 (65) | 0.69 (65) | 0.69 (65) | 0.69 (65) | 0.69 (65)
| Metering Device |  | EEV | EEV | EEV | EEV | EEV
Outdoor Coil | Face Area | Sq. Ft. | 5.9 | 8.16 | 8.16 | 14.08 | 13.53
| No. Rows |  | 2 | 2 | 3 | 1.6 | 2
| Fins per inch |  | 20 | 20 | 20 | 18 | 18
| Circuits |  | 6 | 4 | 4 | 8 | 8
Compressor | Type |  | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter | Rotary Inverter
| Model |  | KTM240D57UMT | KTM240D57UMT | KTF310D43UMT | EAPQ420D1UMUA | EAPQ420D1UMUA
| Oil Type |  | VG74 | VG74 | VG74 | VG74 | VG74
| Oil Charge | Fl. Oz. | 22.7 | 22.7 | 33.8 | 49.4 | 49.4
| Rated Current | RLA | 10 | 15 | 16.5 | 32 | 33
Airflow & Sound | Airflow | CFM | 1279 | 3000 | 3000 | 4500 | 4412
| Sound Pressure | dB(A) | 58 | 64 | 62 | 64 | 64
* Condensing unit above or below indoor unit
Copyright 2022 CAC/BDP • Atlanta, GA, 30339 | [9 empty] | Catalog No.: 38MURA-01SB
SUBJECT TO CHANGE WITHOUT NOTICE | [9 empty] | Replaces: NEW
Performance
Performance - Heat Pump (Standard Heat)
| Outdoor Size |  | 1.5T | 2T | 2.5T | 3T | 4T | 5T
M Ratings
Air Handler | Indoor Model |  | 18K | 24K | 30K | 36K | 48K | 60K
| Energy Star |  | NO | NO | NO | NO | NO | NO
| Cooling Rated Capacity | Btu/h | 18000 | 24000 | 30000 | 36000 | 47000 | 57000
| Cooling Cap. Range Min - Max | Btu/h | 5400~18700 | 7500~26000 | 9500~33000 | 7700~38900 | 10500~48000 | 4400~60200
| SEER |  | 19 | 19.4 | 19.5 | 18 | 17.3 | 18
| EER |  | 11.1 | 11.3 | 10.9 | 10.4 | 9.3 | 10.3
| Heating Rated Capacity (47°F) | Btu/h | 18500 | 26000 | 31000 | 36000 | 55000 | 60000
| Heating Rated Capacity (17°F) | Btu/h | 11500 | 17000 | 19000 | 18400 | 33000 | 33900
| Heating Rated Capacity (5°F) | Btu/h | 9500 | 17000 | 20000 | 21000 | 27000 | 29000
| Heating Cap. Range Min - Max | Btu/h | 5600~18700 | 5600~30000 | 12200~32000 | 6000~36400 | 11700~57000 | 11400~63100
| HSPF |  | 10.8 | 11.3 | 10.3 | 9.1 | 10 | 9.2
| COP (47°F) | W/W | 3.49 | 3.54 | 3.19 | 3.02 | 3 | 3.55
| COP (17°F) | W/W | 2.7 | 2.75 | 2.34 | 2.29 | 2 | 2.46
| COP (5°F) | W/W | 1.85 | 1.75 | 1.95 | 1.8 | 1.72 | 1.8
M1 Ratings
| Cooling Rated Capacity | Btu/h | 18000 | 24000 | 30000 | 36000 | 47000 | 57000
| Cooling Cap. Range Min - Max | Btu/h | 5400~18700 | 7500~26000 | 9500~33000 | 8900~38900 | 10500~48000 | 4400~60200
| SEER2 |  | 16 | 17 | 17.3 | 16.9 | 15.8 | 14.7
| EER2 |  | 13.5 | 12.9 | 13.7 | 12.8 | 10.9 | 11.3
| Heating Rated Capacity (47°F) | Btu/h | 18000 | 26000 | 31000 | 36000 | 55000 | 60000
| Heating Rated Capacity (17°F) | Btu/h | 11500 | 20700 | 20000 | 20500 | 36500 | 36000
| Heating Rated Capacity (5°F) | Btu/h | 10000 | 17000 | 17800 | 21000 | 32000 | 34800
| Heating Cap. Range Min - Max | Btu/h | 5600~18700 | 5600~30000 | 12200~32000 | 9700~36400 | 11700~57000 | 11400~63100
| HSPF2 |  | 8.7 | 9.1 | 8.5 | 8.2 | 9.4 | 8.4
| COP (47°F) | W/W | 3.5 | 3.45 | 3.25 | 3.39 | 3.15 | 3.45
| COP (17°F) | W/W | 2.78 | 2.4 | 2.47 | 2.42 | 2.3 | 2.35
| COP (5°F) | W/W | 2 | 2 | 1.74 | 1.88 | 1.98 | 1.89
Performance - Heat Pump (High Heat)
| Outdoor Size |  | 1.5T - HH | 2T - HH | 2.5T - HH | 3T - HH | 4T - HH | 5T - HH
M Ratings
| Indoor Model |  | 18K | 24K | 30K | 36K | 48K | 60K
| Energy Star |  | YES | YES | NO | NO | NO | NO
| Cooling Rated Capacity | Btu/h | 18000 | 24000 | 30000 | 36000 | 47000
| Cooling Cap. Range Min - Max | Btu/h | 6900~21000 | 6400~27000 | 10400~33600 | 12000~47400 | 18000~48000
| SEER |  | 20 | 20 | 18 | 18 | 16
| EER |  | 12.5 | 12.5 | 11 | 10.5 | 8.5
| Heating Rated Capacity (47°F) | Btu/h | 19000 | 24000 | 33000 | 41500 | 50000
| Heating Rated Capacity (17°F) | Btu/h | 13000 | 16700 | 19400 | 24100 | 32000
| Heating Rated Capacity (5°F) | Btu/h | 19000 | 24000 | 28500 | 43300 | 47000
| Heating Cap. Range Min - Max | Btu/h | 2800~21000 | 10100~31000 | 12000~37000 | 9000~57200 | 20000~55000
| HSPF |  | 11 | 12 | 10.5 | 10.5 | 10
| COP (47°F) | W/W | 3.59 | 3.45 | 3.48 | 3.45 | 3
| COP (17°F) | W/W | 2.78 | 2.74 | 2.61 | 2.68 | 2.34
| COP (5°F) | W/W | 1.9 | 1.8 | 1.95 | 1.8 | 1.88
M1 Ratings
| Cooling Rated Capacity | Btu/h | 18000 | 24000 | 30000 | 36000 | 47000
| Cooling Cap. Range Min - Max | Btu/h | 6900~21000 | 6400~27000 | 10400~33600 | 12000~47400 | 18000~48000
| SEER2 |  | 18 | 17.4 | 16.2 | 15.8 | 15.6
| EER2 |  | 12.4 | 11.7 | 9.8 | 9.8 | 8.2
| Heating Rated Capacity (47°F) | Btu/h | 19000 | 24000 | 33000 | 41000 | 50000
| Heating Rated Capacity (17°F) | Btu/h | 13000 | 18600 | 20400 | 29500 | 35000
| Heating Rated Capacity (5°F) | Btu/h | 16500 | 22700 | 24100 | 34500 | 46000
| Heating Cap. Range Min - Max | Btu/h | 2800~21000 | 10100~31000 | 12000~37000 | 9000~57200 | 20000~55000
| HSPF2 |  | 9.2 | 9.8 | 8.8 | 9.5 | 9.3
| COP (47°F) | W/W | 3.6 | 3.4 | 3.3 | 3.35 | 3.15
| COP (17°F) | W/W | 2.5 | 2.4 | 2.3 | 2.4 | 2.3
| COP (5°F) | W/W | 2 | 1.85 | 1.8 | 1.95 | 1.9
Dimensions
Size 3T - HH, 4T, 4T - HH & 5T are dual fan models.
Refer to Product Data for detailed dimensional drawings.
| Size |  | 1.5T | 2T | 2.5T | 3T | 4T | 5T
| Width (W) | in (mm) | 31.69 (805) | 35.04 (890) | 37.24 (946) | 37.24 (946) | 37.48 (952) | 37.48 (952)
| Height (H) | in (mm) | 21.81 (554) | 26.50 (673) | 31.89 (810) | 31.89 (810) | 52.48 (1333) | 52.48 (1333)
| Depth (D) | in (mm) | 12.99 (330) | 13.29 (338) | 16.02 (407) | 16.02 (407) | 16.34 (415) | 16.34 (415)
| L1 | in (mm) | 26.1 (663) | 26.1 (663) | 26.5 (673) | 26.5 (673) | 25 (634) | 25 (634)
| L2 | in (mm) | 13.65 (346.7) | 13.65 (346.7) | 15.85 (402.6) | 15.85 (402.6) | 15.9 (404) | 15.9 (404)
| Operating Weight | lbs (kg) | 75.84 (34.4) | 102.29 (46.4) | 141.76 (64.3) | 151.68 (68.8) | 217.59 (98.7) | 217.15 (98.5)
| Shipping Width | in (mm) | 36.02 (915) | 39.17 (995) | 42.91 (1090) | 42.91 (1090) | 43.11 (1095) | 43.11 (1095)
| Shipping Height | in (mm) | 24.21 (615) | 29.13 (740) | 34.84 (885) | 34.84 (885) | 58.27 (1480) | 58.27 (1480)
| Shipping Depth | in (mm) | 14.57 (370) | 15.67 (398) | 19.69 (500) | 19.69 (500) | 19.49 (495) | 19.49 (495)
| Shipping Weight | lbs (kg) | 81.35 (36.9) | 109.13 (49.5) | 151.46 (68.7) | 161.16 (73.1) | 248.68 (112.8) | 248.46 (112.7)
| Size |  | 1.5T - HH | 2T - HH | 2.5T - HH | 3T - HH | 4T - HH | 5T - HH
| Width (W) | in (mm) | 35.04 (890) | 37.24 (946) | 37.24 (946) | 37.48 (952) | 37.48 (952)
| Height (H) | in (mm) | 26.50 (673) | 31.89 (810) | 31.89 (810) | 52.48 (1333) | 52.48 (1333)
| Depth (D) | in (mm) | 13.29 (338) | 16.02 (407) | 16.02 (407) | 16.34 (415) | 16.34 (415)
| L1 | in (mm) | 26.1 (663) | 26.5 (673) | 26.5 (673) | 25 (634) | 25 (634)
| L2 | in (mm) | 13.65 (346.7) | 15.85 (402.6) | 15.85 (402.6) | 15.9 (404) | 15.9 (404)
| Operating Weight | lbs (kg) | 102.29 (46.4) | 141.76 (64.3) | 141.76 (64.3) | 217.59 (98.7) | 217.59 (98.7)
| Shipping Width | in (mm) | 39.17 (995) | 42.91 (1090) | 42.91 (1090) | 43.11 (1095) | 43.11 (1095)
| Shipping Height | in (mm) | 29.13 (740) | 34.84 (885) | 34.84 (885) | 58.27 (1480) | 58.27 (1480)
| Shipping Depth | in (mm) | 15.67 (398) | 19.69 (500) | 19.69 (500) | 19.49 (495) | 19.49 (495)
| Shipping Weight | lbs (kg) | 109.13 (49.5) | 151.46 (68.7) | 151.46 (68.7) | 248.68 (112.8) | 248.68 (112.8)
Copyright 2022 CAC/BDP • Atlanta, GA, 30339 | [9 empty] | Catalog No.: 38MURA-01SB
SUBJECT TO CHANGE WITHOUT NOTICE | [9 empty] | Replaces: NEW