## TABLE OF CONTENTS
TABLE OF CONTENTS
SINGLE ZONE DUCTLESS
| Compatibility Single Zone – Elevate Series | 2
| Compatibility Single Zone – Excel Series | 3
| Compatibility Single Zone – Essence Series | 4
MULTI-ZONE DUCTLESS
| Compatibility Multi-zone – Excel Series | 5
CONTROLS DUCTLESS
| Compatibility Controls | 6

## SINGLE ZONE HIGH TIER
Compatibility Single Zone – Elevate Series
INDOOR UNIT |  |  | HEAT PUMP OUTDOOR UNIT
|  |  | 38MPRAQ09AA3 | 38MPRAQ12AA3 |  | 38MPRAQ18AA3 | 38MPRAQ24AA3
|  |  | 38MPRBQ09AA3 | 38MPRBQ12AA3 | 38MPRBQ18AA3
High Wall | DHMPHAQ09XA3 | DHMPHBQ09XA3 | ●
| DHMPHAQ12XA3 | DHMPHBQ12XA3 |  | ●
|  | DHMPHBQ18XA3 |  |  | ● | ●
DHMPHAQ18XA3
| DHMPHAQ24XA3 | [5 empty] | ●
PHASED OUT
NOT AVAILABLE / COMPATIBLE
CURRENT MODELS

## SINGLE ZONE MID-TIER
Compatibility Single Zone – Excel Series
INDOOR UNIT
[12 empty] | 38MBRQ36A--3 | 38MBRQ48A--3 | 38MBRQ58A--3
|  |  | 38MAQB12R--1 |  | 38MAQB09R--3 | 38MAQB12R--3 | 38MAQB18R--3 | 38MAQB24R--3 | 38MAQB30R--3 | 38MAQB36R--3 |  | 38MBRBQ36AA3 | 38MBRBQ48AA3
|  |  | 38MARBQ12AA1 | 38MARBQ06AA3 | 38MARBQ09AA3 | 38MARBQ12AA3 | 38MARBQ18AA3 | 38MARBQ24AA3 | 38MARBQ30AA3 | 38MARBQ36AA3 | 38MARBQ36AB3 | 38MBRCQ36AA3 | 38MBRCQ48AA3 | 38MBRCQ58AA3
High Wall | DHMSHAQ12XA1 | DHMAHBQ12XA1 | ●
|  | DHMAHBQ06XA3 |  | ●
| DHMSHAQ09XA3 | DHMAHBQ09XA3 |  |  | ●
| DHMSHAQ12XA3 | DHMAHBQ12XA3 |  |  |  | ●
| DHMSHAQ18XA3 | DHMAHBQ18XA3 |  |  |  |  | ●
| DHMSHAQ24XA3 | DHMAHBQ24XA3 | [5 empty] | ●
| DHMSHAQ30XA3 | DHMAHBQ30XA3 | [6 empty] | ●
| DHMSHAQ36XA3 | DHMAHBQ36XA3 | [7 empty] | ●
Cassette |  | 40MBCQ09---3 |  |  | ●
|  | 40MBCQ12---3 |  |  |  | ●
|  | 40MBCQ18---3 |  |  |  |  | ●
| 40MBCQ24---3 | 40MBCAQ24XA3 | [5 empty] | ●
| 40MBCQ36---3 | 40MBCAQ36XA3 | [9 empty] | ●
| 40MBCQ48---3 | 40MBCAQ48XA3 | [10 empty] | ●
1way-Cassette |  | 40MCCAQ09XA3 |  | ● | ●
|  | 40MCCAQ18XA3 |  |  |  | ● | ●
Ducted |  | 40MBDQ09---3 40MBDAQ09XH3 |  |  | ●
|  | 40MBDQ12---3 40MBDAQ12XH3 |  |  |  | ●
|  | 40MBDQ18---3 40MBDAQ18XH3 |  |  |  |  | ●
|  | 40MBDQ24---3 40MBDAQ24XH3 |  |  |  |  | ● | ●
|  | 40MBDQ36---3 40MBDAQ36XH3 | [9 empty] | ●
|  | 40MBDQ48---3 40MBDAQ48XH3 | [10 empty] | ●
|  | 40MBDQ58---3 40MBDAQ58XH3 | [11 empty] | ●
Console | 40MBFQ12---3 | 40MBFAQ12XA3 |  |  |  | ●
|  | 40MBFQ18---3 |  |  |  |  | ●
|  | 40MBFQ24---3 | [5 empty] | ●
|  | 40MBFQ36---3 | [9 empty] | ●
|  | 40MBFQ48---3 | [10 empty] | ●
|  | 40MBFQ58---3 | [11 empty] | ●
Air Handler |  | 40MBABQ18XB3 |  |  |  |  | ● †
| 40MBAAQ24XA3 | 40MBABQ24XB3 | [5 empty] | ● †
|  | 40MBABQ30XB3 | [6 empty] | ● †
|  | 40MBABQ36XB3 | [8 empty] | ●
| 40MBAAQ36XA3 | 40MBABQ36XA3 | [9 empty] | ● †
| 40MBAAQ48XA3 | 40MBABQ48XA3 | [10 empty] | ● †
|  | 40MBABQ60XA3 | [11 empty] | ● †
PHASED OUT |  |  | † Notes:
NOT AVAILABLE / COMPATIBLE |  |  | Compatible with phased out outdoor unit models starting with serial number: V224940000, see TIC 2022-0021 for additional information
CURRENT MODELS

## SINGLE ZONE ENTRY TIER
Compatibility Single Zone – Essence Series
INDOOR UNIT |  |  |  | COOLING ONLY OUTDOOR UNIT
|  |  |  | 38MHRC09A--1 | 38MHRC12A--1 | 38MHRC09A--3 | 38MHRC12A--3 | 38MHRC18A--3 | 38MHRC24A--3
[5 empty] | 38MHRBC12AA1 |  | 38MHRBC12AA3 | 38MHRBC18AA3 | 38MHRBC24AA3
[5 empty] | 38MHRCC12AA1 |  | 38MHRCC12AA3 | 38MHRCC18AA3 | 38MHRCC24AA3
[5 empty] | 38MHRDC12AA1 | 38MHRDC09AA3 | 38MHRDC12AA3 | 38MHRDC18AA3 | 38MHRDC24AA3
High Wall | 40MHHC09---1 |  |  | ●
| 40MHHC12---1 |  |  |  | ●
|  | 40MHHC12--A1 | 40MHHAC12XA1 |  | ●
| 40MHHC09---3 |  | 40MHHAC09XA3 |  |  | ●
| 40MHHC12---3 |  | 40MHHAC12XA3 |  |  |  | ●
|  | 40MHHC12--A3 | 40MHHAC12XA3 |  |  |  | ●
|  | 40MHHC18---3 | 40MHHAC18XA3 |  |  |  |  | ●
|  | 40MHHC24---3 | 40MHHAC24XA3 | [5 empty] | ●
INDOOR UNIT |  |  | HEAT PUMP OUTDOOR UNIT
|  |  | 38MHRQ09A--1 | 38MHRQ12A--1 | 38MHRQ09A--3 | 38MHRQ12A--3 | 38MHRQ18A--3 | 38MHRQ24A--3
|  |  |  | 38MHRBQ12AA1 | 38MHRBQ09AA3 | 38MHRBQ12AA3 | 38MHRBQ18AA3 | 38MHRBQ24AA3
|  |  | 38MHRCQ09AA1 | 38MHRCQ12AA1 | 38MHRCQ09AA3 | 38MHRCQ12AA3 | 38MHRCQ18AA3 | 38MHRCQ24AA3 | 38MHRCQ30AA3 | 38MHRCQ36AA3
High Wall | 40MHHQ09---1 | 40MHHAQ09XA1 | ●
| 40MHHQ12---1 | 40MHHAQ12XA1 |  | ●
| 40MHHQ09---3 | 40MHHAQ09XA3 |  |  | ●
| 40MHHQ12---3 | 40MHHAQ12XA3 |  |  |  | ●
| 40MHHQ18---3 | 40MHHAQ18XA3 |  |  |  |  | ●
| 40MHHQ24---3 | 40MHHAQ24XA3 | [5 empty] | ●
|  | 40MHHAQ30XA3 | [6 empty] | ●
|  | 40MHHAQ36XA3 | [7 empty] | ●
PHASED OUT
NOT AVAILABLE / COMPATIBLE
CURRENT MODELS

## MULTI-ZONE
Compatibility Multi-zone – Excel Series
INDOOR UNIT |  |  | HEAT PUMP OUTDOOR UNIT
|  |  | 38MGRQ18B--3 | 38MGRQ24C--3 | 38MGRQ30D--3 |  | 38MGRQ36D--3 † | 38MGRQ48E--3 †
|  |  | 38MGRBQ18BA3 | 38MGHBQ24CA3 | 38MGHBQ30DA3 | 38MGRBQ36DA3 | 38MGHBQ36DA3 | 38MGRBQ48EA3 | 38MGHBQ48EA3
High Wall Elevate | DHMPHAQ09XA3 | DHMPHBQ09XA3 | ● | ● | ● | ● | ● | ● | ●
| DHMPHAQ12XA3 | DHMPHBQ12XA3 | ● | ● | ● | ● | ● | ● | ●
|  | DHMPHBQ18XA3 |  |  | ● | ● | ● | ● | ●
DHMPHAQ18XA3
DHMPHAQ24XA3
High Wall Excel |  | DHMAHBQ06XA3 | ● | ● | ● | ● | ● | ● | ●
| DHMSHAQ09XA3 | DHMAHBQ09XA3 | ● | ● | ● | ● | ● | ● | ●
| DHMSHAQ12XA3 | DHMAHBQ12XA3 | ● | ● | ● | ● | ● | ● | ●
| DHMSHAQ18XA3 | DHMAHBQ18XA3 |  | ● | ● | ● | ● | ● | ●
| DHMSHAQ24XA3 | DHMAHBQ24XA3 |  |  | ● | ● | ● | ● | ●
|  | DHMAHBQ30XA3 |  |  |  |  | ●† | ●† | ●
|  | DHMAHBQ36XA3 |  |  |  |  | ●† | ●† | ●
High Wall Essence |  | 40MHHAQ09XA3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MHHAQ12XA3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MHHAQ18XA3 |  | ● | ● | ● | ● | ● | ●
|  | 40MHHAQ24XA3 |  |  | ● | ● | ● | ● | ●
|  | 40MHHAQ30XA3 |  |  |  |  | ●† | ●† | ●
|  | 40MHHAQ36XA3 |  |  |  |  | ●† | ●† | ●
Cassette |  | 40MBCQ09---3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBCQ12---3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBCQ18---3 |  | ● | ● | ● | ● | ● | ●
| 40MBCQ24---3 | 40MBCAQ24XA3 |  |  | ● | ● | ● | ● | ●
1way-Cassette |  | 40MCCAQ09XA3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MCCAQ18XA3 | ● | ● | ● | ● | ● | ● | ●
Ducted |  | 40MBDQ09---3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBDQ12---3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBDQ18---3 |  | ● | ● | ● | ● | ● | ●
|  | 40MBDQ24---3 |  |  | ● | ● | ● | ● | ●
High Static Ducted |  | 40MBDAQ09XH3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBDAQ12XH3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBDAQ18XH3 |  | ● | ● | ● | ● | ● | ●
|  | 40MBDAQ24XH3 |  |  | ● | ● | ● | ● | ●
|  | 40MBDAQ36XH3 |  |  |  |  | ●† | ●† | ●
Console |  | 40MBFAQ12XA3 | ● | ● | ● | ● | ● | ● | ●
|  | 40MBFQ18---3 |  | ● | ● | ● | ● | ● | ●
|  | 40MBFQ24---3 |  |  | ● | ● | ● | ● | ●
Air Handler † |  | 40MBABQ18XB3 |  | ● | ● | ● | ● | ● | ●
| 40MBAAQ24XA3 | 40MBABQ24XB3 |  |  | ● | ● | ● | ● | ●
|  | 40MBABQ30XB3 |  |  |  |  | ●† | ●† | ●†
|  | 40MBABQ36XB3 |  |  |  |  | ●† | ●† | ●†
PHASED OUT |  |  | † Notes: | A maximum two (2) AHUs can be added to a MZ system. Refer to the application tables in the prodcut data for allowed combinations
NOT AVAILABLE / COMPATIBLE |  |  |  | Regardless of size, when two (2) AHUs are connected to any MZ ODU, no other indoor units can be added to the system
CURRENT MODELS |  |  |  | If a 30k or 36k AHU is connected to a any outdoor unit, 500g (17.6 Oz) of additional refrigerant charge has to be added to the system
30k or 36k indoor units are not compatilble with phased out models

## CONTROLS
Compatibility Controls
| Indoor unit type |  | HIGH WALL |  |  |  |  | CASSETTE |  | DUCTED | CONSOLE | AIR HANDLER
| Indoor Family Name | Single Zone / Multi-zone | DHMPHA | DHMPHB | DHMSHA | DHMAHB | 40MHH | 40MBCQ | 40MBCAQ | 40MBDQ | 40MBFQ | 40MBAA | 40MBAB
WIRED CONTROLLERS | KSACN0101AAA | Single Zone & Multi-zone |  | ○ 18k | ○ | ○ |  | ○ 9 - 18 | ○ | ○ | ○
| KSACN0601AAA | Single Zone & Multi-zone | ○ | ○ 9-12k | ○ † |  | ○ |  |  |  | ○ 9 -12 ‡
| KSACN0701AAA | Single Zone & Multi-zone | [5 empty] | ○ | ○ | ●** | ○ 18-58
| KSACN0801AAA | Single Zone & Multi-zone |  | ○ 18k |  | ○
| KSACN0901AAA | Single Zone & Multi-zone |  |  |  |  | ○***
| KSACN1001AAA | Single Zone & Multi-zone | [10 empty] | ●
24V INTERFACE* | KSAIC0101115 | Single Zone Only |  |  | ○ 115V |  | ○ 115V
| KSAIC0101230 | Single Zone Only | ○ |  | ○ 230V |  | ○ 230V | ○ |  | ○ | ○ 12-58 Ͱ
| KSAIC0301230 | Single Zone & Multi-zone | ○ | ○ | ○ 230V | ○ 230V | ○ 230V | ○ | ○ | ○ | ○ 12-58 Ͱ | BUILT-IN | BUILT-IN
WI-FI KITS | KSAIF0101AAA | Single Zone & Multi-zone |  |  |  |  | ○ 9/12/24k
| KSAIF0201AAA | Single Zone & Multi-zone |  |  |  |  | ○ 18k
| KSAIF0301AAA | Single Zone & Multi-zone | ˩ | ˩ | ○ | ˩ | ˩
| KSAIF0401AAA | Single Zone & Multi-zone | [5 empty] | ○ |  | ○ | ○ 18-58 |  | ○
| KSAIF0601AAA | Single Zone & Multi-zone | ● | ● |  | ○ |  |  | ○
○ | Optional
● | Standard
Notes:
† 7 Day programmable compatible with indoor units starting with Serial Number 0216V10001.
‡ Compatible with indoor units starting with Serial Number 0117V10001.
*** Only compatible with 40MHHAQ (Heat Pump High Wall)
** Starting with Serial Number 2820V10001 (Week 28, Year 2020) the KSACN0701AAA became the standard controller but is backwards compatible with previous production units
*24V interface compatible with all indoor units starting with Serial Number 4216V10001 unless noted
Ͱ 24V Interface compatible with all the sizes except sizes 12 and 58. Starting with Serial Number 1419V10001 the sizes 12 and 58 are shipped with the compatible control board.
Units built prior these serial number would require a Control Board Replacement on the Indoor unit.
Board replacement for forward compatibility is not covered as a warranty claim
˩ Indoor unit model comes with everything to be compatible with the USB WiFi Dongle Model 17310900000281 from the KSAIF0301AAA kit. If installed in a high wall unit other than the 40MAQ, install the USB WiFi Dongle 17310900000281 into the high wall unit's factory USB port only and discard all other components of the KSAIF0301AAA kit.
Board replacement for forward compatibility is not covered as a warranty claim
PHASED OUT
NOT AVAILABLE / COMPATIBLE
CURRENT MODELS