## TABLE OF CONTENTS
TABLE OF CONTENTS
SINGLE ZONE DUCTLESS
| Compatibility Single Zone – Evolution® System (37MPRAQ/37MAHAQ/37MBHAQ) | 2
| Compatibility Single Zone – Preferred Series Heat Pump (37MARAQ/37MBRAQ) | 3
| Compatibility Single Zone – Legacy Line (37MHRAQ/37MHRAC) | 4
| Compatibility Crossover Heat Pumps (37MUHAQ/37MURAQ) | 7
MULTI-ZONE DUCTLESS
| Compatibility Multi-zone – Evolution® System | 5
| Compatibility Multi-zone – Preferred System | 6
CONTROLS / ACCESSORIES DUCTLESS
| Compatibility Ductless Controls | 8
| Compatibility Ductless Accessories | 9

## SINGLE ZONE HIGH TIER
Compatibility Single Zone – Evolution® System (37MPRAQ/37MAHAQ/37MBHAQ)
Evolution INDOOR UNIT |  | Evolution HEAT PUMP OUTDOOR UNIT
|  | 37MPRAQ06AA3 | 37MPRAQ09AA3 | 37MPRAQ12AA3 | 37MPRAQ18AA3
High Wall Evolution | 615PHAQ06XA3 | ●
| 615PHAQ09XA3 |  | ●
| 615PHAQ12XA3 |  |  | ●
| 615PHAQ18XA3 |  |  |  | ●
Compatibility Single Zone –Evolution® System (37MAHAQ)
Preferred INDOOR UNIT |  | Evolution® SINGLE ZONE HEAT PUMP OUTDOOR UNIT
|  | 37MAHAQ06AA3 | 37MAHAQ09AA3 | 37MAHAQ12AA3 | 37MAHAQ18AA3 | 37MAHAQ24AA3 | 37MAHAQ33AA3 | 37MBHAQ36AA3 | 37MBHAQ48AA3 | 37MBHAQ58AA3
High Wall Preferred | 615AHAQ12XA1
| 615AHAQ06XA3 | ●
| 615AHAQ09XA3 |  | ●
| 615AHAQ12XA3 |  |  | ●
| 615AHAQ18XA3 |  |  |  | ●
| 615AHAQ24XA3 |  |  |  |  | ●
615AHAQ30XA3
| 615AHAQ33XA3 | [5 empty] | ●
615AHAQ36XA3
4-Way Cassette | 45MBCAQ12XA3 |  | ● | ●
| 45MBCAQ18XA3 |  |  |  | ●
| 45MBCAQ24XA3 |  |  |  |  | ●
| 45MBCAQ36XA3 | [5 empty] | ●
| 45MBCAQ48XA3 | [6 empty] | ●
1-way cassette | 45MCCAQ06XA3 | ●
| 45MCCAQ12XA3 |  | ●
| 45MCCAQ18XA3 |  |  | ● | ●
Floor Console | 45MBFAQ09XA3 |  | ●
| 45MBFAQ12XA3 |  |  | ●
| 45MBFAQ16XA3 |  |  |  | ●
Underceiling Console | 45MCFAQ18XA3 |  |  |  | ●
| 45MCFAQ24XA3 |  |  |  |  | ●
| 45MCFAQ36XA3 | [6 empty] | ●
| 45MCFAQ48XA3 | [7 empty] | ●
| 45MCFAQ58XA3 | [8 empty] | ●
Low Static Ducted | 45MBDAQ06XA3 | ●
| 45MBDAQ12XA3 |  | ●
| 45MBDAQ12XA3 |  |  | ●
| 45MBDAQ18XA3 |  |  |  | ●
High Static Ducted | 45MBDAQ12XH3 |  | ●
| 45MBDAQ12XH3 |  |  | ●
| 45MBDAQ18XH3 |  |  |  | ●
| 45MBDAQ24XH3 |  |  |  |  | ●
| 45MBDAQ36XH3 | [6 empty] | ●
| 45MBDAQ48XH3 | [7 empty] | ●
| 45MBDAQ58XH3 | [8 empty] | ●
Air Handler | 45MBAAQ18XB3 |  |  |  | ●
| 45MBAAQ24XB3 |  |  |  |  | ●
45MBAAQ30XB3
| 45MBAAQ36XB3 | [5 empty] | ●
| 45MBAAQ36XA3 | [6 empty] | ●
| 45MBAAQ48XA3 | [7 empty] | ●
| 45MBAAQ60XA3 | [8 empty] | ●
X1A0T
X1A0T
X1A0T
X1A0T

## SINGLE ZONE MID-TIER
Compatibility Single Zone – Preferred Series Heat Pump (37MARAQ/37MBRAQ)
Preferred INDOOR UNIT |  | Preferred SINGLE ZONE HEAT PUMP OUTDOOR UNIT
|  | 37MARAQ12AA1 | 37MARAQ09AA3 | 37MARAQ12AA3 | 37MARAQ18AA3 | 37MARAQ24AA3 | 37MARAQ30AA3 | 37MARAQ36AA3 | 37MBRAQ36AA3 | 37MBRAQ48AA3 | 37MBRAQ58AA3
High Wall | 615AHAQ12XA1 | ●
615AHAQ06XA3
| 615AHAQ09XA3 |  | ●
| 615AHAQ12XA3 |  |  | ●
| 615AHAQ18XA3 |  |  |  | ●
| 615AHAQ24XA3 |  |  |  |  | ●
| 615AHAQ30XA3 | [5 empty] | ●
615AHAQ33XA3
| 615AHAQ36XA3 | [6 empty] | ●
4-Way Cassette | 45MBCAQ12XA3 |  | ● | ●
| 45MBCAQ18XA3 |  |  |  | ●
| 45MBCAQ24XA3 |  |  |  |  | ●
| 45MBCAQ36XA3 | [7 empty] | ●
| 45MBCAQ48XA3 | [8 empty] | ●
1-Way cassette | 45MCCAQ06XA3
| 45MCCAQ12XA3 |  | ●
| 45MCCAQ18XA3 |  |  | ● | ●
Floor Console | 45MBFAQ09XA3 |  | ●
| 45MBFAQ12XA3 |  |  | ●
| 45MBFAQ16XA3 |  |  |  | ●
Underceiling Console | 45MCFAQ18XA3 |  |  |  | ●
| 45MCFAQ24XA3 |  |  |  |  | ●
| 45MCFAQ36XA3 | [7 empty] | ●
| 45MCFAQ48XA3 | [8 empty] | ●
| 45MCFAQ58XA3 | [9 empty] | ●
Low Static Ducted | 45MBDAQ06XA3
| 45MBDAQ12XA3 |  | ●
| 45MBDAQ12XA3 |  |  | ●
| 45MBDAQ18XA3 |  |  |  | ●
High Static Ducted | 45MBDAQ12XH3 |  | ●
| 45MBDAQ12XH3 |  |  | ●
| 45MBDAQ18XH3 |  |  |  | ●
| 45MBDAQ24XH3 |  |  |  |  | ●
| 45MBDAQ36XH3 | [7 empty] | ●
| 45MBDAQ48XH3 | [8 empty] | ●
| 45MBDAQ58XH3 | [9 empty] | ●
Air Handler | 45MBAAQ18XB3 |  |  |  | ●
| 45MBAAQ24XB3 |  |  |  |  | ●
| 45MBAAQ30XB3 | [5 empty] | ●
| 45MBAAQ36XB3 | [6 empty] | ●
| 45MBAAQ36XA3 | [7 empty] | ●
| 45MBAAQ48XA3 | [8 empty] | ●
| 45MBAAQ60XA3 | [9 empty] | ●
X2A0T
X2A0T
X2A0T
X2A0T

## SINGLE ZONE ENTRY TIER
Compatibility Single Zone – Legacy Line (37MHRAQ/37MHRAC)
INDOOR UNIT |  | HEAT PUMP OUTDOOR UNIT
|  | 37MHRAQ09AA1 | 37MHRAQ12AA1 | 37MHRAQ09AA3 | 37MHRAQ12AA3 | 37MHRAQ18AA3 | 37MHRAQ24AA3 | 37MHRAQ30AA3 | 37MHRAQ36AA3
High Wall Legacy | 45MHHAQ09XC1 | ●
| 45MHHAQ12XC1 |  | ●
| 45MHHAQ09XC3 |  |  | ●
| 45MHHAQ12XC3 |  |  |  | ●
| 45MHHAQ18XC3 |  |  |  |  | ●
| 45MHHAQ24XC3 | [5 empty] | ●
| 45MHHAQ30XC3 | [6 empty] | ●
| 45MHHAQ36XC3 | [7 empty] | ●
Compatibility Single Zone 37MHRAC Cooling Only Outdoor Unit - Legacy Line
INDOOR UNIT |  | OUTDOOR UNIT (Cooling Only)
|  | 37MHRAC12AA1 | 37MHRAC09AA3 | 37MHRAC12AA3 | 37MHRAC18AA3 | 37MHRAC24AA3
High Wall | 45MHHAC12XC1 | ●
| 45MHHAC09XC3 |  | ●
| 45MHHAC12XC3 |  |  | ●
| 45MHHAC18XC3 |  |  |  | ●
| 45MHHAC24XC3 |  |  |  |  | ●
X3A0T
X3A0T
X3A0T
X3A0T

## MULTI-ZONE HIGH TIER
Compatibility Multi-zone – Evolution® System
INDOOR UNIT |  | MULTIZONE HEAT PUMP OUTDOOR UNIT
|  | 37MGHAQ18CA3 | 37MGHAQ24DA3 | 37MGHAQ30EA3 | 37MGHAQ36EA3 | 37MGHAQ48FA3 | 37MGHAQ55FA3
High Wall Evolution* | 615PHAQ06XA3 | ● | ● | ● | ● | ● | ●
| 615PHAQ09XA3 | ● | ● | ● | ● | ● | ●
| 615PHAQ12XA3 | ● | ● | ● | ● | ● | ●
| 615PHAQ18XA3 | ● | ● | ● | ● | ● | ●
High Wall Preferred | 615AHAQ06XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ09XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ12XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ18XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ24XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ30XA3 |  | ● | ● | ● | ● | ●
| 615AHAQ33XA3 |  |  | ● | ● | ● | ●
| 615AHAQ36XA3 |  |  | ● | ● | ● | ●
4-Way Cassette | 45MBCAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBCAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBCAQ18XA3 | ● | ● | ● | ● | ● | ●
| 45MBCAQ24XA3 | ● | ● | ● | ● | ● | ●
1-way cassette | 45MCCAQ06XA3 | ● | ● | ● | ● | ● | ●
| 45MCCAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MCCAQ18XA3 | ● | ● | ● | ● | ● | ●
Floor Console | 45MBFAQ09XA3 | ● | ● | ● | ● | ● | ●
| 45MBFAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBFAQ16XA3 | ● | ● | ● | ● | ● | ●
Underceiling Console | 45MCFAQ18XA3 | ● | ● | ● | ● | ● | ●
| 45MCFAQ24XA3 | ● | ● | ● | ● | ● | ●
Low Static Ducted | 45MBDAQ06XA3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ18XA3 | ● | ● | ● | ● | ● | ●
High Static Ducted | 45MBDAQ12XH3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ12XH3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ18XH3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ24XH3 | ● | ● | ● | ● | ● | ●
Air Handler | 45MBAAQ18XB3 | ● | ● | ● | ● | ● | ●
| 45MBAAQ24XB3 | ● | ● | ● | ● | ● | ●
| 45MBAAQ30XB3 |  | ● | ● | ● | ● | ●
| 45MBAAQ36XB3 |  |  | ● | ● | ● | ●
For high tier 6K/9K/12K high wall indoor units, they are considered as 18K unit in the multi-zone combination. (Same chassis with mid tier 18K High wall)
For high tier 18K high wall indoor units, they are considered as 24K unit in the multi-zone combination. (Same chassis size with mid tier 24K High wall)
Up to 2 AHUs can be used for the following combinations only: 18+18, 18+24, 18+30, 18+36, 24+24, 24+30, 24+36. In the case that 2 AHU units are selected, no other units may be connected to the outdoor unit, regardless of remaining ports or capacity availability.
When a 30k or 36k AHU is utilized with a Multi-Zone ODU, 500 grams (17.6 Oz) of additional refrigerant should be added to the system
Note on C12: chhabrm: This is different with High Heat model, but Midea is confirming this,
Note on D13: chhabrm: This is different with High Heat model, but Midea is confirming this,
X4A0T
X4A0T
X4A0T
X4A0T

## MULTI-ZONE MID TIER
Compatibility Multizone 37MGRAQ Heat Pump - Preferred Series
INDOOR UNIT |  | MULTIZONE HEAT PUMP OUTDOOR UNIT
|  | 37MGRAQ18CA3 | 37MGRAQ24DA3 | 37MGRAQ30EA3 | 37MGRAQ36EA3 | 37MGRAQ48FA3 | 37MGRAQ55FA3
High Wall Evolution | 615PHAQ06XA3 |  | ● | ● | ● | ● | ●
| 615PHAQ09XA3 |  | ● | ● | ● | ● | ●
| 615PHAQ12XA3 |  | ● | ● | ● | ● | ●
| 615PHAQ18XA3 |  | ● | ● | ● | ● | ●
High Wall Preferred | 615AHAQ06XA3 |  | ● | ● | ● | ● | ●
| 615AHAQ09XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ12XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ18XA3 | ● | ● | ● | ● | ● | ●
| 615AHAQ24XA3 |  | ● | ● | ● | ● | ●
| 615AHAQ30XA3 |  |  | ● | ● | ● | ●
| 615AHAQ33XA3 |  |  |  |  | ● | ●
| 615AHAQ36XA3 |  |  |  |  | ● | ●
4-way Cassette | 45MBCAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBCAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBCAQ18XA3 | ● | ● | ● | ● | ● | ●
| 45MBCAQ24XA3 |  | ● | ● | ● | ● | ●
1-way cassette | 45MCCAQ06XA3 | ● | ● | ● | ● | ● | ●
| 45MCCAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MCCAQ18XA3 | ● | ● | ● | ● | ● | ●
Floor Console | 45MBFAQ09XA3 | ● | ● | ● | ● | ● | ●
| 45MBFAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBFAQ16XA3 | ● | ● | ● | ● | ● | ●
Underceiling Console | 45MCFAQ18XA3 | ● | ● | ● | ● | ● | ●
| 45MCFAQ24XA3 |  | ● | ● | ● | ● | ●
Low Static Ducted | 45MBDAQ06XA3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ12XA3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ18XA3 | ● | ● | ● | ● | ● | ●
High Static Ducted | 45MBDAQ12XH3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ12XH3 | ● | ● | ● | ● | ● | ●
| 45MBDAQ18XH3 |  | ● | ● | ● | ● | ●
| 45MBDAQ24XH3 |  | ● | ● | ● | ● | ●
Air Handler | 45MBAAQ18XB3 | ● | ● | ● | ● | ● | ●
| 45MBAAQ24XB3 | ● | ● | ● | ● | ● | ●
| 45MBAAQ30XB3 |  |  | ● | ● | ● | ●
| 45MBAAQ36XB3 |  |  |  |  | ● | ●
For high tier 6K/9K/12K high wall indoor units, they are considered as 18K unit in the multi-zone combination. (Same chassis with mid tier 18K High wall)
For high tier 18K high wall indoor units, they are considered as 24K unit in the multi-zone combination. (Same chassis size with mid tier 24K High wall)
Up to 2 AHUs can be used for the following combinations only: 18+18, 18+24, 18+30, 18+36, 24+24, 24+30, 24+36. In the case that 2 AHU units are selected, no other units may be connected to the outdoor unit, regardless of remaining ports or capacity availability.
When a 30k or 36k AHU is utilized with a Multi-Zone ODU, 500 grams (17.6 Oz) of additional refrigerant should be added to the system
X5A0T
X5A0T
X5A0T
X5A0T

## CROSSOVER
Compatibility Crossover Heat Pumps (37MUHAQ/37MURAQ)
INDOOR UNIT |  | Preferred SINGLE ZONE HEAT PUMP OUTDOOR UNIT
|  | 37MUHAQ18AA3 | 37MUHAQ24AA3 | 37MUHAQ30AA3 | 37MUHAQ36AA3 | 37MUHAQ48AA3 | 37MUHAQ60AA3
Air Handler - Preferred | 45MUHAQ24XX3 | ●
| 45MUHAQ24XX3 |  | ●
| 45MUHAQ36XX3 |  |  | ●
| 45MUHAQ36XX3 |  |  |  | ●
| 45MUHAQ60XX3 |  |  |  |  | ●
| 45MUHAQ60XX3 | [5 empty] | ●
Air Handler - Legacy | 45MUAAQ18XX3 | ●
| 45MUAAQ24XX3 |  | ●
| 45MUAAQ30XX3 |  |  | ●
| 45MUAAQ36XX3 |  |  |  | ●
| 45MUAAQ48XX3 |  |  |  |  | ●
| 45MUAAQ60XX3 | [5 empty] | ●
INDOOR UNIT |  | Legacy SINGLE ZONE HEAT PUMP OUTDOOR UNIT
|  | 37MURAQ18AA3 | 37MURAQ24AA3 | 37MURAQ30AA3 | 37MURAQ36AA3 | 37MURAQ48AA3 | 37MURAQ60AA3
Air Handler - Legacy | 45MUAAQ18XX3 | ●
| 45MUAAQ24XX3 |  | ●
| 45MUAAQ30XX3 |  |  | ●
| 45MUAAQ36XX3 |  |  |  | ●
| 45MUAAQ48XX3 |  |  |  |  | ●
| 45MUAAQ60XX3 | [5 empty] | ●
X6A0T
X6A0T
X6A0T
X6A0T

## CONTROLS
Compatibility Ductless Controls
| Indoor unit type |  | HIGH WALL |  |  |  |  | CASSETTE |  | DUCTED | CONSOLE |  | AIR HANDLER
| Indoor Family Name | Unit Type | **45MPHA | **45MAHA | **45MHHAQ | **45MHHAC | **D5MVHA | 45MBCA | 45MCCA | 45MBDA | 45MBFA | 45MCFA | 45MBAA | 45MUAA | 45MUHA
WIRED CONTROLLERS | KSACN1201AAA | Single Zone & Multi-zone | ● | ● | ● | ● | ● | ● | ● | ● | ● | ●
| KSACN1401AAA (In built Wi-Fi) | Single Zone & Multi-zone | ● | ● | ● | ● |  | ● | ● | ● | ● | ● | ● | ● | ●
WIFI KIT | KSAIF0701AAA | Single Zone & Multi-zone | ● | ● | ● | ● | ● | ● | ● |  | ● |  | ● | ● | ●
24V MINI INTERFACE | KSAIC0601230 | Single Zone & Multi-zone | ● | ● | ● | ● | ● | ● | ● | ● | ● | ●
*24V Mini is powered by 5V/12 Voltage, It Is backward compatible with R410A
| Indoor unit type |  | HIGH WALL |  |  |  |  | CASSETTE |  | DUCTED | CONSOLE | AIR HANDLER
| Indoor Family Name | Unit Type | 40MPHB | 40MAHB | 40MHHAQ | 40MHHAC | DHMVHA | 40MBC(A)Q | 40MCCA | 40MBDA/Q | 40MBF(Q)A | 40MUAA | 40MBAB
WIRED CONTROLLERS | KSACN1201AAA | Single Zone & Multi-zone | ● | ● | ● | ● | ● | ● | ● | ● | ●
| KSACN1401AAA (In built Wi-Fi) | Single Zone & Multi-zone | [5 empty] | ● | ● | ● |  | ● | ●
WIFI KIT | KSAIF0701AAA | Single Zone & Multi-zone | ● | ● | ● | ● |  | ● | ● |  |  | ● | ●
24V MINI INTERFACE | KSAIC0601230 | Single Zone & Multi-zone | [5 empty] | ● | ● | ● | ● ***
Notes:
Compatible | ●
Not Compatible
Puron Advance
**Only these Puron Advance ductless models are compatible with the Puron ductless Wi-Fi Kit (KSAIF0601AAA) - All other Puron ductless Wi-Fi Kits are not compatible with the Puron Advance ductless product line
Puron ductless wired controllers are not compatible with the Puron Advance ductless product line
24V Mini Interface is not compatible with Puron Advance Air Handlers
R410A Models
***24V Mini Interface is compatible with Puron ductless model Ceiling/Floor Consoles sizes 18K and over
24V Mini Interface is compatible with Puron ductless Cassettes and Ducted models but not compatible with Puron ductless High Walls, Puron 12K Floor Console, and Puron Air Handlers
X7A0T
X7A0T
X7A0T
X7A0T

## ACC
INDOOR UNIT |  | HEAT PUMP OUTDOOR UNIT (AHU2, AHU3)
|  | 45MUAAQ18XX3 | 45MUAAQ24XX3 | 45MUAAQ30XX3 | 45MUAAQ36XX3 |  | 45MUAAQ48XX3 | 45MUAAQ60XX3
|  | 45MBAAQ18XB3 | 45MBAAQ24XB3 | 45MBAAQ30XB3 | 45MBAAQ36XB3 | 45MBAAQ36XA3 | 45MBAAQ48XA3 | 45MBAAQ60XA3
C Heaters | EHKMC05KN | ● | ● | ● | ● | ●
| EHKMC08KN | ● | ● | ● | ● | ● | ●
| EHKMC10KN | ● | ● | ● | ● | ● | ● | ●
| EHKMC15KN |  | ● | ● | ● | ● | ● | ●
| EHKMC20KN |  |  |  | ● | ● | ● | ●
| EHKMC25KN | [6 empty] | ●
INDOOR UNIT |  | HEAT PUMP OUTDOOR UNIT (AHU4)
|  | 45MUHAQ24XX3 | 45MUHAQ36XX3 | 45MUHAQ60XX3
D Heaters | EHKMD05KN | ● | ●
| EHKMD08KN | ● | ●
| EHKMD10KN | ● | ● | ●
| EHKMD15KN | ● | ● | ●
| EHKMD20KN |  | ● | ●
| EHKMD25KN |  |  | ●
Cassette Panel | Model# R410 | Model# R454B
9K-18K | 40MBCQ01XXX3 | 45MBCQ01XXX3
24K-48K | 40MBCQ02XXX4 | 45MBCQ02XXX4
*R410A 9K-18K Cassette Panel will not be compatible with R454B Cassette Panel.
X8A0T
X8A0T
X8A0T