Project Name:
New Job
Specification
Date: 2/2/2017

Project Number:
2


1.0 PART 2 - PRODUCTS
1.1 Materials

1.1.1 Application Specific Controllers

1.1.1.1 VVT System Applications

1.1.1.1.1 VVT Controllers Retrofit: Zone and Bypass 

1.1  boofoo

A.  Controller Software 

1.  Building and energy management application software shall reside and operate in system controllers. Applications shall be configurable through the operator workstation, web browser interface, or engineering workstation.

2.  Memory and System Time. All controllers shall have a Non-Volatile Memory providing indefinite storage of application and configuration data. The system must have an ability to maintain time, and automatically correct for daylight savings time and leap year adjustments. In the event of power failure or user generated power cycle, all system components must automatically updated with current time and date from a network Time Sync device. The controller shall also have the capability of changing occupancy mode by reading a set of discrete, dry contacts controlled by an external time clock.

3.  Stand alone capability. All controllers shall be capable of providing all control functions of the HVAC system without the use of a computer. The controllers shall include the inherent capability to access the system control selections as well as to monitor system performance by means of a communicating network with a PC and EMS software program.

4.  System Security: Other hand held or wall mounted local interface device that allow configuration access shall be password protected with minimum of two levels of security. Level one shall provide limited access to controller operational parameters and level two shall provide full access to controller operational and configuration parameters. 

5.  Scheduling. 

a.  System shall provide the following schedule options as a minimum: 

b.  Weekly. Provide separate schedules for each day of the week. Each schedule shall be able to include up to 5 occupied periods (5 start-stop pairs or 10 events).

c.  Exception. Operator shall be able to designate an exception schedule for each of the next 365 days. After an exception schedule has executed, system shall discard and replace exception schedule with standard schedule for that day of the week.

d.  Holiday. Operator shall be able to define 24 special or holiday schedules of varying length on a scheduling calendar that repeats each year.

6.  Remote Communication. System shall automatically contact operator workstation or server on receipt of critical alarms.

7.  Sequencing. Application software shall sequence chillers, boilers, and pumps as specified in Sequence of Operations for HVAC Controls.

8.  PID Control. System shall provide direct- and reverse-acting PID (proportional-integral-derivative) algorithms. Each algorithm shall have anti-windup and selectable controlled variable, setpoint, and PID gains. Each algorithm shall calculate a time-varying analog value that can be used to position an output or to stage a series of outputs.

9.  Staggered Start. System shall stagger controlled equipment restart after power outage. Operator shall be able to adjust equipment restart order and time delay between equipment restarts.

10.  Anti-Short Cycling. Binary output objects shall be protected from short cycling by means of preconfigured minimum on-time and off-time settings, customized for the specific requirements of the application.

11.  On and Off Control with Differential. System shall provide direct- and reverse-acting on and off algorithms with adjustable differential to cycle a binary output based on a controlled variable and setpoint.

12.  Zoning system compatible with constant volume air source (Variable Volume/Variable Temperature) (VVT). The zoning system shall be compatible with constant volume air source and consist of programmable, multiple communicating Zone Controllers and a Bypass Controller. The system shall also include a complete array of input and output devices. The system shall provide full control of HVAC heating and cooling equipment in a multiple zone application. The zoning system shall be capable of operating as a stand-alone system or networked with multiple systems to communicating air source controllers. 

a.  Zone control. Each zone shall be capable of monitoring space conditions and providing the correct amount of conditioned air to satisfy the space load. Each zone shall be capable of the following:

1)  Space temperatures control. To maintain individual heating and cooling set points.

2)  Relative Humidity/Air Quality (DCV). Each zone shall be capable of maintaining space relative humidity set point or air quality set point (zone level demand control ventilation) as defined in ASHRAE 62-1989 (including Addendum 62a-1990).

3)  Demand coordination. Each zone shall be capable of zone demand data coordination with other zones in the system.  

b.  Static pressure control. The zoning system shall be capable of maintaining a user adjustable supply air duct static pressure set point. 

1)  The Bypass controller shall additionally provide the capability to increase system airflow during conditions when the temperature of the supply air from the equipment is approaching the limits of operation. In these cases, the Bypass controller shall raise the static pressure setpoint to a user configurable maximum limit in order to increase the system airflow during these conditions. 

2)  The Bypass control shall contain the ability to monitor the bypass damper movement (or VFD speed) and automatically adjust the setpoint control band and/or hysteresis in order to provide stability and prevent premature actuator failure. 

c.  Air source control. Shall control all associated HVAC rooftop equipment functions, and be capable of stand-alone or networked operation. The resident algorithms shall use error reduction logic as designated in ASHRAE standard 90.1 to provide temperature control and lower energy usage. The Air source shall be capable of zone demand data coordination with the associated zones. 

d.  System Terminal Modes. Each air terminal mode shall be based on the current air source mode, terminal type, space temperature, and the current temperature set points. 

1)  Off:

a)  All terminal dampers will maintain a 65% open position. Fans shall be disabled.

b)  If the zone requirement is heating, all single duct terminals shall maintain their damper position at 65%. Any zone controller servicing a parallel box shall fully close their dampers while the fan is operating. If local heat is available, the parallel fans shall start and local heat shall be enabled to maintain its unoccupied heating set point. The damper shall be modulated open to 65% after heating is no longer required.

2)  Cooling and Night Time Free Cooling (NTFC):

a)  If the zone requirement is none, then the zone controllers shall modulate their dampers to maintain their minimum cooling damper position or damper ventilation position if the supply air temp is between 65 and 75 F. During the NTFC mode the zone controller shall control between its occupied heating and cooling set points. During the cooling mode, the zone controller shall modulate its damper to its appropriate (occupied or unoccupied) cooling set point.

b)  If the zone requirement is cooling, then the zone controllers shall modulate their air dampers between their minimum and maximum cooling damper position to maintain their cooling set point. Parallel fans shall be disabled unless the damper has closed below the user adjustable fan-on minimum position (optional). In that case, the fan shall be energized to mix return air with the cold primary air in order to prevent "cold air dumping" from the diffusers. 

c)  If the zone requirement is heating, then the zone controllers shall modulate their dampers to maintain their minimum cooling damper position. Any zone controllers servicing single duct units with reheat capability shall maintain the greater of either the minimum cooling damper position or the specified reheat damper position. Zone controllers servicing parallel units shall enable their fans while the damper shall maintain its minimum cooling damper position.

3)  Vent:

a)  If the air source equipment is operating in a fan only mode to provide ventilation without mechanical heating or cooling, then the zone controllers shall maintain the user configured ventilation damper position.

4)  Heat:

a)  If the zone requirement is none, then the zone controller shall maintain its minimum heating damper position. Parallel fans shall be disabled and their air damper shall be modulated to maintain their minimum heating damper position. 

b)  If the zone requirement is cooling, then the zone controller shall modulate its damper to maintain its minimum heating damper position. Parallel fans shall be disabled. 

c)  If the zone requirement is heating, then the zone controllers shall modulate their air dampers between their minimum and maximum heating damper position to maintain their heating set point.

5)  Pressurization:

a)  If the zone requirement is none or cooling, then the zone controller shall maintain its maximum cooling damper position. Parallel fans shall be disabled.

b)  If the zone requirement is heating, and the zone controller has been enabled to provide local heating, then the zone controller shall modulate its damper to its maximum cooling damper position and enable its auxiliary heat. If local heat is not available, the damper shall still be modulated to maintain its maximum cooling damper position.

6)  Evacuation:

a)  During the Evacuation mode all terminal fans shall be disabled and all dampers shall close.

e.  Air source interface. The zoning system shall be capable of zone demand data coordination with a communicating rooftop. Setpoint and zone temperature information from the zones shall be shared with the rooftop controller so that the rooftop controller's error reduction calculations can determine the proper number of heating or cooling stages to operate in order to satisfy the system load.

1)  The zoning system shall have the capability of linking up to 32 zones to a single air source and determining system heating and cooling requirements.

2)  The zoning system shall be capable of providing a communication check of all associated controls and display device type as well as error conditions.

3)  The zoning system shall coordinate and exchange the flowing data as minimum: 

a)  Average zone temperature

b)  Average occupied zone temperature

c)  Average occupied and unoccupied heat/cool set points

d)  Occupancy status

f.  Space temperature and space temperature set points for use by the air source controller shall include a weighted factor, proportional to the size of the zone. 

g.  Only those zones with valid temperature readings shall be included.

h.  The zoning system shall provide periodic updates to the air source. 

i.  The zoning system shall obtain and support the following air source modes as a minimum: 

1)  Off

2)  Cooling

3)  Heating

4)  Night Time Free Cooling

5)  Ventilation

6)  Pressurization

7)  Evacuation

j.  The air source controller shall, through the Air Distribution System, bias its occupancy time schedules to provide optimization routines and occupant override.

k.  For those zoning systems that do not include inherent air source interface capacity, each zone shall independently determine the operational mode of the equipment through its associated duct temperature sensor mounted in the supply ductwork. If there is air source controller, then the system will assumed to be always On.

13.  HVAC Equipment Protection. The air sources controller shall be capable of monitoring the leaving air temperature to control stages in both the heating and cooling modes. It shall have the capability to shut down stages based on a rise or fall in leaving air temperature above or below adjustable or calculated values. Calculated supply air temperature requirements shall be based on error reduction calculations from reference zone data to determine the optimum supply air temperature to satisfy space requirements. The system shall provide protection from short cycling of heating and cooling by utilizing time guards and minimum run time configurations.

14.  Energy Conservation. 

a.  Load balancing from error reduction calculations that optimize staging.

b.  The locking out of mechanical heating or cooling modes based on configurable outside air temperature limits.

c.  Staggered start. The system shall intelligently start all equipment in a stagger start manner after a transition from unoccupied to occupied modes as well as power failure to reduce high peak power consumption on start-up.

d.  Peak Demand Limiting. Controllers in the system shall have the capability of being overridden by separate heating and cooling Peak Demand Limiting signals. Option/General purpose controller existing on the communications bus shall be able to send a demand limiting broadcast to reduce overall energy consumption and control on and off peak time kW usage

e.  Temperature compensated start. The zone controller shall be capable of supporting temperature compensated start with the air source. Prior to occupancy the zone controllers and Air Source shall work together to provide zone-by-zone temperature compensated conditioning. The air source will track the time required for recovery report the optimal start bias time to the zones prior to each occupied period so that the zone can start conditioning the space prior to occupancy.

15.  Abnormal Conditions. The proposed system shall include the ability to detect abnormal conditions, and to react to them automatically. A return to normal conditions shall also generate a return to normal notification and the system shall revert back to its original control scheme before the abnormal condition existed. The following abnormal terminal conditions shall automatically generate an alarm and the system shall take the following actions:

a.  If a space temperature sensor is determined by the zone controller to be invalid, the zone controller shall generate an alarm. During this condition, the zone damper will be positioned to either the minimum heating, minimum cooling or the configured ventilation damper position, based on the air source equipment operating mode.

b.  If a relative humidity sensor is determined by the zone controller to be invalid, the zone controller shall generate an alarm. 

c.  If an indoor air quality sensor is determined by the zone controller to be invalid, the zone controller shall generate an alarm, and disable its IAQ algorithm.

d.  System level demand coordination. If an air source controller is participating in demand coordination with other zones and loses communication with the associated zones, it shall generate an alarm. Likewise, any zone detecting a communication failure, will generate an alarm.

e.  Zone level demand coordination. If the system looses communication with one of the zones associated with that system the zoning system shall remove that zone temperature from its weighted averages. The zone controller shall continue to operate in a stand-alone mode.

f.  If the zoning system if configured to interface with the air source for  zone demand data coordination and that communication is broken, each zone controller shall determine the equipment operating mode based on the temperature of the primary air. The air source will be assumed to be always on.

B.  Controllers 

1.  General. The control system shall be available as a complete package with the required input sensors and devices readily available. Provide Building Controllers (BC), Advanced Application Controllers (AAC), Application Specific Controllers (ASC), and Sensors (SEN) as required to achieve performance specified in Controller Software Section. 

2.  Every device in the system which executes control logic and directly controls HVAC equipment must conform to a standard BACnet Device profile as specified in ANSI/ASHRAE 135, BACnet Annex L. Unless otherwise specified.

3.  BACnet. 

a.  Building Controllers (BCs). Each BC shall conform to BACnet Building Controller (B-BC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-BC in the BACnet Testing Laboratories (BTL) Product Listing.

b.  Advanced Application Controllers (AACs). Each AAC shall conform to BACnet Advanced Application Controller (B-AAC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-AAC in the BACnet Testing Laboratories (BTL) Product Listing.

c.  Application Specific Controllers (ASCs). Each ASC shall conform to BACnet Application Specific Controller (B-ASC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-ASC in the BACnet Testing Laboratories (BTL) Product Listing.

d.  BACnet Communication. 

1)  Each BC shall reside on or be connected to a BACnet network using ISO 8802-3 (Ethernet) Data Link/Physical layer protocol and BACnet/IP addressing.

2)  BACnet routing shall be performed by BCs or other BACnet device routers as necessary to connect BCs to networks of AACs and ASCs.

3)  Each AAC shall reside on a BACnet network using ISO 8802-3 (Ethernet) Data Link/Physical layer protocol with BACnet/IP addressing, or it shall reside on a BACnet network using the MS/TP Data Link/Physical layer protocol.

4)  Each ASC shall reside on a BACnet network using the MS/TP Data Link/Physical layer protocol.

4.  Communication. 

a.  Service Port. Each controller shall provide a service communication port for connection to a Portable Operator's Terminal. Connection shall be extended to space temperature sensor ports where shown on drawings. 

b.  Signal Management. BC and ASC operating systems shall manage input and output communication signals to allow distributed controllers to share real and virtual object information and to allow for central monitoring and alarms.

c.  Data Sharing. Each BC and AAC shall share data as required with each networked BC and AAC.

d.  Stand-Alone Operation. Each piece of equipment shall be controlled by a single controller to provide stand-alone control in the event of communication failure. All I/O points specified for a piece of equipment shall be integral to its controller. Provide stable and reliable stand-alone control using default values or other method for values normally read over the network. 

5.  Environment. Controller hardware shall be suitable for anticipated ambient conditions. 

a.  Controllers used outdoors or in wet ambient conditions shall be mounted in waterproof enclosures and shall be rated for operation at -29°C to 60°C (-20°F to 140°F).

b.  Controllers used in conditioned space shall be mounted in dust-protective enclosures and shall be rated for operation at 0°C to 50°C (32°F to 120°F).

6.  Keypad. Where specified provide a local keypad and display for each BC and ASC. Operator shall be able to use keypad to view and edit data. Keypad and display shall require password to prevent unauthorized use. If the manufacturer does not normally provide a keypad and display for each BC and ASC, provide the software and any interface cabling needed to use a laptop computer as a Portable Operator's Terminal for the system. 

7.  Serviceability.

a.  Controllers shall have diagnostic LEDs for power, communication, and processor.

b.  Wires shall be connected to a field-removable modular terminal strip or to a termination card connected by a ribbon cable.

c.  All controllers in the system shall continually check its processor and memory circuit status and shall generate an alarm on abnormal operation. System shall continuously check controller network and generate alarm for each controller that fails to respond.

8.  Memory.

a.  Controller memory shall support operating system, database, and programming requirements.

b.  Each controller in the system shall use nonvolatile memory providing indefinite storage of BIOS, application programming, and all configuration data in the event of power loss. 

9.  Immunity to Power and Noise. Controllers shall be able to operate at 90% to 110% of nominal voltage rating and shall perform an orderly shutdown below 80% nominal voltage. Operation shall be protected against electrical noise of 5 to 120 Hz and from keyed radios up to 5 W at 1 m (3 ft).

10.  Zone Controller (ZC). Defined as Application Specific Controllers (ASC) shall be capable of independent zone control or function as part of the zoning system to achieve performance as specified for zone control in Controller Software Section. 

a.  Input and output devices shall be wired to "quick-connect plug type" terminals to facilitate removal of the module without disconnecting wiring from the plug type terminal.

b.  ZC shall have an integrated brushless actuator and be capable of operating zone dampers as well as parallel fan powered terminal boxes.

c.  ZC shall be capable of controlling supplemental heat or auxiliary heat sources, including fan control, when required at the zone level.

d.  The zone controller shall have the capability to support adjustable minimum and maximum damper positions.

e.  ZC shall be capable of reading an analog signal from a CO2 sensor or other sensor measuring volatile contaminants, or relative humidity and provide DCV at the zone by calculating a DCV damper position and participate in system DCV operation with the air source.

11.  Bypass Controller. Defined as Application Specific Controllers (ASC) shall be capable of reading supply static pressure and controlling the bypass damper (or a VFD speed control output) to maintain the supply static set point. This operation shall be provided when operating within a zoning system application, as specified for bypass control in Controller Software Section or in a stand-alone mode.

a.  Input and output devices shall be wired to "quick-connect plug type" terminals to facilitate removal of the module without disconnecting wiring from the plug type terminal.

b.  The controller shall contain an onboard pressure sensor to measure duct static pressure. The sensor measuring range shall be from 0.0 to 2.0 inches H2O.

c.  Bypass Controller shall have an integrated brushless actuator providing a minimum of 35 in/lbs of torque and be capable of operating a bypass damper. The direction of rotation shall be reversible in the field to accommodate field supplied bypass damper assemblies.

d.  Bypass Controller shall provide an analog output signal for an external actuator or to control the speed of a variable frequency drive (VFD).

12.  Communicating Room Space Temperature (SPT)

a.  Shall have integrated, easy-to-read LCD on display. Able to display space temperature, outside air temperature, heating setpoint, cooling setpoint, and local override (after hours occupancy), time

b.  Shall have Precise 10K ohm thermistor with + 0.36ºF (0.2ºC) standard accuracy and less than 0.18ºF (0.01ºC) drift over a ten year span - requires no maintenance or re-calibration 

c.  Shall allow zone setpoints adjustment by pressing the Warmer or Cooler buttons 

d.  Shall have a hidden communication port allows a laptop computer or a handheld keypad to commission and maintain the connected equipment easily 

e.  Shall allow multiple SPT sensors to be daisy-chained to one controller for temperature averaging or high/low select control 

f.  Shall have ability to mount on a standard 2" x 4" electrical box for easy installation

1.1.1.1.2 VVT Controllers Factory: Zone and Bypass

1.2  boofoo

A.  Controller Software VVT
1.  Building and energy management application software shall reside and operate in system controllers. Applications shall be configurable through the operator workstation, web browser interface, or engineering workstation.

2.  Memory and System Time. All controllers shall have a Non-Volatile Memory providing indefinite storage of application and configuration data. The system must have an ability to maintain time, and automatically correct for daylight savings time and leap year adjustments. In the event of power failure or user generated power cycle, all system components must automatically updated with current time and date from a network Time Sync device. The controller shall also have the capability of changing occupancy mode by reading a set of discrete, dry contacts controlled by an external time clock.
3.  Stand alone capability. All controllers shall be capable of providing all control functions of the HVAC system without the use of a computer. The controllers shall include the inherent capability to access the system control selections as well as to monitor system performance by means of a communicating network with a PC and EMS software program.

4.  System Security. 

a.  Other hand held or wall mounted local interface device that allow configuration access shall be password protected with minimum of two levels of security. Level one shall provide limited access to controller operational parameters and level two shall provide full access to controller operational and configuration parameters. 

5.  Scheduling. 

a.  System shall provide the following schedule options as a minimum: 

b.  Weekly. Provide separate schedules for each day of the week. Each schedule shall be able to include up to 5 occupied periods (5 start-stop pairs or 10 events).

c.  Exception. Operator shall be able to designate an exception schedule for each of the next 365 days. After an exception schedule has executed, system shall discard and replace exception schedule with standard schedule for that day of the week.

d.  Holiday. Operator shall be able to define 24 special or holiday schedules of varying length on a scheduling calendar that repeats each year.
6.  Remote Communication. System shall automatically contact operator workstation or server on receipt of critical alarms.

7.  Sequencing. Application software shall sequence chillers, boilers, and pumps as specified in Sequence of Operations for HVAC Controls.

8.  PID Control. System shall provide direct- and reverse-acting PID (proportional-integral-derivative) algorithms. Each algorithm shall have anti-windup and selectable controlled variable, setpoint, and PID gains. Each algorithm shall calculate a time-varying analog value that can be used to position an output or to stage a series of outputs.

9.  Staggered Start. System shall stagger controlled equipment restart after power outage. Operator shall be able to adjust equipment restart order and time delay between equipment restarts.

10.  Anti-Short Cycling. Binary output objects shall be protected from short cycling by means of preconfigured minimum on-time and off-time settings, customized for the specific requirements of the application.

11.  On and Off Control with Differential. System shall provide direct- and reverse-acting on and off algorithms with adjustable differential to cycle a binary output based on a controlled variable and setpoint.

12.  Zoning system compatible with constant volume air source (Variable Volume/Variable Temperature) (VVT). The zoning system shall be compatible with constant volume air source and consist of programmable, multiple communicating Zone Controllers and a Bypass Controller. The system shall also include a complete array of input and output devices. The system shall provide full control of HVAC heating and cooling equipment in a multiple zone application. The zoning system shall be capable of operating as a stand-alone system or networked with multiple systems to communicating air source controllers. 

a.  Zone control. Each zone shall be capable of monitoring space conditions and providing the correct amount of conditioned air to satisfy the space load. Each zone shall be capable of the following:

1)  Space temperatures control. To maintain individual heating and cooling set points.

2)  Relative Humidity/Air Quality (DCV). Each zone shall be capable of maintaining space relative humidity set point or air quality set point (zone level demand control ventilation) as defined in ASHRAE 62-1989 (including Addendum 62a-1990).

3)  Demand coordination. Each zone shall be capable of zone demand data coordination with other zones in the system.  

b.  Static pressure control. The zoning system shall be capable of maintaining a user adjustable supply air duct static pressure set point. 
1)  The Bypass controller shall additionally provide the capability to increase system airflow during conditions when the temperature of the supply air from the equipment is approaching the limits of operation. In these cases, the Bypass controller shall raise the static pressure setpoint to a user configurable maximum limit in order to increase the system airflow during these conditions. 
2)  The Bypass control shall contain the ability to monitor the bypass damper movement (or VFD speed) and automatically adjust the setpoint control band and/or hysteresis in order to provide stability and prevent premature actuator failure. 

c.  Air source control. Shall control all associated HVAC rooftop equipment functions, and be capable of stand-alone or networked operation. The resident algorithms shall use error reduction logic as designated in ASHRAE standard 90.1 to provide temperature control and lower energy usage. The Air source shall be capable of zone demand data coordination with the associated zones. 

d.  System Terminal Modes. Each air terminal mode shall be based on the current air source mode, terminal type, space temperature, and the current temperature set points. 

1)  Off:

a)  All terminal dampers will maintain a 65% open position. Fans shall be disabled.

b)  If the zone requirement is heating, all single duct terminals shall maintain their damper position at 65%. Any zone controller servicing a parallel box shall fully close their dampers while the fan is operating. If local heat is available, the parallel fans shall start and local heat shall be enabled to maintain its unoccupied heating set point. The damper shall be modulated open to 65% after heating is no longer required.

2)  Cooling and Night Time Free Cooling (NTFC):

a)  If the zone requirement is none, then the zone controllers shall modulate their dampers to maintain their minimum cooling damper position or damper ventilation position if the supply air temp is between 65 and 75 F. During the NTFC mode the zone controller shall control between its occupied heating and cooling set points. During the cooling mode, the zone controller shall modulate its damper to its appropriate (occupied or unoccupied) cooling set point.
b)  If the zone requirement is cooling, then the zone controllers shall modulate their air dampers between their minimum and maximum cooling damper position to maintain their cooling set point. Parallel fans shall be disabled unless the damper has closed below the user adjustable fan-on minimum position (optional). In that case, the fan shall be energized to mix return air with the cold primary air in order to prevent “cold air dumping” from the diffusers. 
c)  If the zone requirement is heating, then the zone controllers shall modulate their dampers to maintain their minimum cooling damper position. Any zone controllers servicing single duct units with reheat capability shall maintain the greater of either the minimum cooling damper position or the specified reheat damper position. Zone controllers servicing parallel units shall enable their fans while the damper shall maintain its minimum cooling damper position.
3)  Vent:

a)  If the air source equipment is operating in a fan only mode to provide ventilation without mechanical heating or cooling, then the zone controllers shall maintain the user configured ventilation damper position.
4)  Heat:

a)  If the zone requirement is none, then the zone controller shall maintain its minimum heating damper position. Parallel fans shall be disabled and their air damper shall be modulated to maintain their minimum heating damper position. 

b)  If the zone requirement is cooling, then the zone controller shall modulate its damper to maintain its minimum heating damper position. Parallel fans shall be disabled. 
c)  If the zone requirement is heating, then the zone controllers shall modulate their air dampers between their minimum and maximum heating damper position to maintain their heating set point.
5)  Pressurization:

a)  If the zone requirement is none or cooling, then the zone controller shall maintain its maximum cooling damper position. Parallel fans shall be disabled.

b)  If the zone requirement is heating, and the zone controller has been enabled to provide local heating, then the zone controller shall modulate its damper to its maximum cooling damper position and enable its auxiliary heat. If local heat is not available, the damper shall still be modulated to maintain its maximum cooling damper position.

6)  Evacuation:

a)  During the Evacuation mode all terminal fans shall be disabled and all dampers shall close.
13.  Air source interface. The zoning system shall be capable of zone demand data coordination with a communicating rooftop. Setpoint and zone temperature information from the zones shall be shared with the rooftop controller so that the rooftop controller’s error reduction calculations can determine the proper number of heating or cooling stages to operate in order to satisfy the system load.
a.  The zoning system shall have the capability of linking up to 32 zones to a single air source and determining system heating and cooling requirements.

b.  The zoning system shall be capable of providing a communication check of all associated controls and display device type as well as error conditions.

c.  The zoning system shall coordinate and exchange the flowing data as minimum: 

1)  Average zone temperature

2)  Average occupied zone temperature

3)  Average occupied and unoccupied heat/cool set points

4)  Occupancy status

d.  Space temperature and space temperature set points for use by the air source controller shall include a weighted factor, proportional to the size of the zone. 

e.  Only those zones with valid temperature readings shall be included.

f.  The zoning system shall provide periodic updates to the air source. 

g.  The zoning system shall obtain and support the following air source modes as a minimum: 

1)  Off

2)  Cooling

3)  Heating

4)  Night Time Free Cooling
5)  Ventilation
6)  Pressurization

7)  Evacuation
h.  The air source controller shall, through the Air Distribution System, bias its occupancy time schedules to provide optimization routines and occupant override.

i.  For those zoning systems that do not include inherent air source interface capacity, each zone shall independently determine the operational mode of the equipment through its associated duct temperature sensor mounted in the supply ductwork. If there is air source controller, then the system will assumed to be always On.

14.  HVAC Equipment Protection. The air sources controller shall be capable of monitoring the leaving air temperature to control stages in both the heating and cooling modes. It shall have the capability to shut down stages based on a rise or fall in leaving air temperature above or below adjustable or calculated values. Calculated supply air temperature requirements shall be based on error reduction calculations from reference zone data to determine the optimum supply air temperature to satisfy space requirements. The system shall provide protection from short cycling of heating and cooling by utilizing time guards and minimum run time configurations.

15.  Energy Conservation. 

a.  Load balancing from error reduction calculations that optimize staging.

b.  The locking out of mechanical heating or cooling modes based on configurable outside air temperature limits.

c.  Staggered start. The system shall intelligently start all equipment in a stagger start manner after a transition from unoccupied to occupied modes as well as power failure to reduce high peak power consumption on start-up.

d.  Peak Demand Limiting. Controllers in the system shall have the capability of being overridden by separate heating and cooling Peak Demand Limiting signals. Option/General purpose controller existing on the communications bus shall be able to send a demand limiting broadcast to reduce overall energy consumption and control on and off peak time kW usage

e.  Temperature compensated start. The zone controller shall be capable of supporting temperature compensated start with the air source. Prior to occupancy the zone controllers and Air Source shall work together to provide zone-by-zone temperature compensated conditioning. The air source will track the time required for recovery report the optimal start bias time to the zones prior to each occupied period so that the zone can start conditioning the space prior to occupancy.
16.  Abnormal Conditions. The proposed system shall include the ability to detect abnormal conditions, and to react to them automatically. A return to normal conditions shall also generate a return to normal notification and the system shall revert back to its original control scheme before the abnormal condition existed. The following abnormal terminal conditions shall automatically generate an alarm and the system shall take the following actions:

a.  If a space temperature sensor is determined by the zone controller to be invalid, the zone controller shall generate an alarm. During this condition, the zone damper will be positioned to either the minimum heating, minimum cooling or the configured ventilation damper position, based on the air source equipment operating mode.

b.  If a relative humidity sensor is determined by the zone controller to be invalid, the zone controller shall generate an alarm. 

c.  If an indoor air quality sensor is determined by the zone controller to be invalid, the zone controller shall generate an alarm, and disable its IAQ algorithm.

d.  System level demand coordination. If an air source controller is participating in demand coordination with other zones and loses communication with the associated zones, it shall generate an alarm. Likewise, any zone detecting a communication failure, will generate an alarm.
e.  Zone level demand coordination. If the system looses communication with one of the zones associated with that system the zoning system shall remove that zone temperature from its weighted averages. The zone controller shall continue to operate in a stand-alone mode.

f.  If the zoning system if configured to interface with the air source for  zone demand data coordination and that communication is broken, each zone controller shall determine the equipment operating mode based on the temperature of the primary air. The air source will be assumed to be always on.
B.  Controllers VVT
1.  General. The control system shall be available as a complete package with the required input sensors and devices readily available. Provide Building Controllers (BC), Advanced Application Controllers (AAC), Application Specific Controllers (ASC), and Sensors (SEN) as required to achieve performance specified in Controller Software Section. 

2.  Every device in the system which executes control logic and directly controls HVAC equipment must conform to a standard BACnet Device profile as specified in ANSI/ASHRAE 135, BACnet Annex L. Unless otherwise specified.
3.  BACnet. 

a.  Building Controllers (BCs). Each BC shall conform to BACnet Building Controller (B-BC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-BC in the BACnet Testing Laboratories (BTL) Product Listing.

b.  Advanced Application Controllers (AACs). Each AAC shall conform to BACnet Advanced Application Controller (B-AAC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-AAC in the BACnet Testing Laboratories (BTL) Product Listing.

c.  Application Specific Controllers (ASCs). Each ASC shall conform to BACnet Application Specific Controller (B-ASC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-ASC in the BACnet Testing Laboratories (BTL) Product Listing.

d.  BACnet Communication. 

1)  Each BC shall reside on or be connected to a BACnet network using ISO 8802-3 (Ethernet) Data Link/Physical layer protocol and BACnet/IP addressing.

2)  BACnet routing shall be performed by BCs or other BACnet device routers as necessary to connect BCs to networks of AACs and ASCs.

3)  Each AAC shall reside on a BACnet network using ISO 8802-3 (Ethernet) Data Link/Physical layer protocol with BACnet/IP addressing, or it shall reside on a BACnet network using the MS/TP Data Link/Physical layer protocol.

4)  Each ASC shall reside on a BACnet network using the MS/TP Data Link/Physical layer protocol.
4.  Communication. 

a.  Service Port. Each controller shall provide a service communication port for connection to a Portable Operator's Terminal. Connection shall be extended to space temperature sensor ports where shown on drawings. 

b.  Signal Management. BC and ASC operating systems shall manage input and output communication signals to allow distributed controllers to share real and virtual object information and to allow for central monitoring and alarms.

c.  Data Sharing. Each BC and AAC shall share data as required with each networked BC and AAC.

d.  Stand-Alone Operation. Each piece of equipment shall be controlled by a single controller to provide stand-alone control in the event of communication failure. All I/O points specified for a piece of equipment shall be integral to its controller. Provide stable and reliable stand-alone control using default values or other method for values normally read over the network. 

5.  Environment. Controller hardware shall be suitable for anticipated ambient conditions. 

a.  Controllers used outdoors or in wet ambient conditions shall be mounted in waterproof enclosures and shall be rated for operation at -29°C to 60°C (-20°F to 140°F).

b.  Controllers used in conditioned space shall be mounted in dust-protective enclosures and shall be rated for operation at 0°C to 50°C (32°F to 120°F).

6.  Keypad. Where specified provide a local keypad and display for each BC and ASC. Operator shall be able to use keypad to view and edit data. Keypad and display shall require password to prevent unauthorized use. If the manufacturer does not normally provide a keypad and display for each BC and ASC, provide the software and any interface cabling needed to use a laptop computer as a Portable Operator's Terminal for the system. 

7.  Serviceability.

a.  Controllers shall have diagnostic LEDs for power, communication, and processor.

b.  Wires shall be connected to a field-removable modular terminal strip or to a termination card connected by a ribbon cable.

c.  All controllers in the system shall continually check its processor and memory circuit status and shall generate an alarm on abnormal operation. System shall continuously check controller network and generate alarm for each controller that fails to respond.

8.  Memory.

a.  Controller memory shall support operating system, database, and programming requirements.

b.  Each controller in the system shall use nonvolatile memory providing indefinite storage of BIOS, application programming, and all configuration data in the event of power loss. 

9.  Immunity to Power and Noise. Controllers shall be able to operate at 90% to 110% of nominal voltage rating and shall perform an orderly shutdown below 80% nominal voltage. Operation shall be protected against electrical noise of 5 to 120 Hz and from keyed radios up to 5 W at 1 m (3 ft).

10.  Factory Mounted Zone Controller (ZC). Defined as Application Specific Controllers (ASC) shall be capable of independent zone control or function as part of the zoning system to achieve performance as specified for zone control in Controller Software Section. 

a.  Input and output devices shall be wired to “quick-connect plug type” terminals to facilitate removal of the module without disconnecting wiring from the plug type terminal.

b.  ZC shall have an integrated brushless actuator and be capable of operating zone dampers as well as parallel fan powered terminal boxes.

c.  ZC shall be capable of controlling supplemental heat or auxiliary heat sources, including fan control, when required at the zone level.

d.  The zone controller shall have the capability to support adjustable minimum and maximum damper positions.

e.  ZC shall be capable of reading an analog signal from a CO2 sensor or other sensor measuring volatile contaminants, or relative humidity and provide DCV at the zone by calculating a DCV damper position and participate in system DCV operation with the air source.

11.  Factory Mounted Bypass Controller. Defined as Application Specific Controllers (ASC) shall be capable of reading supply static pressure and controlling the bypass damper (or a VFD speed control output) to maintain the supply static set point. This operation shall be provided when operating within a zoning system application, as specified for bypass control in Controller Software Section or in a stand-alone mode.

a.  Input and output devices shall be wired to “quick-connect plug type” terminals to facilitate removal of the module without disconnecting wiring from the plug type terminal.
b.  The controller shall contain an onboard pressure sensor to measure duct static pressure. The sensor measuring range shall be from 0.0 to 2.0 inches H2O.
c.  Bypass Controller shall have an integrated brushless actuator providing a minimum of 35 in/lbs of torque and be capable of operating a bypass damper. The direction of rotation shall be reversible in the field to accommodate field supplied bypass damper assemblies.
d.  Bypass Controller shall provide an analog output signal for an external actuator or to control the speed of a variable frequency drive (VFD).

12.  Communicating Room Space Temperature (SPT)
a.  Shall have integrated, easy-to-read LCD on display. Able to display space temperature, outside air temperature, heating setpoint, cooling setpoint, and local override (after hours occupancy), time
b.  Shall have Precise 10K ohm thermistor with + 0.36ºF (0.2ºC) standard accuracy and less than 0.18ºF (0.01ºC) drift over a ten year span – requires no maintenance or re-calibration 

c.  Shall allow zone setpoints adjustment by pressing the Warmer or Cooler buttons 

d.  Shall have a hidden communication port allows a laptop computer or a handheld keypad to commission and maintain the connected equipment easily 

e.  Shall allow multiple SPT sensors to be daisy-chained to one controller for temperature averaging or high/low select control 
f.  Shall have ability to mount on a standard 2” x 4” electrical box for easy installation

1.1.1.1.3 VVT Demand Controlled Ventilation

1.3  boofoo

A.  Ventilation Sensors: Wall-Mounted Combination Sensors

1.  Wall-mounted combination sensors shall contain a space temperature sensor and Carbon Dioxide (CO2) sensors in a single, decorative housing. The CO2 sensor shall use single-beam absorption infrared diffusion technology (non-dispersive infrared), and shall have integral programming to perform automatic baseline calibration without user interface. The recommended manual recalibration period shall not be less than five years. 

2.  Other sensors features shall include:

a.  Operating conditions: 60 to 90ºF (15 to 32ºC), and 0 to 95% RH, non-condensing.

b.  Power supply: 18-30 VAC, 50/60 Hz [18-42 VDC polarity protected].

c.  CO2 sampling method: diffusion.

d.  CO2 sensor output: 4 to 20 ma or 0 to 10-Volt signal.

e.  CO2 measurement range: 0-2,000 PPM.

f.  Sensitivity: ±20 PPM.

g.  Accuracy: ±100 PPM at 60 to 90ºF (15 to 32ºC); and 760 mmHg.

h.  CO2 sensor calibration: single point calibration via push button and LED.

i.  Space temperature sensor: 10K-ohm ±2% at 77ºF (25ºC) thermistor with pushbutton override [and a temperature setpoint adjustment potentiometer].

j.  Combination sensors shall be provided with the manufacturer's recommended Carbon Dioxide calibration kit. The quantity shall be suitable to initially calibrate each project sensor.

B.  Ventilation Sensors: Wall-Mounted Carbon Dioxide Sensors

1.  Carbon dioxide (CO2) sensors shall be manufactured in a decorative, wall-mounted housing. The CO2 sensor shall use single- or dual-beam absorption infrared diffusion technology (non-dispersive infrared), and shall have integral programming to perform automatic baseline calibration without user interface. The recommended manual recalibration period shall not be less than five years. Sensors shall be equipped with an LED display. 

2.  Other features of wall-mounted Carbon Dioxide sensors shall include:

a.  Operating conditions: 60 to 90ºF (15 to 32ºC), and 0 to 95% RH, non-condensing

b.  Power supply: 18-30 VAC, 50/60 Hz half-wave rectified [18--42 VDC polarity protected]

c.  CO2 sampling method: diffusion or flow-through.

d.  CO2 sensor output: 4 to 20 ma or 0 to 10-volt signal.

e.  CO2 measurement range: 0-10,000 PPM.

f.  Setpoint: adjustable.

g.  Sensitivity: ±10 PPM.

h.  Accuracy: ±50 PPM (0-2000 PPM), ±5% of reading (2000-10,000 PPM).

i.  CO2 sensor calibration: single point calibration via push button and LED

j.  Relay contacts: normally open or normally closed, 2 amps at 24 vac.

k.  Carbon Dioxide sensors shall be provided with the manufacturer's recommended calibration kit. The quantity shall be suitable to initially calibrate each sensor provided for the project.

C.  Ventilation Sensors: Duct-Mounted Carbon Dioxide Sensors 

1.  Carbon Dioxide (CO2) sensors for duct-mounted applications shall be identical to the wall-mounted sensors specified above except as described below.

2.  The CO2 sensor shall be mounted in an enclosed aspirator box that mounts directly to the duct.  The aspirator box shall be equipped with an induction tube to direct a side-stream of air from the duct through the CO2 sensor.  A hinged, clear access door shall be installed on the front of the aspirator box to permit access to the sensor and to permit viewing the sensor without opening the door.

3.  CO2 sensors for duct-mounted applications shall be designed for flow-through sampling.

D.  Controller Software 

1.  Demand Control Ventilation (DCV). The zone shall be capable of reading an analog signal from a CO2 sensor or other sensor measuring volatile contaminants, or relative humidity and provide DCV at the zone by calculating a DCV damper position and participate in system DCV operation with the air source

a.  System DCV (System Level).The zoning system shall have the ability to collect the DCV value from any or all of the zone controllers in the system. These values may be the average or the highest sensor value which will be transmitted to an air source controller's analog DCV sensor input. The air sources configured DCV routine may perform the appropriate actions to reduce CO2 concentration at the reporting zones. The system shall be capable of maintaining a ventilation setpoint through a DCV algorithm in conjunction with zone to fulfill the requirements of ASHRAE standard, 62-1989 "Ventilation For Acceptable Indoor Air Quality" (including Addendum 62a-1990)..

b.  Local DCV (Zone Level). Each zone shall be capable of reading an analog signal from a CO2 sensor or other sensors measuring volatile contaminants and maintaining a ventilation setpoint through a DCV algorithm in conjunction with system controller to fulfill the requirements of ASHRAE standard, 62-1989 "Ventilation For Acceptable Indoor Air Quality" (including Addendum 62a-1990). The zone shall calculate a DCV damper position for the zone based on an error reduction calculation. When the DCV damper position value is greater than temperature control damper position the DCV damper position shall be used to position the damper.  System heating and cooling and installation

1.1.1.1.4 VVT Demand Limit

1.4  boofoo

A.  Demand Limiting. 

1.  System shall monitor building power consumption from building power meter pulse generator signals or from building feeder line watt transducer or current transformer.

2.  When power consumption exceeds adjustable levels, system shall automatically adjust set points, de-energize low-priority equipment, and take other programmatic actions to reduce demand as specified in Sequence of Operations for HVAC Controls. When demand drops below adjustable levels, system shall restore loads as specified.

3.  The controller shall be capable of providing separate heating and cooling demand control utilizing two independent demand inputs.

1.1.1.1.5 VVT Zone Dampers

1.5  boofoo

A.  Zone Dampers. Each Zone Damper shall include:

1.  A motorized damper assembly constructed of 24 gage galvanized iron with blade of 20 gage.

2.  Blade operation providing full modulation from open to closed position.

3.  The ability to operate in a controlling/link arrangement, where the controlling damper is operated by the zone controller. 

4.  The zone controller shall provide a separate 0-10 vdc output proportional to the controlling damper position (available only if no modulating heat is used) to be used to link additional zone dampers. These additional dampers will track the position of the controlling damper and modulate to the same position as the controlling damper. The number of additional dampers are dependent upon the load of each field supplied damper actuator and the external output drive capability.

5.  Round dampers shall have elliptical blades with a seal around the entire damper blade edge. Rectangular dampers shall have fully sealed edges.

6.  A duct temperature sensor shall be an integral part of the damper assembly.

2.0 Sequences of Operation

2.1 Sequence of Operation for 
Prepared By: 
Page 1 of 17

