## Slide 1
APPLICATION & dESIGN
Return air pmv kits

## Slide 2
Table of Contents
Application & design – Return air pmv kits
    Intro
        Return Air PMV Kit System Schematic
        PMV Application Approval Process Flow
        Field-Provided Scope
        Available Combinations
  Decision-Making Tree
        Key Questions
        PMV Checklist
        Entering Air Temperatures (EATs)
  Application Scenarios
    “Medium-Sized” AHUs
    Custom Form Factors / Dimensions
    Large AHUs
    Benefits
  Deep-Dive
    Kit Sizes
    DN Code Settings
    Control Wiring – Required Connections
    Control Wiring – Optional Connections
    Factory-Installed Relay Information
Course objectives & Table of contents

## Slide 3
Return Air PMV Kit System Schematic
introduction
Refrigerant piping
Control wiring (Field installed)
Temperature sensor wiring
Notes: The PMV Kits can be applied to “build-your-own” AHU with VRF expansion valve and IDU controls; behaves essentially like a conventional High Static Ducted TC VRF IDU.
Toshiba Carrier provides 2 pieces: PMV Kit & PMV Controller; the AHU and all inside “the box” are additional FIELD-SOURCED material. This essentially makes a high-static 1:1 Heat Pump in this schematic.

## Slide 4
PMV Application Approval Process Flow
introduction
Distribution Sales Engineer (external)
Select AHU based on Airside requirements:
  CFM & ESP
  Cooling & Heating Capacities
Send the performance summary to VRF Product Group
Send expected Control Scheme to VRF Product Group
VRF Product Group (internal)
Investigate potential PMV Combos that meet Airside & Toshiba requirements using PMV Checklist.
If viable, approval via email:
  Contingent upon PMV Checklist (highlighted values)
  Include Vroom selection file for double-check of combos and BOM
Distributor Sales Engineer (external)
Source custom Heat Pump coils based on PMV Checklist requirements
Order equipment: Airside, Toshiba VRF, Custom Coils, Misc. Controls
Price & Coordinate Additional Labor & Misc. Parts for:
  Installing Custom Coil(s)
  Installing PMV Kit Piping
  Installing PMV Kit-Controller Wiring
Notes: These kits are very exciting and flexible. However, these are an applied product that require additional care, parts sourcing, & coordination.
Please adhere to this process to obtain factory approval from Toshiba VRF. Please do not sell PMV Kits without approval email from VRF product group.
Please also refer to PMV Kit Installation & Startup training PPT for details.

## Slide 5
Field-Provided Scope
introduction
If PMV Application is approved by the factory, the following items will need to be sourced, installed, and “owned” by Sales Engineer in distribution & their contractors:
Parts:
  Custom Dx Coil(s) per our specifications, rated for Heat Pump duty with R-410A
  Misc. parts
    Wire for PMVs
    Wire for coil sensors
    External controls for start/stop
    Misc. wiring as needed (i.e. fan prover, float switches, CNs, etc.)
Labor:
  Refrigerant Piping for Custom AHU & PMV Kit
    Piping from PMV to coil inlet / distributor
    Piping from coil gas header to stub-out
  Mount Coil Sensor Holders & Sensors
  Wiring
    208/230V 1ph power to Controller (like “normal” VRF IDU)
    Coil Sensors to PMV Controller
    PMV to PMV Controller
    Misc. interlocks as needed (i.e. fan proof, float switches to CN inputs)
Note: this is not an all-inclusive list. Please coordinate project specifics with Carrier Product group.
Notes: Please reiterate that this is a highly APPLIED product and requires factory checks and approval for each application. Then, additional equipment and labor must be field-provided and coordinated.

## Slide 6
Available Combinations – Normal Coils
introduction
DX-coil type |  |  | Normal (Single-Circuit) |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Capacity | Capacity Code |  | 012 | 015 | 018 | 021 | 024 | 030 | 036 | 042 | 048 | 060 | 072 | 096 | 168 | 192 | 336 | 384
 | Tonnage |  | 1 | 1.25 | 1.5 | 1.75 | 2 | 2.5 | 3 | 3.5 | 4 | 5 | 6 | 8 | 14 | 16 | 28 | 32
Controller | TCB-IFDA1GUL |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dx-PMV Kit | RBM-A0121GUL | 1 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | RBM-A0301GUL | 1.3 |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  | 1.5 |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  | 1.8 |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  | 
 |  | 2 |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  | 
 |  | 2.5 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  | 
 | RBM-A0601GUL | 3 |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 
 |  | 3.5 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 
 |  | 4 |  |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  | 
 |  | 5 |  |  |  |  |  |  |  |  |  | 1 |  |  |  |  |  | 
 | RBM-A0961GUL | 6 |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  |  | 
 |  | 8 |  |  |  |  |  |  |  |  |  |  |  | 1 |  |  |  | 
 | RBM-A1921GUL | 14 |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | 2 | 
 |  | 16 |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 |  | 2
Applied | Mixing with normal FCU |  | Yes with PMV Kits 8-ton or less. |  |  |  |  |  |  |  |  |  |  |  | No |  |  | 
 | Group Control |  | Yes |  |  |  |  |  |  |  |  |  |  |  | No |  |  | 
Outdoor Unit | SMMS-e (Heat Pump) |  | Yes |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | 
 | SHRM-e (Heat Recovery) |  | Yes |  |  |  |  |  |  |  |  |  |  |  | No |  |  | 
 | MCY (Single-Phase Heat Pump 3,4,5 ton) |  | Yes |  |  |  |  |  |  |  |  |  | No |  | No |  |  | 
Normal (Single-Circuit) Coil
Notes: Note break at 8 tons

## Slide 7
Available Combinations – Interlaced & Face-Split Coils
introduction
Interlaced Coil
Face-Split Coil
DX-coil type |  |  | Interlaced or Face-Split |  |  |  |  |  |  | 
Capacity | Capacity Code |  | 120 | 144 | 216 | 240 | 264 | 288 | 336 | 384
 | Tonnage |  | 10 | 12 | 18 | 20 | 22 | 24 | 28 | 32
Controller | TCB-IFDA1GUL |  | 2 | 2 | 3 | 3 | 3 | 3 | 2 | 2
 | RBM-A0601GUL | 5 | 2 |  |  |  |  |  |  | 
 | RBM-A0961GUL | 6 |  | 2 | 3 | 2 | 1 |  |  | 
 |  | 8 |  |  |  | 1 | 2 | 3 |  | 
 | RBM-A1921GUL | 14 |  |  |  |  |  |  | 2 | 
 |  | 16 |  |  |  |  |  |  |  | 2
Applied | Mixing with normal FCU |  | No |  |  |  |  |  |  | 
 | Group Control |  | No |  |  |  |  |  |  | 
Outdoor Unit | SMMS-e (Heat Pump) |  | Yes |  |  |  |  |  |  | 
 | SHRM-e (Heat Recovery) |  | No |  |  |  |  |  |  | 
 | MCY (Single-Phase Heat Pump 3,4,5 ton) |  | No |  |  |  |  |  |  | 

## Slide 8
Decision-making tree
Key Questions
  Will a “normal” Toshiba Carrier IDU suffice?
    If yes, go with that first.
  Is Heat Recovery required?
    If yes, 8 tons max per AHU w PMV kit.
  Mixing with “normal” Toshiba Carrier IDUs?
    If yes, 8 tons max per AHU w PMV kit.
  Can the project support additional work required?
    Additional field-provided parts, labor, and project management.
  Can we “meet the numbers”?
    See PMV Checklist…
Notes: Look for simplest solution first. If conventional VRF ducted IDUs can be used, consider these first.

## Slide 9
Decision-making tree
PMV Checklist
  The PMV Checklist is used by Carrier VRF Product Group in approval process
  Yellow cells are critical metrics that are required for approval
  Green cells are metrics verified within range
  Orange cells are FYI on PMV & Controller Kit quantities
Job Name | Example |  | 
Job Location | Memphis, TN |  | 
System Tag |  |  | AHU-12
Area Served |  |  | Jungle Room
Capacity code |  |  | 192
Tonnage |  |  | 16
Air Volume (cfm) | Standard: | Standard | 4,950
 | Min: | Min. | 3,960
 | Max: | Max. | 5,940
Coil internal volume (inch3) | Standard: | Standard | 610
 | Min: | Min. | 519
 | Max: | Max. | 702
Enter Project Requirements | Nominal Tons |  | 16
 | CFM |  | 6,000
 | CFM / ton |  | 357
 | CFM % over/under |  | 101%
 | Total Cooling (MBH) |  | 201.5
 | Sensible Cooling (MBH) |  | 131.1
 | Sensible Ratio |  | 65%
 | EAT Cooling (DB) |  | 80.0
 | EAT Cooling (WB) |  | 67.0
 | Total Heating (MBH) |  | N/A
 | EAT Heating (DB) |  | N/A
 | Control Type |  | Return Air
 | Coil Config. |  | Normal (Single-Circuit)
Enter Actual | Custom Coil Internal Volume (inch3) |  | 692.00
Controller Quantities: |  |  | 
TCB-IFDA1GUL | (RA Control) |  | 1
Dx Kit Model: | Coil Capacity (MBH) |  | Kit Quantities:
RBM-A1921GUL | 168 |  | 
 | 192 |  | 1
Notes: Walk through 10 critical metrics in yellow
(Tip: ~300cfm/ton)

## Slide 10
Decision-making tree
Entering Air Temperatures (EATs)
  Allowed EATs are the same as “normal” Toshiba-Carrier IDU
  If conditioning small percentage of outside air, an ERV may help mitigate EATs
  Run mixed-air calculations to make sure they’re in range of allowed EATs
Notes: Snip taken from RA Controller Installation manual.
Translation: “Air On” = Entering Air.

## Slide 11
“Medium-sized” AHUs
Application scenarios
  Carrier 39L
  For projects with multiple, “medium-sized” AHUs, kits can be installed offsite
  Potential economies of scale and “sweet spot”
Notes: Picture from “assembly line” application from distributor with multiple 39Ls. PMV kits installed in their warehouse with 39Ls kept on pallet; shrink-wrapped for shipment to jobsite.

## Slide 12
Custom Form Factors / Dimensions
Application scenarios
  Low-Profile 3rd-Party AHU
  PMV Kits can be adapted to virtually any style of AHU, as long as we meet requirements. (Refer to PMV Checklist)
Notes: Note temp sensors brazed on at angle

## Slide 13
Large AHUs
Application scenarios
  Up to 32-ton systems available
  For large, open, conditioned spaces that function well as “single-zone”
  i.e. warehouse, gym, auditorium, etc.
  Carrier 39M
  Carrier 39M
Notes: 39M shown as example.
Interesting “balance” from VRF application perspective: large single-zone ducted is generally antithetical to VRF, but this is “hybrid” that brings VRF’s efficiency, precision, and low-noise to large AHUs.

## Slide 14
Large AHUs
Application scenarios
DX controller
TC1
TC1
TC1
TCJ
TCJ
TCJ
TC2
TC2
TC2
TA
TA
TA
U5/U6
Liquid pipe
Gas Pipe
U1/U2
A/B
AHU
Dx-PMV kit
PMV
PMV
PMV
Remote
controller
  Face-split coils get “stacked”

## Slide 15
Benefits
Application scenarios
  General Benefits
  Flexibility to use AHU manufacturer’s accessories
  Can address ventilation / OA requirements
  “Muscle” of commercial AHU + precision of VRF ODU
  Can be combined to make VERY large Dx AHUs (> 32 tons)
  For retrofits
  Existing AHU can be reused (large, built-ups for example)
  Modular ODUs can fit in freight elevator (may not need crane, helicopter, etc.)
  Minimally-invasive indoor work
  Custom Coil in Large AHU
Notes: Custom coil in Large AHU picture is of an Interlaced coil (see feeds coming off of the 2 distributors on upper/left).

## Slide 16
PMV Kit Sizes
Deep dive
PMV Kit Model Number | Capacity Code | Tonnage
RBM-A0121GUL | 012 | 1
RBM-A0301GUL | 015 | 1.3
 | 018 | 1.5
 | 021 | 1.8
 | 024 | 2
 | 030 | 2.5
RBM-A0601GUL | 036 | 3
 | 042 | 3.5
 | 048 | 4
 | 060 | 5
RBM-A0961GUL | 072 | 6
 | 096 | 8
RBM-A1921GUL | 168 | 14
 | 192 | 16
Notes: Note that each PMV Kit model (above 1ton) covers MULTIPE CAPACITIES.
Capacities beyond 16-tons are available as COMBINATIONS of these individual PMV kits.

## Slide 17
DN Code Settings
Deep-dive
Notes: You have to tell the PMV Controller which size PMV kit is connected to it; this is done via DN11.

## Slide 18
RA Controller (TCB-IFDA1GUL) Terminal Blocks
Control Wiring – Required Connections
installation
PMV Wires
TC1,TC2,TCJ,TA
U1/U2 Bus
A/B Bus
FAN
Fan Output from CN60 via Relay KP2 (250VAC, 6A max)
CN34
(like water input on Verticals)
Notes: These are the critical connections you must make for it to work.
Factory jumper installed on C5/C6 (which is from CN34 on board).
Note “KP” relays provided:
These are factory-included pilot relays that are triggered by normal CN outputs
Green LEDs light up when energized (“FAN” top left and in picture to the right)
See last slide for further details on relays
Note that we only have binary fan output – on/off; we DO NOT have ability to modulate fan speed.
Note 12 PMV Wire Terminals: Larger combo kits can use 2 PMVs; each PMV uses up to 6 wires.

## Slide 19
Control Wiring – Optional Connections
installation
RA Controller (TCB-IFDA1GUL) Terminal Blocks
CN80 external error input (Normally-Open)
ALARM
CN61 alarm output
THERMO
COOL/SEC
CN82
Thermo-on output
CN82 Cooling / Secondary Heating output
CN61 external on/off
Notes: We have many of the “normal” Toshiba CN I/O options available as well; reach out to Product team for details as needed for application.
Don’t forget jumper J01 on C1/C2 external on/off (next slide).

## Slide 20
Control Wiring – Optional Connections
Deep dive
Reminder:
C1,C2 uses familiar CN61 External On/Off input
Jumper J01 should be clipped for “switch” behavior; else “pulse” behavior.
Notes: Just like normal applications with CN61 accessory, cut jumper J01 for normal “switch” response instead of pulse / “push button”.
Also, as we know, this input should NOT be used as a “thermostatic” on/off switch for BMS “temperature control”. (We speak from experience on this and previous misapplications.)

## Slide 21
Factory-Installed Relay Information
Deep dive
Qty. (4) factory-installed on DIN rail of PMV controller.
Outputs for Fan, Alarm, Thermo-On, and Cooling / Secondary Heat
No need to purchase “CN” accessory plugs & pilot relays for these outputs
  Relay Information:
  Make: Schneider
  Model: RSL1PVJU
  Coil: 12VDC
  Contact Load Current: 6A @ 250VAC
  Form: SPDT (Note NO, COM, NC in picture.)
Link to Schneider page:
https://www.schneider-electric.com/en/product/RSL1PVJU/slim-relay-mounted-on-screw-socket-with-led-and-protection-circuit%2C-12-v/
Notes: Thank you!