Project Name:
New Job
Specification
Date: 2/2/2017

Project Number:
2


1.0 PART 2 - PRODUCTS
1.1 Materials

1.1.1 Building Controllers

1.1.1.1 BACnet Controllers: General Purpose

1.1  boofoo

A.  Advanced Application Controllers (AAC) shall be a solid state micro-controller with configurable control module with pre-tested and factory configured software specifically designed for regulating building equipment using closed-loop Direct Digital Control and facility management routines. Controllers shall be capable operating in a stand-alone or networked manner, and shall be located where shown on the plans. The controller shall be powered from standard, off-the-shelf, Class II, 24-volt transformers. The controller shall be easily mounted in a standard NEMA 1 type enclosure without special rails or mounting hardware and as local and national code dictates. The controller shall be capable of operating in either a stand-alone mode or as part of a network with an EMS operator's station and other system elements including Product Integrated Controllers (PIC's)

B.  BACnet. Advanced Application Controllers (AACs). AAC shall conform to BACnet Advanced Application Controller (B-AAC) device profile as specified in ANSI/ASHRAE 135, BACnet Annex L and shall be listed as a certified B-AAC in the BACnet Testing Laboratories (BTL) Product Listing. AAC shall reside on a BACnet network using the MS/TP Data Link/Physical layer protocol.

C.  Custom Programming

The controller shall contain a graphical controller based programming language for creating complex control strategies for specific unique applications. Custom programs shall be retained in controller memory and shall not require a host CPU to operate. All custom programming point data shall be transferable from one controller to another (if networked) directly without an on-line CPU or host computer.

D.  Communication.

1.  Service Port. Each controller shall provide a service communication port for connection to a Portable Operator's Terminal. Connection shall be extended to space temperature sensor ports where shown on drawings. 

2.  Data Sharing. Each AAC shall share data as required with each networked.

E.  Environment. Controller hardware shall be suitable for anticipated ambient conditions. 

1.  Controllers used outdoors or in wet ambient conditions shall be mounted in waterproof enclosures and shall be rated for operation at -29°C to 60°C (-20°F to 140°F).

2.  Controllers used in conditioned space shall be mounted in dust-protective enclosures and shall be rated for operation at 0°C to 50°C (32°F to 120°F).

F.  Memory. 

1.  The Controller shall have a Non-Volatile Memory providing indefinite storage of application and configuration data. 

2.  Controller memory shall support operating system, database, and programming requirements.

G.  Controller Time.

Controller shall feature and maintain a 365-day Real-Time Clock/Calendar with holiday functions.

H.  Stand alone capability. The controller shall be capable of providing all control functions of the HVAC system without the use of a computer. 

1.  It shall establish occupancy scheduling based on its own local occupancy schedule, the closure of a contact connected to an external time clock or EMS system, or by a timed override request (1 to 24 hours) through its space temperature sensor override button. 

I.  Networked capability. The controller shall include the inherent capability to access the system control selections as well as to monitor system performance by means of a communicating network with a PC and EMS software program.

1.  When networked, occupancy may be established by user interface or occupancy signal from other controller located in network. 

J.  Scheduling. AAC shall provide the following schedule options as a minimum: 

1.  Weekly. Provide separate schedules for each day of the week. Each schedule shall be able to include up to 5 occupied periods (5 start-stop pairs or 10 events).

2.  Exception. Operator shall be able to designate an exception schedule for each of the next 365 days. After an exception schedule has executed, system shall discard and replace exception schedule with standard schedule for that day of the week.

3.  Holiday. Operator shall be able to define 24 special or holiday schedules of varying length on a scheduling calendar that repeats each year.

K.  Serviceability.

1.  Controller shall have diagnostic LEDs for power, communication, and processor.

2.  Wires shall be connected to a field-removable modular terminal strip or to a termination card connected by a ribbon cable.

L.  Immunity to Power and Noise. AAC shall be able to operate at 90% to 110% of nominal voltage rating and shall perform an orderly shutdown below 80% nominal voltage. Operation shall be protected against electrical noise of 5 to 120 Hz and from keyed radios up to 5 W at 1 m (3 ft).

M.  Input and output devices shall be wired to "quick-connect plug type" terminals to facilitate removal of the module without disconnecting wiring from the plug type terminal.

N.  Alarm Processing. The controller shall contain a routine to process alarms. Alarm processing logic shall also monitor return to normal conditions as part of the alarm scan. The operator will have the ability to modify the alarm/alert priority level.

O.  PID Control. System shall provide direct- and reverse-acting PID (proportional-integral-derivative) algorithms. Each algorithm shall have anti-windup and selectable controlled variable, setpoint, and PID gains. Each algorithm shall calculate a time-varying analog value that can be used to position an output or to stage a series of outputs.

P.  Anti-Short Cycling. Binary output objects shall be protected from short cycling by means of preconfigured minimum on-time and off-time settings, customized for the specific requirements of the application.

Q.  On and Off Control with Differential. System shall provide direct- and reverse-acting on and off algorithms with adjustable differential to cycle a binary output based on a controlled variable and setpoint.

R.  Inputs. Shall support the following input types as a minimum

1.  Dry or pulsed dry contacts

2.  0-5 VDC

3.  0-10 VDC

4.  4-20 mA

5.  10K thermistors

6.  1000-ohm Nickel RTD

S.  Outputs. Shall support the following input types as a minimum

1.  Discrete types

2.  0-10 VDC analog type

3.  4-20 mA analog type

T.  Real-Time Clock. Shall feature and maintain a 365-day hardware clock/calendar with holiday functions.

U.  Library of direct digital control routines. The following types of factory tested direct digital control routines shall be provided as a minimum:

1.  Indoor/Outdoor Lighting Control

2.  Time Schedule with/without override

3.  Enthalpy/Analog Comparison

4.  Analog Comparison

5.  Interlock / Permissive Interlock

6.  Fan Control

7.  Time Schedule with/without override

8.  Unit Heater

9.  Constant Volume Air Source control with Demand Controlled Ventilation

10.  VAV Air Source control with Demand Controlled Ventilation

11.  WSHP Loop Monitor and Pump Control

12.  WSHP Loop Cooling - Closed Circuit Tower

13.  WSHP Loop Cooling - Open Circuit Tower

14.  WSHP Loop Heating

15.  Electric Meter with Demand Limit

2.0 Sequences of Operation

2.1 Sequence of Operation for 
Prepared By: 
Page 1 of 4

