## Read Me
ASHRAE Standard 140-2017
Informative Annex B8, Section B8.1 Example Results
for
Section 5.2 - Building Thermal Envelope and Fabric Load Tests
195 through 960, and 600FF through 950FF
This spreadsheet contains the Standard 140, Informative Annex B8, Section B8.1 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE: (see RESULTS5-2A.DOCX for spreadsheet navigation)
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results. See instructions on page.
"Program List" : Documentation of simulation programs used to produce informative Annex B8, Section B8.1 example results
"Table List": List of Informative Annex B8, Section B8.1 Tables in workbook with locations.
"Figure List": List of Informative Annex B8, Section B8.1 Figures in workbook with locations.
"Tables 1" through "Tables 6" : Formatted result tables
"Fig B8-1 Ann Incident Solar" through "Fig B8-59 Hrly-Loads-Case900" : Figures
"data for charts" : Unformatted results for use in charts.
Individual Example Result Worksheets as follows:
ESP-DMU: Example Results for ESP-RV8, submitted by De Montfort University, U.K.
BLAST-USIT: Example Results for BLAST-3.0 level 193 v.1 submitted by National Renewable Energy Lab, U.S & Politecnico Torino, Italy
DOE21D: Example Results for DOE2.1 D submitted by National Renewable Energy Lab, U.S
SRES-SUN:Example Results for SERIRES/SUNCODE 5.7 submitted by National Renewable Energy Lab, U.S
SRES-BRE: Example Results for SERIRES 1.2 submitted by Building Research Establishment, UK
S3PAS: Example Results for S3PAE submitted by University of Sevilla, Spain
TRNSYS: Example Results for TRNSYS, Version 13.1 by Building Research Establishment, U.K and Vrije Universiteit (VUB) Brussels, Belgium
TASE: Example Results for TASE submitted by Tampere University, Finland

## Adding Results
RESULTS5-2A.XLSX
Output spreadsheet for Section 5.2 - Building Thermal Envelope Tests 195-960, & 600FF-950FF
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell B61 of Sec5-2Aout.XLS is in B61 of Sheet "YourData"
Check that the first value Annual Heating Load for Case 600) lands in YourData!B65.
Data should land in "YourData" cells as tabulated below. Your data will then appear in the rightmost column
of each table on sheets "Tables1" to "Tables6". Charts are also updated with "your data" automatically.
Complete the program information block on "Yourdata" which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT SHEETS AND NEW RESULTS
Gives locations for data in "YourData" sheet and in participant sheets.
Program Name and Version (with full build detail):
A46 |  |  |  |  | Program and version fields in rows 62 through 900 of "YourData"
Program Version Release Date: |  |  |  | E47 | are not used in this workbook.
Program Name for Tables and Charts (short): |  |  |  | E48
Results Submission Date: |  |  |  | E49
Modeler Organization for Titles (long):
A51
Modeler Organization for Tables and Charts (short): |  |  |  | E52
Model / Organization Indentifier for Charts (short): |  |  |  | E54
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | B62
VERSION: | B63
CASE# | MWh
600 | B65
610 | B66
620 | B67
630 | B68
640 | B69
650 | B70
900 | B71
910 | B72
920 | B73
930 | B74
940 | B75
950 | B76
960 | B77
195 | B78
200 | B79
210 | B80
215 | B81
220 | B82
230 | B83
240 | B84
250 | B85
270 | B86
280 | B87
290 | B88
300 | B89
310 | B90
320 | B91
395 | B92
400 | B93
410 | B94
420 | B95
430 | B96
440 | B97
800 | B98
810 | B99
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM:
VERSION:
CASE# | MWh
600 | B104
610 | B105
620 | B106
630 | B107
640 | B108
650 | B109
900 | B110
910 | B111
920 | B112
930 | B113
940 | B114
950 | B115
960 | B116
195 | B117
200 | B118
210 | B119
215 | B120
220 | B121
230 | B122
240 | B123
250 | B124
270 | B125
280 | B126
290 | B127
300 | B128
310 | B129
320 | B130
395 | B131
400 | B132
410 | B133
420 | B134
430 | B135
440 | B136
800 | B137
810 | B138
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | kW | DATE | TIME
600 | B146 | C146 | D146
610 | B147 | C147 | D147
620 | B148 | C148 | D148
630 | B149 | C149 | D149
640 | B150 | C150 | D150
650 | B151 | C151 | D151
900 | B152 | C152 | D152
910 | B153 | C153 | D153
920 | B154 | C154 | D154
930 | B155 | C155 | D155
940 | B156 | C156 | D156
950 | B157 | C157 | D157
960 | B158 | C158 | D158
195 | B159 | C159 | D159
200 | B160 | C160 | D160
210 | B161 | C161 | D161
215 | B162 | C162 | D162
220 | B163 | C163 | D163
230 | B164 | C164 | D164
240 | B165 | C165 | D165
250 | B166 | C166 | D166
270 | B167 | C167 | D167
280 | B168 | C168 | D168
290 | B169 | C169 | D169
300 | B170 | C170 | D170
310 | B171 | C171 | D171
320 | B172 | C172 | D172
395 | B173 | C173 | D173
400 | B174 | C174 | D174
410 | B175 | C175 | D175
420 | B176 | C176 | D176
430 | B177 | C177 | D177
440 | B178 | C178 | D178
800 | B179 | C179 | D179
810 | B180 | C180 | D180
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | kW | DATE | TIME
600 | B199 | C199 | D199
610 | B200 | C200 | D200
620 | B201 | C201 | D201
630 | B202 | C202 | D202
640 | B203 | C203 | D203
650 | B204 | C204 | D204
900 | B205 | C205 | D205
910 | B206 | C206 | D206
920 | B207 | C207 | D207
930 | B208 | C208 | D208
940 | B209 | C209 | D209
950 | B210 | C210 | D210
960 | B211 | C211 | D211
195 | B212 | C212 | D212
200 | B213 | C213 | D213
210 | B214 | C214 | D214
215 | B215 | C215 | D215
220 | B216 | C216 | D216
230 | B217 | C217 | D217
240 | B218 | C218 | D218
250 | B219 | C219 | D219
270 | B220 | C220 | D220
280 | B221 | C221 | D221
290 | B222 | C222 | D222
300 | B223 | C223 | D223
310 | B224 | C224 | D224
320 | B225 | C225 | D225
395 | B226 | C226 | D226
400 | B227 | C227 | D227
410 | B228 | C228 | D228
420 | B229 | C229 | D229
430 | B230 | C230 | D230
440 | B231 | C231 | D231
800 | B232 | C232 | D232
810 | B233 | C233 | D233
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | TEMP (C) | DATE | TIME
600FF | B254 | C254 | D254
900FF | B255 | C255 | D255
650FF | B256 | C256 | D256
950FF | B257 | C257 | D257
960 | B258 | C258 | D258
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM:
VERSION:
CASE# | TEMP (C) | DATE | TIME
600FF | B263 | C263 | D263
900FF | B264 | C264 | D264
650FF | B265 | C265 | D265
950FF | B266 | C266 | D266
960 | B267 | C267 | D267
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM:
VERSION:
CASE# | TEMP (C)
600FF | B272
900FF | B273
650FF | B274
950FF | B275
960 | B276
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
SURFACE | kWh/m2
= | = | = | =
600NORTH | B294
600EAST | B295
600WEST | B296
600SOUTH | B297
600HORZ. | B298
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
CASE# | kWh/m2
= | = | = | =
920WEST | B313
900SOUTH | B314
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
CASE# | kWh/m2
= | = | = | =
930WEST | B333
910SOUTH | B334
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | B349
2 | B350
3 | B351
4 | B352
5 | B353
6 | B354
7 | B355
8 | B356
9 | B357
10 | B358
11 | B359
12 | B360
13 | B361
14 | B362
15 | B363
16 | B364
17 | B365
18 | B366
19 | B367
20 | B368
21 | B369
22 | B370
23 | B371
24 | B372
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | B389
2 | B390
3 | B391
4 | B392
5 | B393
6 | B394
7 | B395
8 | B396
9 | B397
10 | B398
11 | B399
12 | B400
13 | B401
14 | B402
15 | B403
16 | B404
17 | B405
18 | B406
19 | B407
20 | B408
21 | B409
22 | B410
23 | B411
24 | B412
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | B429
2 | B430
3 | B431
4 | B432
5 | B433
6 | B434
7 | B435
8 | B436
9 | B437
10 | B438
11 | B439
12 | B440
13 | B441
14 | B442
15 | B443
16 | B444
17 | B445
18 | B446
19 | B447
20 | B448
21 | B449
22 | B450
23 | B451
24 | B452
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | B469
2 | B470
3 | B471
4 | B472
5 | B473
6 | B474
7 | B475
8 | B476
9 | B477
10 | B478
11 | B479
12 | B480
13 | B481
14 | B482
15 | B483
16 | B484
17 | B485
18 | B486
19 | B487
20 | B488
21 | B489
22 | B490
23 | B491
24 | B492
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | B508
2 | B509
3 | B510
4 | B511
5 | B512
6 | B513
7 | B514
8 | B515
9 | B516
10 | B517
11 | B518
12 | B519
13 | B520
14 | B521
15 | B522
16 | B523
17 | B524
18 | B525
19 | B526
20 | B527
21 | B528
22 | B529
23 | B530
24 | B531
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | B548
2 | B549
3 | B550
4 | B551
5 | B552
6 | B553
7 | B554
8 | B555
9 | B556
10 | B557
11 | B558
12 | B559
13 | B560
14 | B561
15 | B562
16 | B563
17 | B564
18 | B565
19 | B566
20 | B567
21 | B568
22 | B569
23 | B570
24 | B571
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | B588
2 | B589
3 | B590
4 | B591
5 | B592
6 | B593
7 | B594
8 | B595
9 | B596
10 | B597
11 | B598
12 | B599
13 | B600
14 | B601
15 | B602
16 | B603
17 | B604
18 | B605
19 | B606
20 | B607
21 | B608
22 | B609
23 | B610
24 | B611
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | B628
2 | B629
3 | B630
4 | B631
5 | B632
6 | B633
7 | B634
8 | B635
9 | B636
10 | B637
11 | B638
12 | B639
13 | B640
14 | B641
15 | B642
16 | B643
17 | B644
18 | B645
19 | B646
20 | B647
21 | B648
22 | B649
23 | B650
24 | B651
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM:
VERSION:
HOUR | kWh
= | = | = | =
1 | B668
2 | B669
3 | B670
4 | B671
5 | B672
6 | B673
7 | B674
8 | B675
9 | B676
10 | B677
11 | B678
12 | B679
13 | B680
14 | B681
15 | B682
16 | B683
17 | B684
18 | B685
19 | B686
20 | B687
21 | B688
22 | B689
23 | B690
24 | B691
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM:
VERSION:
HOUR | kWh
= | = | = | =
1 | B708
2 | B709
3 | B710
4 | B711
5 | B712
6 | B713
7 | B714
8 | B715
9 | B716
10 | B717
11 | B718
12 | B719
13 | B720
14 | B721
15 | B722
16 | B723
17 | B724
18 | B725
19 | B726
20 | B727
21 | B728
22 | B729
23 | B730
24 | B731
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
TEMP (C) | # HOURS
= | = | = | =
-50 | B749
-49 | B750
-48 | B751
-47 | B752
-46 | B753
-45 | B754
-44 | B755
-43 | B756
-42 | B757
-41 | B758
-40 | B759
-39 | B760
-38 | B761
-37 | B762
-36 | B763
-35 | B764
-34 | B765
-33 | B766
-32 | B767
-31 | B768
-30 | B769
-29 | B770
-28 | B771
-27 | B772
-26 | B773
-25 | B774
-24 | B775
-23 | B776
-22 | B777
-21 | B778
-20 | B779
-19 | B780
-18 | B781
-17 | B782
-16 | B783
-15 | B784
-14 | B785
-13 | B786
-12 | B787
-11 | B788
-10 | B789
-9 | B790
-8 | B791
-7 | B792
-6 | B793
-5 | B794
-4 | B795
-3 | B796
-2 | B797
-1 | B798
0 | B799
1 | B800
2 | B801
3 | B802
4 | B803
5 | B804
6 | B805
7 | B806
8 | B807
9 | B808
10 | B809
11 | B810
12 | B811
13 | B812
14 | B813
15 | B814
16 | B815
17 | B816
18 | B817
19 | B818
20 | B819
21 | B820
22 | B821
23 | B822
24 | B823
25 | B824
26 | B825
27 | B826
28 | B827
29 | B828
30 | B829
31 | B830
32 | B831
33 | B832
34 | B833
35 | B834
36 | B835
37 | B836
38 | B837
39 | B838
40 | B839
41 | B840
42 | B841
43 | B842
44 | B843
45 | B844
46 | B845
47 | B846
48 | B847
49 | B848
50 | B849
51 | B850
52 | B851
53 | B852
54 | B853
55 | B854
56 | B855
57 | B856
58 | B857
59 | B858
60 | B859
61 | B860
62 | B861
63 | B862
64 | B863
65 | B864
66 | B865
67 | B866
68 | B867
69 | B868
70 | B869
71 | B870
72 | B871
73 | B872
74 | B873
75 | B874
76 | B875
77 | B876
78 | B877
79 | B878
80 | B879
81 | B880
82 | B881
83 | B882
84 | B883
85 | B884
86 | B885
87 | B886
88 | B887
89 | B888
90 | B889
91 | B890
92 | B891
93 | B892
94 | B893
95 | B894
96 | B895
97 | B896
98 | B897
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## YourData
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell B61 of Sec5-2Aout.XLS is in B61 of Sheet "YourData"
Check that the first value Annual Heating Load for Case 600) lands in YourData!B65.
Data should land in "YourData" cells as tabulated in the cell map of the "Adding Results" tab.
Your data will then appear in the rightmost column of each table and chart automatically.
Complete the program information block starting at cell A45. This is used for table axis labels and chart legends.
Content Instructions (same as for Sec5-2Aout.XLS)
1) Use specified units
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
shall be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
Carrier Hourly Analysis Program 6.0.0.888 |  |  |  |  | Paste new data in row 61 and below.
Program Version Release Date: |  |  |  | 2023-02-14 | Cells in blue are used in titles and labels
Program Name for Tables and Charts (short): |  |  |  | HAP | Editing them here flows thru to other tabs
Results Submission Date: |  |  |  | 2023-10-21 | To print pdf file, see instructions on "Title Page" tab.
Modeler Organization for Titles (long):
Carrier Global Corporation
Modeler Organization for Tables and Charts (short): |  |  |  | Carrier
Model / Organization Indentifier for Charts (short): |  |  |  | HAP/Carrier | defaults to short program name / short organization name
© Carrier 2023. All rights reserved.
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM:
VERSION:
CASE# | MWh
600 | 4.467
610 | 4.47
620 | 4.454
630 | 4.712
640 | 3.312
650 | 0
900 | 1.743
910 | 1.964
920 | 3.427
930 | 4.116
940 | 1.302
950 | 0
960 | 2.432
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
800
810
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM:
VERSION:
CASE# | MWh
600 | 7.93
610 | 5.719
620 | 5.109
630 | 3.522
640 | 7.648
650 | 5.197
900 | 3.966
910 | 2.277
920 | 3.422
930 | 2.331
940 | 3.565
950 | 0.39
960 | 0.992
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
800
810
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | kW | DATE | TIME
600 | 3.945 | 2023-01-04 | 3
610 | 3.911 | 2023-01-04 | 3
620 | 3.789 | 2023-01-04 | 4
630 | 3.764 | 2023-01-04 | 4
640 | 7.298 | 2023-01-02 | 8
650 | 0
900 | 3.815 | 2023-01-04 | 7
910 | 3.793 | 2023-01-04 | 7
920 | 3.858 | 2023-01-04 | 7
930 | 3.843 | 2023-01-04 | 7
940 | 5.362 | 2023-01-04 | 8
950 | 0
960 | 2.747 | 2023-01-04 | 9
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
800
810
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | kW | DATE | TIME
600 | 7.346 | 2023-10-17 | 13
610 | 6.959 | 2023-12-23 | 13
620 | 4.615 | 2023-07-02 | 9
630 | 3.934 | 2023-07-26 | 17
640 | 7.338 | 2023-10-17 | 13
650 | 7.169 | 2023-10-17 | 12
900 | 4.926 | 2023-10-17 | 13
910 | 4.125 | 2023-10-17 | 14
920 | 3.727 | 2023-07-26 | 17
930 | 3.304 | 2023-07-26 | 17
940 | 4.985 | 2023-10-17 | 14
950 | 3.495 | 2023-09-12 | 15
960 | 1.428 | 2023-07-26 | 16
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
800
810
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | HAP
VERSION: | Carrier
CASE# | TEMP (C) | DATE | TIME
600FF | 61.72 | 2023-10-17 | 16
900FF | 45.61 | 2023-09-02 | 15
650FF | 63.22 | 2023-10-17 | 15
950FF | 35.975 | 2023-09-02 | 16
960 | 74.28 | 2023-10-17 | 14
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: | HAP
VERSION: | Carrier
CASE# | TEMP (C) | DATE | TIME
600FF | -15.227 | 2023-01-04 | 8
900FF | -3.295 | 2023-01-04 | 8
650FF | -23.06 | 2023-01-04 | 7
950FF | -19.97 | 2023-01-04 | 7
960 | -2.799 | 2023-02-06 | 6
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
CASE# | TEMP (C)
600FF | 28.05
900FF | 27.08
650FF | 19.23
950FF | 14.18
960 | 30.62
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
SURFACE | kWh/m2
= | = | = | =
600NORTH | 431.46
600EAST | 1177.84
600WEST | 1039.59
600SOUTH | 1545.41
600HORZ. | 1839.29
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
CASE# | kWh/m2
= | = | = | =
920WEST | 655
900SOUTH | 952.78
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
CASE# | kWh/m2
= | = | = | =
930WEST | 474.16
910SOUTH | 766.1
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3.8168
8 | 19.2215
9 | 34.7925
10 | 48.4197
11 | 58.0502
12 | 63.4937
13 | 63.4812
14 | 57.4075
15 | 46.5834
16 | 32.2993
17 | 16.2611
18 | 3.1327
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3.7882
8 | 18.9029
9 | 33.9683
10 | 47.3243
11 | 56.6638
12 | 61.2148
13 | 61.5117
14 | 56.5965
15 | 46.6302
16 | 32.8882
17 | 16.7956
18 | 3.1962
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 1.9091
6 | 33.7081
7 | 88.5197
8 | 136.7472
9 | 258.4548
10 | 381.7547
11 | 457.8998
12 | 478.0129
13 | 469.2892
14 | 408.1205
15 | 311.6345
16 | 182.8382
17 | 83.567
18 | 53.6695
19 | 16.3694
20 | 0.80671
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 1.9091
6 | 33.7081
7 | 88.5197
8 | 128.0895
9 | 146.0308
10 | 152.3023
11 | 149.8995
12 | 142.9895
13 | 249.3785
14 | 451.1566
15 | 613.5218
16 | 671.4247
17 | 522.2558
18 | 172.7792
19 | 30.1416
20 | 1.2111
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | TEMP (C)
= | = | = | =
1 | -7.7028
2 | -9.2047
3 | -10.6232
4 | -11.849
5 | -12.917
6 | -13.866
7 | -14.7205
8 | -15.2271
9 | -13.1183
10 | -8.2162
11 | -0.46838
12 | 8.1674
13 | 15.7391
14 | 21.864
15 | 26.0163
16 | 27.415
17 | 25.1433
18 | 20.9741
19 | 16.8694
20 | 13.14
21 | 9.824
22 | 6.8516
23 | 4.2459
24 | 1.9525
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | TEMP (C)
= | = | = | =
1 | 0.19483
2 | -0.43113
3 | -1.0129
4 | -1.5269
5 | -2.0278
6 | -2.5116
7 | -2.9838
8 | -3.2952
9 | -2.4372
10 | -0.70055
11 | 2.0135
12 | 4.7599
13 | 6.9583
14 | 8.6582
15 | 9.6605
16 | 9.6872
17 | 8.4813
18 | 7.0317
19 | 5.9548
20 | 5.089
21 | 4.3328
22 | 3.6358
23 | 3.0215
24 | 2.4507
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | TEMP (C)
= | = | = | =
1 | 23.9355
2 | 22.1389
3 | 20.9043
4 | 19.9694
5 | 19.2819
6 | 19.256
7 | 20.6617
8 | 23.4614
9 | 27.5572
10 | 32.4359
11 | 37.2916
12 | 41.9333
13 | 46.0799
14 | 49.0693
15 | 50.6371
16 | 50.6716
17 | 49.6563
18 | 47.8903
19 | 38.0153
20 | 33.8908
21 | 30.6722
22 | 28.2523
23 | 26.4232
24 | 25.0843
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
HOUR | TEMP (C)
= | = | = | =
1 | 26.5401
2 | 25.4593
3 | 24.6305
4 | 23.872
5 | 23.224
6 | 22.9861
7 | 23.5992
8 | 25.4089
9 | 26.949
10 | 28.5539
11 | 30.0202
12 | 31.3657
13 | 32.5538
14 | 33.3357
15 | 33.7302
16 | 33.7684
17 | 33.7276
18 | 33.5033
19 | 31.475
20 | 30.6968
21 | 29.87
22 | 28.9545
23 | 28.1401
24 | 27.3968
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | HAP
VERSION: | Carrier
HOUR | kWh
= | = | = | =
1 | 3.7574
2 | 3.9161
3 | 3.9447
4 | 3.9245
5 | 3.9233
6 | 3.9186
7 | 3.9206
8 | 3.4557
9 | 0.99839
10 | 0
11 | -0.15154
12 | -3.8604
13 | -4.543
14 | -4.096
15 | -2.8463
16 | -0.78944
17 | 0
18 | 0.20065
19 | 2.8773
20 | 3.4716
21 | 3.5561
22 | 3.5731
23 | 3.5225
24 | 3.4923
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | HAP
VERSION: | Carrier
HOUR | kWh
= | = | = | =
1 | 3.4622
2 | 3.6331
3 | 3.6882
4 | 3.7203
5 | 3.7615
6 | 3.7885
7 | 3.8151
8 | 3.565
9 | 2.1402
10 | 0.58142
11 | 0
12 | 0
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0
18 | 0
19 | 0
20 | 0.72571
21 | 1.5679
22 | 2.0622
23 | 2.3715
24 | 2.6037
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | HAP
VERSION: | Carrier
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 0
-4 | 0
-3 | 1
-2 | 4
-1 | 2
0 | 6
1 | 14
2 | 11
3 | 11
4 | 16
5 | 18
6 | 18
7 | 26
8 | 29
9 | 32
10 | 40
11 | 46
12 | 61
13 | 86
14 | 108
15 | 120
16 | 163
17 | 176
18 | 212
19 | 223
20 | 253
21 | 305
22 | 335
23 | 363
24 | 336
25 | 346
26 | 347
27 | 361
28 | 380
29 | 416
30 | 431
31 | 425
32 | 410
33 | 431
34 | 327
35 | 338
36 | 331
37 | 281
38 | 257
39 | 191
40 | 157
41 | 138
42 | 86
43 | 44
44 | 29
45 | 15
46 | 4
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## Title Page
ASHRAE Standard 140-2017 | To print example results:
Informative Annex B8, Section B8.1 | 1. Select results type in cell B21:
"Example" for Standard 140 Annex B8 Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF | "Title Page" thru "Figure List"
"Tables 1" thru "Tables 6"
"Fig B8-1 Ann Incident Solar" thru "Fig B8-59 Hrly-Loads-Case900"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Scratch area for Table subtitle 1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Scratch area for Table subtitle 2
Scratch area for chart subtitles
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1 Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF

## Program List
ASHRAE Standard 140-2017
Computer Programs, Program Authors, and Producers of Example Results for
Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
The programs used to generate the example results are described in Table B11-1. Under the
computer program column, the first entry in each cell is the proper program name and version
number. The entries in parentheses are the abbreviations for the programs generally used in the
tables and charts which follow.
The second column ("Authoring Organization") indicates the national research facility, university,
or industry organization with expertise in building science that wrote the simulation software.
The third column ("Implemented By") indicates the national research facility, university, or industry
organization with expertise in building science that performed the simulations. The majority of
organizations that performed simulations either ran software written by their organization or
otherwise ran other building energy simulation software in addition to that written by their organization.
See Standard 140, Annex B11 for further details.
TABLE B11-1
Computer Programs, Program Authors, and Producers of Example Results
Computer Program (Abbrev.) | Authoring Organization | Example Results Produced by
BLAST-3.0 level 193 v.1 (BLAST-US/IT) | CERL,a United States (U.S.) | NREL,b U.S. Politecnico Torino, Italy
DOE-2.1D 14 (DOE21D) | LANL/LBNL,c U.S. | NREL, U.S.
ESP-RV8 (ESP-DMU) | Strathclyde University, United Kingdom (U.K.) | De Montfort University, U.K.
SERIRES/SUNCODE 5.7 (SRES/SUN) | NREL/Ecotope, U.S. | NREL, U.S.
SERIRES 1.2 (SRES-BRE) | NREL/BRE,d U.S./U.K. | BRE, U.K.
S3PAS | University of Sevilla, Spain | University of Sevilla, Spain
TASE | Tampere University, Finland | Tampere University, Finland
TRNSYS 13.1 (TSYS-BEL/BRE) | University of Wisconsin, U.S. | BRE, U.K. Vrije Universiteit (VUB) Brussels, Belgium
aCERL-U.S. Army Construction Engineering Research Laboratories
bNREL-National Renewable Energy Laboratory
cLANL/LBNL-Los Alamos National Laboratory/Lawrence Berkeley National Laboratory
dBRE-Building Research Establishment

## Table List
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B8-1 | Annual Heating Loads | Tables 1 | B7 - P47
| B8-2 | Annual Sensible Cooling Loads |  | B48 - P89
| B8-3 | Annual Hourly Integrated Peak Heating Loads | Tables 2 | B7 - AH47
| B8-4 | Annual Hourly Integrated Peak Sensible Cooling Loads |  | B48 - AH88
| B8-5 | Free-Float Temperature Output |  | B89 - AH118
| B8-6 | Low Mass Basic Sensitivity Tests | Tables 3 | B7 - P39
| B8-7 | High Mass Basic Sensitivity Tests |  | B41 - P81
| B8-8 | Low Mass In-Depth (Cases 195 thru 320) Sensitivity Tests | Tables 4 | B7 - P78
| B8-9 | Low Mass In-Depth (Cases 395 thru 440) Sensitivity Tests | Tables 5 | B7 - P45
| B8-10 | High Mass Basic and In-Depth Sensitivity Tests |  | B47 - P91
| B8-11 | Annual Transmissivity Coefficient of Windows | Tables 6 | B7 - O14
| B8-12 | Annual Shading Coefficient of Window Shading Devices: Overhangs & Fins |  | B16 - O23
| B8-13 | Case 600 Annual Incident Solar Radiation (kWh/m2) |  | B25 - O34
| B8-14 | Case 600 Annual Transmitted Solar Radiation – Unshaded (kWh/m2) |  | B36 - O42
| B8-15 | Case 600 Annual Transmitted Solar Radiation –Shaded (kWh/m2) |  | B44 - O50

## Figure List
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
List of Figures
| Figure | Title | Sheet Tab
| B8-1 | BESTEST BASIC Annual Incident Solar Radiation | Fig B8-1 Ann Incident Solar
| B8-2 | BESTEST BASIC Annual Transmitted Solar Radiation Unshaded | Fig B8-2 Ann SolRad Unshaded
| B8-3 | BESTEST BASIC Annual Transmitted Solar Radiation Shaded | Fig B8-3 Ann SolRad Shaded
| B8-4 | BESTEST BASIC Annual Transmissivity Coefficient of Windows | Fig B8-4 Trans Coeff
(Unshaded Transmitted)/(Incident Solar Radiation)
| B8-5 | BESTEST BASIC Annual Overhang and Fin Shading Coefficients | Fig B8-5 OH&Fin Shade Coeff
(1-(Shaded)/(Unshaded)) Transmitted Solar Radiation
| B8-6 | BESTEST BASIC Low Mass Annual Heating | Fig B8-6 Lomass Ann Heat
| B8-7 | BESTEST BASIC Low Mass Annual Sensible Cooling | Fig B8-7 Lomass Ann Cool
| B8-8 | BESTEST BASIC Low Mass Peak Heating | Fig B8-8 Lomass Peak Heat
| B8-9 | BESTEST BASIC Low Mass Peak Sensible Cooling | Fig B8-9 Lomass Peak Cool
| B8-10 | BESTEST BASIC High Mass Annual Heating | Fig B8-10 Himass Ann Heat
| B8-11 | BESTEST BASIC High Mass Annual Sensible Cooling | Fig B8-11 Himass Ann Cool
| B8-12 | BESTEST BASIC High Mass Peak Heating | Fig B8-12 Himass Peak Heat
| B8-13 | BESTEST BASIC High Mass Peak Sensible Cooling | Fig B8-13 Himass Peak Cool
| B8-14 | BESTEST BASIC Maximum Hourly Annual Temperature Free-Float Cases | Fig B8-14 FF Maximum Temp
| B8-15 | BESTEST BASIC Minimum Hourly Annual Temperature Free-Float Cases | Fig B8-15 FF Minimum Temp
| B8-16 | BESTEST BASIC Average Hourly Annual Temperature Free-Float Cases | Fig B8-16 FF Average Temp
| B8-17 | BESTEST BASIC South Window Shading (Delta) | Fig B8-17 Delta-S Shade-Load
Annual Heating and Sensible Cooling
| B8-18 | BESTEST BASIC South Window Shading (Delta) | Fig B8-18 Delta-S Shade-Peak
Peak Heating and Sensible Cooling
| B8-19 | BESTEST BASIC East & West Window (Delta) | Fig B8-19 Delta-E&W-Load
Annual Heating and Sensible Cooling
| B8-20 | BESTEST BASIC East & West Window (Delta) | Fig B8-20 Delta-E&W-Peak
Peak Heating and Sensible Cooling
| B8-21 | BESTEST BASIC East & West Shaded Window (Delta) | Fig B8-21 Delta-E&WShade-Load
Annual Heating and Sensible Cooling
| B8-22 | BESTEST BASIC East & West Shaded Window (Delta) | Fig B8-22 Delta-E&WShade-Peak
Peak Heating and Sensible Cooling
| B8-23 | BESTEST BASIC Thermostat Setback (Delta) Annual Heating | Fig B8-23 Delta-TSetback-Heat
| B8-24 | BESTEST BASIC Thermostat Setback (Delta) Peak Heating | Fig B8-24 Delta-TSetback-Peak
| B8-25 | BESTEST BASIC Vent Cooling (Delta) Annual Sensible Cooling | Fig B8-25 Delta-VentCool-Load
| B8-26 | BESTEST BASIC Vent Cooling (Delta) Peak Sensible Cooling | Fig B8-26 Delta-VentCool-Peak
| B8-27 | BESTEST BASIC Sunspace (Delta) Annual Heating and Sensible Cooling | Fig B8-27 Delta-Sunspace-Load
| B8-28 | BESTEST BASIC Sunspace (Delta) Peak Heating and Sensible Cooling | Fig B8-28 Delta-Sunspace-Peak
| B8-29 | BESTEST BASIC AND IN-DEPTH Mass Effect (Delta) | Fig B8-29 Delta-Mass Effect-Ann
Annual Heating and Sensible Cooling
| B8-30 | BESTEST BASIC AND IN-DEPTH Mass Effect (Delta) | Fig B8-30 Delta-Mass Effect-Pk
Peak Heating and Sensible Cooling
| B8-31 | BESTEST IN-DEPTH South Window (Delta) | Fig B8-31 Delta-S Win-Ann
Annual Heating and Sensible Cooling
| B8-32 | BESTEST IN-DEPTH South Window (Delta) | Fig B8-32 Delta-S Win-Peak
Peak Heating and Sensible Cooling
| B8-33 | BESTEST IN-DEPTH Low Mass Annual Heating Cases 195 to 250 | Fig B8-33 Indepth 1
| B8-34 | BESTEST IN-DEPTH Low Mass Annual Sensible Cooling Cases 195 to 250 | Fig B8-34 Indepth 2
| B8-35 | BESTEST IN-DEPTH Low Mass Peak Heating Cases 195 to 250 | Fig B8-35 Indepth 3
| B8-36 | BESTEST IN-DEPTH Low Mass Peak Sensible Cooling Cases 195 to 250 | Fig B8-36 Indepth 4
| B8-37 | BESTEST IN-DEPTH Low Mass Annual Heating Cases 270 to 320 | Fig B8-37 Indepth 5
| B8-38 | BESTEST IN-DEPTH Low Mass Annual Sensible Cooling Cases 270 to 320 | Fig B8-38 Indepth 6
| B8-39 | BESTEST IN-DEPTH Low Mass Peak Heating Cases 270 to 320 | Fig B8-39 Indepth 7
| B8-40 | BESTEST IN-DEPTH Low Mass Peak Sensible Cooling Cases 270 to 320 | Fig B8-40 Indepth 8
| B8-41 | BESTEST IN-DEPTH Cases 195 to 220 (Delta) | Fig B8-41 Indepth Delta 1
Annual Heating and Sensible Cooling
| B8-42 | BESTEST IN-DEPTH Cases 195 to 220 (Delta) | Fig B8-42 Indepth Delta 2
Peak Heating and Sensible Cooling
| B8-43 | BESTEST IN-DEPTH Cases 220 to 270 (Delta) | Fig B8-43 Indepth Delta 3
Annual Heating and Sensible Cooling
| B8-44 | BESTEST IN-DEPTH Cases 220 to 270 (Delta) | Fig B8-44 Indepth Delta 4
Peak Heating and Sensible Cooling
| B8-45 | BESTEST IN-DEPTH Cases 270 to 320 (Delta) | Fig B8-45 Indepth Delta 5
Annual Heating and Sensible Cooling
| B8-46 | BESTEST IN-DEPTH Cases 270 to 320 (Delta) | Fig B8-46 Indepth Delta 6
Peak Sensible Cooling
| B8-47 | BESTEST IN-DEPTH Annual Heating Cases 395 to 440, 800, 810 | Fig B8-47 Indepth 9
| B8-48 | BESTEST IN-DEPTH Annual Sensible Cooling Cases 395 to 440, 800, 810 | Fig B8-48 Indepth 10
| B8-49 | BESTEST IN-DEPTH Peak Heating Cases 395 to 440, 800, 810 | Fig B8-49 Indepth 11
| B8-50 | BESTEST IN-DEPTH Peak Sensible Cooling Cases 395 to 440, 800, 810 | Fig B8-50 Indepth 12
| B8-51 | BESTEST IN-DEPTH Cases 395 to 600 (Delta) | Fig B8-51 Indepth Delta 7
Annual Heating and Sensible Cooling
| B8-52 | BESTEST IN-DEPTH Cases 395 to 600 (Delta) | Fig B8-52 Indepth Delta 8
Peak Heating and Sensible Cooling
| B8-53 | BESTEST Case 900FF Annual Hourly Temperature Frequency | Fig B8-53 Hrly-Temp Freq
| B8-54 | BESTEST Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-54 Hrly-IncidentSol-S
South Facing Surface
| B8-55 | BESTEST Case 600 Cloudy & Clear Day Hourly Incident Solar | Fig B8-55 Hrly-IncidentSol-W
West Facing Surface
| B8-56 | BESTEST HOURLY FREE FLOAT TEMPERATURES | Fig B8-56 Hrly-FF Temp-ColdDay
Clear Cold Day - Cases 600FF and 900FF
| B8-57 | BESTEST HOURLY FREE FLOAT TEMPERATURES | Fig B8-57 Hrly-FF Temp-HotDay
Clear Hot Day - Cases 650FF and 950FF
| B8-58 | BESTEST HOURLY LOADS Clear Cold Day, Case 600 | Fig B8-58 Hrly-Loads-Case600
Heating (+), Sensible Cooling (-)
| B8-59 | BESTEST HOURLY LOADS Clear Cold Day, Case 900 | Fig B8-59 Hrly-Loads-Case900
Heating (+), Sensible Cooling (-)

## Tables 1
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-1. Annual Heating Loads (MWh)
Simulation Model: | ESP | BLAST | DOE21D | SRES-SUN | SRES* | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | (Max-Min)/ | Carrier
Case | [11 empty] | Mean** (%)
600 Base Case, South Windows | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 4.872 | 5.362 | 4.296 | 5.709 | 5.0895 | 27.76% | 4.467
610 S. Windows + Overhang | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 4.97 | 5.383 | 4.355 | 5.786 | 5.1464 | 27.81% | 4.47
620 East & West Windows | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.073 | 5.728 | 4.613 | 5.944 | 5.4074 | 24.61% | 4.454
630 E&W Windows + Overhang & Fins | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 | 5.624 |  | 5.05 | 6.469 | 5.783 | 24.54% | 4.712
640 Case 600 with Htg Temp. Setback | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.043 | 3.309 | 2.751 | 3.803 | 3.2071 | 32.8% | 3.312
650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 | 4.171e-06 | 5.2138e-07 | ---- | 0
900 South Windows | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 1.655 | 2.041 | 1.17 | 2.041 | 1.7454 | 49.9% | 1.743
910 S. Windows + Overhang | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.097 | 2.22 | 1.575 | 2.282 | 2.0659 | 34.22% | 1.964
920 East & West Windows | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 3.776 | 4.3 | 3.313 | 4.3 | 3.9728 | 24.84% | 3.427
930 E&W Windows + Overhang & Fins | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 | 4.74 |  | 4.143 | 5.335 | 4.7451 | 25.12% | 4.116
940 Case 900 with Htg Temp. Setback | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.08 | 1.323 | 0.793 | 1.411 | 1.1596 | 53.29% | 1.302
950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 | 7.801e-06 | 9.7513e-07 | ---- | 0
960 Sunspace | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 3.373 | 2.816 | 2.311 | 3.373 | 2.8462 | 37.31% | 2.432
195 Solid Conduction | 4.167 | [7 empty] | 4.167 | 4.167 | 4.167 | 0%
200 Surface Convection (Int & Ext IR="off") | 5.252 | [7 empty] | 5.252 | 5.252 | 5.252 | 0%
210 Infrared Radiation (Int IR="off", Ext IR="on") | 6.456 | 6.559 |  |  |  |  | 6.554 | 6.967 | 6.456 | 6.967 | 6.634 | 7.703%
215 Infrared Radiation (Int IR="on", Ext IR="off") | 5.547 | [7 empty] | 5.547 | 5.547 | 5.547 | 0%
220 In-Depth Base Case | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.297 | 7.437 | 6.944 | 8.787 | 7.6664 | 24.04%
230 Infiltration | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.84 | 10.964 | 10.376 | 12.243 | 11.1853 | 16.69%
240 Internal Gains | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.076 | 6.234 | 5.649 | 7.448 | 6.3956 | 28.13%
250 Exterior Shortwave Absorptance | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.764 | 5.738 | 4.751 | 7.024 | 6.0314 | 37.69%
270 South Solar Windows | 4.51 | 4.93 |  | 5.341 | 5.92 |  | 5.047 | 5.489 | 4.51 | 5.92 | 5.2062 | 27.08%
280 Cavity Albedo | 4.675 | 5.125 |  | 5.937 | 6.148 |  | 5.279 | 5.841 | 4.675 | 6.148 | 5.5008 | 26.78%
290 South Shading | 4.577 | 4.959 |  | 5.406 | 5.942 |  | 5.132 | 5.509 | 4.577 | 5.942 | 5.2542 | 25.98%
300 East/West Window | 4.761 | 5.077 |  | 5.587 | 5.964 |  | 5.124 | 5.786 | 4.761 | 5.964 | 5.3832 | 22.35%
310 East/West Shading | 5.221 | 5.327 |  | 5.85 | 6.165 |  | 5.61 |  | 5.221 | 6.165 | 5.6346 | 16.75%
320 Thermostat | 3.859 | 4.209 |  | 4.627 | 5.141 |  | 4.348 | 4.84 | 3.859 | 5.141 | 4.504 | 28.46%
395 Low Mass Solid Conduction | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839 | 4.799 | 5.835 | 5.0849 | 20.37%
400 Low Mass Opaque Windows | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.166 | 7.326 | 6.9 | 8.77 | 7.5579 | 24.74%
410 Low Mass Infiltration | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 8.936 | 9.085 | 8.596 | 10.506 | 9.3094 | 20.52%
420 Low Mass Internal Gains | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.697 | 7.863 | 7.298 | 9.151 | 8.0164 | 23.12%
430 Low Mass Ext. Shortwave Absorptance | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51 | 5.429 | 7.827 | 6.7225 | 35.67%
440 Low Mass Cavity Albedo | 4.449 | 4.987 |  | 5.652 | 5.811 |  | 5.098 | 5.642 | 4.449 | 5.811 | 5.2732 | 25.83%
800 High Mass Opaque Windows | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861 | 4.868 | 7.228 | 6.1527 | 38.36%
810 High Mass Cavity Albedo | 1.839 | 2.446 |  | 3.004 | 2.828 |  | 2.567 | 2.962 | 1.839 | 3.004 | 2.6077 | 44.68%
* SRES-BRE simulations for cases with interior solar absorptance = 0.9 have an input error that likely affects annual heating and cooling loads by <0.2 MWh/y (2-3%); see Annex B7, Section B7.1.1.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-2. Annual Sensible Cooling Loads (MWh)
Simulation Model: | ESP | BLAST | DOE21D | SRES-SUN | SRES* | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | (Max-Min)/ | Carrier
Case | [11 empty] | Mean** (%)
600 Base Case, South Windows | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.492 | 6.778 | 6.137 | 7.964 | 6.8316 | 26.74% | 7.93
610 S. Windows + Overhang | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 4.601 | 5.506 | 3.915 | 5.778 | 4.9644 | 37.53% | 5.719
620 East & West Windows | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 3.901 | 4.351 | 3.417 | 5.004 | 4.2179 | 37.63% | 5.109
630 E&W Windows + Overhang & Fins | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 | 2.416 |  | 2.129 | 3.701 | 2.8321 | 55.51% | 3.522
640 Case 600 with Htg Temp. Setback | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.246 | 6.508 | 5.952 | 7.811 | 6.5915 | 28.2% | 7.648
650 Case 600 with Night Ventilation | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.119 | 5.456 | 4.816 | 6.545 | 5.4816 | 31.54% | 5.197
900 South Windows | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.485 | 2.599 | 2.132 | 3.415 | 2.6779 | 47.91% | 3.966
910 S. Windows + Overhang | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.326 | 1.767 | 0.821 | 1.872 | 1.4471 | 72.63% | 2.277
920 East & West Windows | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.418 | 2.613 | 1.84 | 3.092 | 2.5524 | 49.05% | 3.422
930 E&W Windows + Overhang & Fins | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 | 1.416 |  | 1.039 | 2.238 | 1.6436 | 72.95% | 2.331
940 Case 900 with Htg. Temp. Setback | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.383 | 2.516 | 2.079 | 3.241 | 2.5775 | 45.08% | 3.565
950 Case 900 with Night Ventilation | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.5606 | 0.771 | 0.387 | 0.921 | 0.60545 | 88.2% | 0.39
960 Sunspace | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.4113 | 0.786 | 0.4113 | 0.803 | 0.61791 | 63.39% | 0.992
195 Solid Conduction | 0.414 | [7 empty] | 0.414 | 0.414 | 0.414 | 0%
200 Surface Convection (Int & Ext IR="off") | 0.57 | [7 empty] | 0.57 | 0.57 | 0.57 | 0%
210 Infrared Radiation (Int IR="off", Ext IR="on") | 0.162 | 0.613 |  |  |  |  | 0.6679 | 0.641 | 0.162 | 0.6679 | 0.52097 | 97.11%
215 Infrared Radiation (Int IR="on", Ext IR="off") | 0.639 | [7 empty] | 0.639 | 0.639 | 0.639 | 0%
220 In-Depth Base Case | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.7368 | 0.683 | 0.186 | 0.835 | 0.63772 | 101.8%
230 Infiltration | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 1.04 | 0.985 | 0.454 | 1.139 | 0.92963 | 73.69%
240 Internal Gains | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.114 | 1.045 | 0.415 | 1.246 | 0.98738 | 84.16%
250 Exterior Shortwave Absorptance | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 2.684 | 3.38 | 2.177 | 3.38 | 2.7925 | 43.08%
270 South Solar Windows | 7.528 | 8.67 |  | 9.828 | 10.35 |  | 8.764 | 8.714 | 7.528 | 10.35 | 8.9757 | 31.44%
280 Cavity Albedo | 4.873 | 5.895 |  | 6.511 | 7.114 |  | 5.761 | 6.257 | 4.873 | 7.114 | 6.0685 | 36.93%
290 South Shading | 5.204 | 7.011 |  | 7.871 | 8.089 |  | 6.699 | 7.431 | 5.204 | 8.089 | 7.0508 | 40.92%
300 East/West Window | 4.302 | 5.836 |  | 6.665 | 7.1 |  | 5.721 | 5.781 | 4.302 | 7.1 | 5.9008 | 47.42%
310 East/West Shading | 2.732 | 4.57 |  | 5.245 | 5.471 |  | 3.727 |  | 2.732 | 5.471 | 4.349 | 62.98%
320 Thermostat | 5.061 | 5.906 |  | 6.725 | 7.304 |  | 5.956 | 5.663 | 5.061 | 7.304 | 6.1025 | 36.76%
395 Low Mass Solid Conduction | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011 | 0 | 0.016 | 0.0090363 | 177.1%
400 Low Mass Opaque Windows | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.04468 | 0.044 | 0 | 0.061 | 0.03646 | 167.3%
410 Low Mass Infiltration | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.06707 | 0.065 | 0 | 0.084 | 0.054009 | 155.5%
420 Low Mass Internal Gains | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.1575 | 0.143 | 0.011 | 0.189 | 0.13006 | 136.9%
430 Low Mass Ext. Shortwave Absorptance | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875 | 0.422 | 0.875 | 0.62805 | 72.13%
440 Low Mass Cavity Albedo | 3.967 | 4.172 |  | 4.674 | 5.204 |  | 3.975 | 4.684 | 3.967 | 5.204 | 4.446 | 27.82%
800 High Mass Opaque Windows | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325 | 0.055 | 0.325 | 0.20166 | 133.9%
810 High Mass Cavity Albedo | 1.052 | 1.405 |  | 1.711 | 1.708 |  | 1.191 | 1.624 | 1.052 | 1.711 | 1.4485 | 45.5%
* SRES-BRE (SERIRES 1.2) simulations for cases with interior solar absorptance = 0.9 have an input error that likely affects annual heating and cooling loads by <0.2 MWh/y (2-3%); see Annex B7,
Section B7.1.1. Affected results for Cases 270 and 290 through 320 are indicated by italics
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 2
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-3. Annual Hourly Integrated Peak Heating Loads
Simulation Model: | ESP |  |  | BLAST |  |  | DOE21D |  |  | SRES-SUN |  |  | SRES | S3PAS |  |  | TSYS |  |  | TASE |  |  | Example Result Statistics |  |  |  | HAP
Organization or Country: | DMU |  |  | US-IT |  |  | NREL |  |  | NREL |  |  | BRE* | SPAIN |  |  | BEL-BRE |  |  | FINLAND |  |  | Min | Max | Mean | (Max-Min)/ | Carrier
Case | kW | Date | Hr | kW | Date | Hr | kW | Date | Hr | kW | Date | Hr |  | kW | Date | Hr | kW | Date | Hr | kW | Date | Hr | kW | kW | kW | Mean** (%) | kW | Date | Hr
600 Base Case, South Windows | 3.437 | 1993-01-04 | 5 | 3.94 | 2022-01-04 | 5 | 4.045 | 2022-01-04 | 5 | 4.258 | 2022-01-04 | 2 |  | 4.037 | 2022-01-04 | 2 | 3.9306 | 2022-01-04 | 6 | 4.354 | 2022-01-04 | 2 | 3.437 | 4.354 | 4.0002 | 22.92% | 3.945 | 2023-01-04 | 3
610 S. Windows + Overhang | 3.437 | 1993-01-04 | 5 | 3.941 | 2022-01-04 | 5 | 4.034 | 2022-01-04 | 5 | 4.258 | 2022-01-04 | 2 |  | 4.037 | 2022-01-04 | 2 | 3.9222 | 2022-01-04 | 6 | 4.354 | 2022-01-04 | 2 | 3.437 | 4.354 | 3.9976 | 22.94% | 3.911 | 2023-01-04 | 3
620 East & West Windows | 3.591 | 1993-01-04 | 6 | 3.941 | 2022-01-04 | 5 | 4.046 | 2022-01-04 | 5 | 4.277 | 2022-01-04 | 2 |  | 4.277 | 2022-01-04 | 2 | 3.9222 | 2022-01-04 | 6 | 4.379 | 2022-01-04 | 2 | 3.591 | 4.379 | 4.0619 | 19.4% | 3.789 | 2023-01-04 | 4
630 E&W Windows + Overhang & Fins | 3.592 | 1993-01-04 | 7 | 3.941 | 2022-01-04 | 5 | 4.025 | 2022-01-04 | 5 | 4.28 | 2022-01-04 | 2 |  | 4.278 | 2022-01-04 | 2 | 3.9222 | 2022-01-04 | 6 |  |  |  | 3.592 | 4.28 | 4.0064 | 17.17% | 3.764 | 2023-01-04 | 4
640 Case 600 with Htg. Temp. Setback | 5.232 | 1993-01-04 | 7 | 5.486 | 2022-01-04 | 8 | 5.943 | 2022-01-04 | 8 | 6.53 | 2022-01-04 | 8 |  | 6.347 | 2022-01-04 | 8 | 5.7222 | 2022-01-04 | 8 | 6.954 | 2022-01-04 | 8 | 5.232 | 6.954 | 6.0306 | 28.55% | 7.298 | 2023-01-02 | 8
Organization or Country: Case: 650 Case 600 with Night Ventilation; DMU kW: 0; US-IT kW: 0; US-IT Date: 2022-01-04; NREL kW: 0; NREL kW: 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | ---- | 0
900 South Windows | 2.85 | 1993-01-04 | 7 | 3.453 | 2022-01-04 | 7 | 3.557 | 2022-01-04 | 7 | 3.76 | 2022-01-04 | 7 |  | 3.608 | 2022-01-04 | 8 | 3.5167 | 2022-01-04 | 7 | 3.797 | 2022-01-04 | 7 | 2.85 | 3.797 | 3.506 | 27.01% | 3.815 | 2023-01-04 | 7
910 S. Windows + Overhang | 2.858 | 1993-01-04 | 7 | 3.456 | 2022-01-04 | 7 | 3.564 | 2022-01-04 | 7 | 3.764 | 2022-01-04 | 7 |  | 3.618 | 2022-01-04 | 8 | 3.5361 | 2022-01-04 | 7 | 3.801 | 2022-01-04 | 7 | 2.858 | 3.801 | 3.5139 | 26.84% | 3.793 | 2023-01-04 | 7
920 East & West Windows | 3.308 | 1993-01-04 | 7 | 3.703 | 2022-01-04 | 7 | 3.805 | 2022-01-04 | 7 | 4.013 | 2022-01-04 | 7 |  | 4.029 | 2022-01-04 | 7 | 3.7083 | 2022-01-04 | 7 | 4.061 | 2022-01-04 | 7 | 3.308 | 4.061 | 3.8039 | 19.8% | 3.858 | 2023-01-04 | 7
930 E&W Windows + Overhang & Fins | 3.355 | 1993-01-04 | 7 | 3.732 | 2022-01-04 | 7 | 3.832 | 2022-01-04 | 7 | 4.042 | 2022-01-04 | 7 |  | 4.064 | 2022-01-04 | 7 | 3.7444 | 2022-01-04 | 7 |  |  |  | 3.355 | 4.064 | 3.7949 | 18.68% | 3.843 | 2023-01-04 | 7
940 Case 900 with Htg. Temp. Setback | 3.98 | 1993-01-04 | 7 | 5.028 | 2022-01-04 | 8 | 5.665 | 2022-01-04 | 8 | 6.116 | 2022-01-04 | 8 |  | 6.117 | 2022-01-04 | 8 | 5.1222 | 2022-01-03 | 9 | 6.428 | 2022-01-04 | 8 | 3.98 | 6.428 | 5.4937 | 44.56% | 5.362 | 2023-01-04 | 8
Organization or Country: Case: 950 Case 900 with Night Ventilation; DMU kW: 0; US-IT kW: 0; NREL kW: 0; NREL kW: 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | ---- | 0
960 Sunspace | 2.41 | 1993-01-04 | 7 | 2.751 | 2022-01-04 | 8 | 2.727 | 2022-01-04 | 8 | 2.863 | 2022-01-04 | 8 |  | 2.852 | 2022-01-04 | 8 | 2.522 | 2022-01-04 | 8 | 2.779 | 2022-01-04 | 8 | 2.41 | 2.863 | 2.7006 | 16.77% | 2.747 | 2023-01-04 | 9
Organization or Country: Case: 195 Solid Conduction; DMU kW: 2.004; DMU Date: 1993-01-04; DMU Hr: 2 | [10 empty] | 2.004 | 2.004 | 2.004 | 0%
Organization or Country: Case: 200 Surface Convection (Int & Ext IR="off"); DMU kW: 2.651; DMU Date: 1993-01-04; DMU Hr: 5 | [10 empty] | 2.651 | 2.651 | 2.651 | 0%
Organization or Country: Case: 210 Infrared Radiation (Int IR="off", Ext IR="on"); DMU kW: 2.701; DMU Date: 1993-01-04; DMU Hr: 5; US-IT kW: 2.973; US-IT Date: 2022-01-04; US-IT Hr: 5 |  |  |  |  | 2.9806 | 2022-01-04 | 5 | 3.325 | 2022-01-04 | 2 | 2.701 | 3.325 | 2.9949 | 20.84%
Organization or Country: Case: 215 Infrared Radiation (Int IR="on", Ext IR="off"); DMU kW: 2.787; DMU Date: 1993-01-04; DMU Hr: 5 | [10 empty] | 2.787 | 2.787 | 2.787 | 0%
220 In-Depth Base Case | 2.867 | 1993-01-04 | 5 | 3.28 | 2022-01-04 | 5 | 3.465 | 2022-01-04 | 5 | 3.695 | 2022-01-04 | 2 |  | 3.348 | 2022-01-04 | 8 | 3.3361 | 2022-01-04 | 6 | 3.52 | 2022-01-04 | 2 | 2.867 | 3.695 | 3.3587 | 24.65%
230 Infiltration | 4.386 | 1993-01-04 | 5 | 4.984 | 2022-01-04 | 2 | 4.994 | 2022-01-04 | 2 | 5.279 | 2022-01-04 | 2 |  | 5.159 | 2022-01-04 | 2 | 4.8917 | 2022-01-04 | 6 | 5.107 | 2022-01-04 | 2 | 4.386 | 5.279 | 4.9715 | 17.96%
240 Internal Gains | 2.685 | 1993-01-04 | 5 | 3.1 | 2022-01-04 | 5 | 3.282 | 2022-01-04 | 5 | 3.495 | 2022-01-04 | 2 |  | 3.159 | 2022-01-04 | 8 | 3.1528 | 2022-01-04 | 6 | 3.333 | 2022-01-04 | 8 | 2.685 | 3.495 | 3.1724 | 25.53%
250 Exterior Shortwave Absorptance | 2.866 | 1993-01-04 | 5 | 3.279 | 2022-01-04 | 5 | 3.465 | 2022-01-04 | 5 | 3.695 | 2022-01-04 | 2 |  | 3.341 | 2022-01-04 | 6 | 3.3361 | 2022-01-04 | 6 | 3.525 | 2022-01-04 | 2 | 2.866 | 3.695 | 3.3582 | 24.69%
270 South Windows | 2.863 | 1993-01-04 | 5 | 3.277 | 2022-01-04 | 5 |  |  |  | 3.661 | 2022-01-04 | 2 |  |  |  |  | 3.3361 | 2022-01-04 | 6 | 3.738 | 2022-01-04 | 2 | 2.863 | 3.738 | 3.375 | 25.93%
280 Cavity Albedo | 2.864 | 1993-01-04 | 5 | 3.278 | 2022-01-04 | 5 |  |  |  | 3.685 | 2022-01-04 | 2 |  |  |  |  | 3.3361 | 2022-01-04 | 6 | 3.759 | 2022-01-04 | 2 | 2.864 | 3.759 | 3.3844 | 26.44%
290 South Shading | 2.863 | 1993-01-04 | 5 | 3.277 | 2022-01-04 | 5 |  |  |  | 3.661 | 2022-01-04 | 2 |  |  |  |  | 3.3278 | 2022-01-04 | 6 | 3.738 | 2022-01-04 | 2 | 2.863 | 3.738 | 3.3734 | 25.94%
300 East/West Window | 3.014 | 1993-01-04 | 6 | 3.276 | 2022-01-04 | 5 |  |  |  | 3.681 | 2022-01-04 | 2 |  |  |  |  | 3.3278 | 2022-01-04 | 6 | 3.77 | 2022-01-04 | 2 | 3.014 | 3.77 | 3.4138 | 22.15%
310 East/West Shading | 3.015 | 1993-01-04 | 6 | 3.277 | 2022-01-04 | 5 |  |  |  | 3.669 | 2022-01-04 | 2 |  |  |  |  | 3.3278 | 2022-01-04 | 6 |  |  |  | 3.015 | 3.669 | 3.3222 | 19.69%
320 Thermostat | 2.861 | 1993-01-04 | 5 | 3.275 | 2022-01-04 | 5 |  |  |  | 3.651 | 2022-01-04 | 2 |  |  |  |  | 3.3361 | 2022-01-04 | 6 | 3.735 | 2022-01-04 | 3 | 2.861 | 3.735 | 3.3716 | 25.92%
395 Low Mass Solid Conduction | 2.062 | 1993-01-04 | 7 | 2.209 | 2022-01-04 | 8 | 2.328 | 2022-01-04 | 3 | 2.385 | 2022-01-04 | 3 |  | 2.263 | 2022-01-04 | 4 | 2.2211 | 2022-01-04 | 8 | 2.27 | 2022-01-04 | 3 | 2.062 | 2.385 | 2.2483 | 14.37%
400 Low Mass Opaque Windows | 2.867 | 1993-01-04 | 5 | 3.28 | 2022-01-04 | 5 | 3.476 | 2022-01-04 | 5 | 3.695 | 2022-01-04 | 2 |  | 3.342 | 2022-01-04 | 8 | 3.3361 | 2022-01-04 | 6 | 3.52 | 2022-01-04 | 2 | 2.867 | 3.695 | 3.3594 | 24.65%
410 Low Mass Infiltration | 3.625 | 1993-01-04 | 5 | 4.124 | 2022-01-04 | 5 | 4.233 | 2022-01-04 | 5 | 4.487 | 2022-01-04 | 2 |  | 4.227 | 2022-01-04 | 2 | 4.1139 | 2022-01-04 | 6 | 4.314 | 2022-01-04 | 2 | 3.625 | 4.487 | 4.1606 | 20.72%
420 Low Mass Internal Gains | 3.443 | 1993-01-04 | 5 | 3.944 | 2022-01-04 | 5 | 4.05 | 2022-01-04 | 5 | 4.287 | 2022-01-04 | 2 |  | 4.044 | 2022-01-04 | 2 | 3.9306 | 2022-01-04 | 6 | 4.126 | 2022-01-04 | 2 | 3.443 | 4.287 | 3.9749 | 21.23%
430 Low Mass Ext. Shortwave Absorptance | 3.442 | 1993-01-04 | 5 | 3.944 | 2022-01-04 | 5 | 4.05 | 2022-01-04 | 5 | 4.287 | 2022-01-04 | 2 |  | 4.044 | 2022-01-04 | 2 | 3.9306 | 2022-01-04 | 6 | 4.137 | 2022-01-04 | 2 | 3.442 | 4.287 | 3.9764 | 21.25%
440 Low Mass Cavity Albedo | 3.439 | 1993-01-04 | 5 | 3.942 | 2022-01-04 | 5 |  |  |  | 4.277 | 2022-01-04 | 2 |  |  |  |  | 3.9306 | 2022-01-04 | 6 | 4.376 | 2022-01-04 | 2 | 3.439 | 4.376 | 3.9929 | 23.47%
800 High Mass Opaque Windows | 3.227 | 1993-01-04 | 5 | 3.793 | 2022-01-04 | 7 | 3.909 | 2022-01-04 | 7 | 4.138 | 2022-01-04 | 2 |  | 3.902 | 2022-01-04 | 8 | 3.7861 | 2022-01-04 | 7 | 3.939 | 2022-01-04 | 7 | 3.227 | 4.138 | 3.8134 | 23.89%
810 High Mass Cavity Albedo | 2.979 | 1993-01-04 | 7 | 3.566 | 2022-01-04 | 7 |  |  |  | 3.915 | 2022-01-04 | 7 |  |  |  |  | 3.6056 | 2022-01-04 | 7 | 3.963 | 2022-01-04 | 7 | 2.979 | 3.963 | 3.6057 | 27.29%
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-4. Annual Hourly Integrated Peak Sensible Cooling Loads
Organization or Country: Case: Simulation Model:; DMU kW: ESP; US-IT kW: BLAST; NREL kW: DOE21D; NREL kW: SRES-SUN | SRES | S3PAS |  |  | TSYS |  |  | TASE |  |  | Example Result Statistics |  |  |  | HAP
Organization or Country: Case: Organization or Country:; DMU kW: DMU; US-IT kW: US-IT; NREL kW: NREL; NREL kW: NREL | BRE* | SPAIN |  |  | BEL-BRE |  |  | FINLAND |  |  | Min | Max | Mean | (Max-Min)/ | Carrier
Case | kW | Date | Hr | kW | Date | Hr | kW | Date | Hr | kW | Date | Hr |  | kW | Date | Hr | kW | Date | Hr | kW | Date | Hr | kW | kW | kW | Mean** (%) | kW | Date | Hr
600 Base Case, South Windows | 6.194 | 1993-10-17 | 13 | 5.965 | 2022-10-16 | 14 | 6.656 | 2022-10-16 | 13 | 6.827 | 2022-10-16 | 14 |  | 6.286 | 2022-11-25 | 14 | 6.4861 | 2009-10-16 | 14 | 6.812 | 2022-10-17 | 14 | 5.965 | 6.827 | 6.4609 | 13.34% | 7.346 | 2023-10-17 | 13
610 S. Windows + Overhang | 5.669 | 1993-11-25 | 13 | 5.824 | 2022-11-25 | 14 | 6.064 | 2022-01-13 | 14 | 6.371 | 2022-11-25 | 14 |  | 6.17 | 2022-11-25 | 14 | 5.675 | 2009-11-25 | 14 | 6.146 | 2022-10-17 | 14 | 5.669 | 6.371 | 5.9884 | 11.72% | 6.959 | 2023-12-23 | 13
620 East & West Windows | 3.634 | 1993-07-26 | 16 | 4.075 | 2022-07-26 | 17 | 4.43 | 2022-07-26 | 17 | 4.593 | 2022-07-26 | 17 |  | 4.297 | 2022-07-26 | 17 | 4.275 | 2009-07-26 | 17 | 5.096 | 2022-07-26 | 16 | 3.634 | 5.096 | 4.3429 | 33.66% | 4.615 | 2023-07-02 | 9
630 E&W Windows + Overhang & Fins | 3.072 | 1993-07-26 | 16 | 3.704 | 2022-07-26 | 17 | 3.588 | 2022-07-26 | 17 | 4.116 | 2022-07-26 | 17 |  | 3.665 | 2022-07-26 | 17 | 3.6083 | 2009-07-26 | 17 |  |  |  | 3.072 | 4.116 | 3.6256 | 28.8% | 3.934 | 2023-07-26 | 17
640 Case 600 with Htg. Temp. Setback | 6.161 | 1993-10-17 | 13 | 5.892 | 2022-10-16 | 14 | 6.576 | 2022-10-16 | 14 | 6.776 | 2022-10-16 | 14 |  | 6.25 | 2022-11-25 | 14 | 6.4417 | 2009-10-16 | 14 | 6.771 | 2022-10-17 | 14 | 5.892 | 6.776 | 6.4097 | 13.79% | 7.338 | 2023-10-17 | 13
650 Case 600 with Night Ventilation | 6.031 | 1993-10-17 | 13 | 5.831 | 2022-10-16 | 14 | 6.516 | 2022-10-16 | 14 | 6.671 | 2022-10-16 | 14 |  | 6.143 | 2022-11-25 | 14 | 6.3778 | 2009-10-17 | 14 | 6.679 | 2022-10-17 | 14 | 5.831 | 6.679 | 6.3213 | 13.42% | 7.169 | 2023-10-17 | 12
900 South Windows | 2.888 | 1993-10-17 | 14 | 3.155 | 2022-10-06 | 15 | 3.458 | 2022-10-17 | 14 | 3.871 | 2022-10-17 | 14 |  | 3.334 | 2022-10-17 | 15 | 3.5667 | 2009-10-17 | 15 | 3.457 | 2022-10-17 | 15 | 2.888 | 3.871 | 3.39 | 29% | 4.926 | 2023-10-17 | 13
910 S. Windows + Overhang | 1.896 | 1993-10-17 | 15 | 2.5 | 2022-10-21 | 15 | 2.336 | 2022-10-17 | 15 | 3.277 | 2022-10-17 | 15 |  | 2.786 | 2022-10-17 | 15 | 2.7917 | 2009-10-17 | 15 | 3.147 | 2022-10-17 | 15 | 1.896 | 3.277 | 2.6762 | 51.6% | 4.125 | 2023-10-17 | 14
920 East & West Windows | 2.385 | 1993-07-26 | 16 | 2.933 | 2022-07-26 | 17 | 3.109 | 2022-07-26 | 17 | 3.487 | 2022-07-26 | 17 |  | 3.071 | 2022-07-26 | 17 | 3.05 | 2009-07-26 | 17 | 3.505 | 2022-07-26 | 17 | 2.385 | 3.505 | 3.0771 | 36.4% | 3.727 | 2023-07-26 | 17
930 E&W Windows + Overhang & Fins | 1.873 | 1993-07-26 | 17 | 2.546 | 2022-07-26 | 17 | 2.388 | 2022-07-26 | 18 | 3.08 | 2022-07-26 | 17 |  | 2.486 | 2022-07-26 | 17 | 2.4983 | 2009-07-26 | 17 |  |  |  | 1.873 | 3.08 | 2.4786 | 48.7% | 3.304 | 2023-07-26 | 17
940 Case 900 with Htg. Temp. Setback | 2.888 | 1993-10-17 | 14 | 3.155 | 2022-10-06 | 15 | 3.458 | 2022-10-17 | 14 | 3.871 | 2022-10-17 | 14 |  | 3.334 | 2022-10-17 | 15 | 3.5667 | 2009-10-17 | 15 | 3.457 | 2022-10-17 | 15 | 2.888 | 3.871 | 3.39 | 29% | 4.985 | 2023-10-17 | 14
950 Case 900 with Night Ventilation | 2.033 | 1993-09-02 | 14 | 2.621 | 2022-09-02 | 15 | 2.664 | 2022-09-02 | 15 | 3.17 | 2022-09-02 | 14 |  | 2.677 | 2022-09-02 | 15 | 2.6861 | 2009-09-02 | 15 | 2.867 | 2022-09-02 | 14 | 2.033 | 3.17 | 2.674 | 42.52% | 3.495 | 2023-09-12 | 15
960 Sunspace | 0.953 | 1993-08-16 | 16 | 1.144 | 2022-07-26 | 16 | 1.057 | 2022-07-26 | 16 | 1.37 | 2022-07-26 | 16 |  | 1.179 | 2022-07-26 | 16 | 1.378 | 2009-07-26 | 16 | 1.403 | 2022-07-26 | 16 | 0.953 | 1.403 | 1.212 | 37.13% | 1.428 | 2023-07-26 | 16
Organization or Country: Case: 195 Solid Conduction; DMU kW: 0.651; DMU Date: 1993-07-26; DMU Hr: 15 | [10 empty] | 0.651 | 0.651 | 0.651 | 0%
Organization or Country: Case: 200 Surface Convection (Int & Ext IR="off"); DMU kW: 0.863; DMU Date: 1993-08-16; DMU Hr: 14 | [10 empty] | 0.863 | 0.863 | 0.863 | 0%
Organization or Country: Case: 210 Infrared Radiation (Int IR="off", Ext IR="on"); DMU kW: 0.476; DMU Date: 1993-08-16; DMU Hr: 16; US-IT kW: 1.017; US-IT Date: 2022-07-26; US-IT Hr: 15 |  |  |  |  | 1.0678 | 2009-07-26 | 16 | 1.142 | 2022-07-26 | 15 | 0.476 | 1.142 | 0.92569 | 71.95%
Organization or Country: Case: 215 Infrared Radiation (Int IR="on", Ext IR="off"); DMU kW: 1.007; DMU Date: 1993-08-11; DMU Hr: 14 | [10 empty] | 1.007 | 1.007 | 1.007 | 0%
220 In-Depth Base Case | 0.56 | 1993-07-27 | 15 | 1.166 | 2022-07-26 | 15 | 0.937 | 2022-07-27 | 14 | 1.34 | 2022-07-26 | 15 |  | 1.215 | 2022-07-26 | 16 | 1.1789 | 2009-07-26 | 16 | 1.213 | 2022-07-26 | 15 | 0.56 | 1.34 | 1.0871 | 71.75%
230 Infiltration | 1.059 | 1993-07-27 | 15 | 1.646 | 2022-07-26 | 15 | 1.455 | 2022-07-27 | 14 | 1.875 | 2022-07-26 | 15 |  | 1.7 | 2022-07-26 | 15 | 1.7078 | 2009-07-26 | 16 | 1.749 | 2022-07-26 | 15 | 1.059 | 1.875 | 1.5988 | 51.04%
240 Internal Gains | 0.739 | 1993-07-27 | 15 | 1.347 | 2022-07-26 | 15 | 1.119 | 2022-07-27 | 14 | 1.54 | 2022-07-26 | 15 |  | 1.398 | 2022-07-26 | 16 | 1.3614 | 2009-07-26 | 16 | 1.397 | 2022-07-26 | 15 | 0.739 | 1.54 | 1.2716 | 62.99%
250 Exterior Shortwave Absorptance | 3.36 | 1993-09-05 | 12 | 3.036 | 2022-09-05 | 12 | 2.605 | 2022-09-05 | 11 | 2.59 | 2022-08-26 | 14 |  | 2.258 | 2022-08-26 | 14 | 3.2278 | 2009-09-05 | 13 | 4.912 | 2022-09-05 | 12 | 2.258 | 4.912 | 3.1413 | 84.49%
270 South Windows | 6.356 | 1993-11-25 | 13 | 6.641 | 2022-11-25 | 14 |  |  |  | 7.234 | 2022-10-16 | 14 |  |  |  |  | 6.7639 | 2009-10-17 | 14 | 6.867 | 2022-10-16 | 14 | 6.356 | 7.234 | 6.7724 | 12.96%
280 Cavity Albedo | 4.444 | 1993-10-17 | 13 | 4.631 | 2022-11-25 | 13 |  |  |  | 5.22 | 2022-10-16 | 14 |  |  |  |  | 4.7861 | 2009-10-16 | 14 | 5.236 | 2022-10-16 | 14 | 4.444 | 5.236 | 4.8634 | 16.28%
290 South Shading | 6.269 | 1993-01-13 | 13 | 6.555 | 2022-11-25 | 14 |  |  |  | 6.976 | 2022-11-25 | 14 |  |  |  |  | 6.2028 | 2009-11-25 | 14 | 6.621 | 2022-11-25 | 14 | 6.2028 | 6.976 | 6.5248 | 11.85%
300 East/West Window | 3.404 | 1993-07-26 | 16 | 4.093 | 2022-07-26 | 17 |  |  |  | 4.657 | 2022-07-26 | 17 |  |  |  |  | 4.2778 | 2009-07-26 | 17 | 4.929 | 2022-07-26 | 17 | 3.404 | 4.929 | 4.2722 | 35.7%
310 East/West Shading | 2.848 | 1993-07-26 | 16 | 3.749 | 2022-06-30 | 17 |  |  |  | 4.164 | 2022-07-26 | 17 |  |  |  |  | 3.5889 | 2009-07-26 | 17 |  |  |  | 2.848 | 4.164 | 3.5875 | 36.68%
320 Thermostat | 5.701 | 1993-11-25 | 13 | 5.946 | 2022-11-25 | 14 |  |  |  | 6.553 | 2022-10-16 | 14 |  |  |  |  | 6.1778 | 2009-10-17 | 14 | 6.141 | 2022-10-16 | 14 | 5.701 | 6.553 | 6.1038 | 13.96%
395 Low Mass Solid Conduction | 0 |  |  | 0.362 | 2022-07-26 | 18 | 0 |  |  | 0.394 | 2022-07-26 | 17 |  | 0.356 | 2022-07-26 | 18 | 0.3625 | 2009-07-26 | 18 | 0.345 | 2022-07-26 | 18 | 0 | 0.394 | 0.25993 | 151.6%
400 Low Mass Opaque Windows | 0 |  |  | 0.581 | 2022-07-26 | 17 | 0.265 | 2022-07-27 | 17 | 0.666 | 2022-07-26 | 16 |  | 0.612 | 2022-07-26 | 17 | 0.61333 | 2009-07-26 | 17 | 0.572 | 2022-07-26 | 17 | 0 | 0.666 | 0.47276 | 140.9%
410 Low Mass Infiltration | 0.035 | 1993-07-27 | 16 | 0.699 | 2022-07-26 | 17 | 0.413 | 2022-07-27 | 17 | 0.814 | 2022-07-26 | 15 |  | 0.724 | 2022-07-26 | 16 | 0.74306 | 2009-07-26 | 17 | 0.71 | 2022-07-26 | 17 | 0.035 | 0.814 | 0.59115 | 131.8%
420 Low Mass Internal Gains | 0.258 | 1993-07-27 | 15 | 0.923 | 2022-07-26 | 15 | 0.631 | 2022-07-27 | 15 | 1.047 | 2022-07-26 | 15 |  | 0.938 | 2022-07-26 | 15 | 0.93778 | 2009-07-26 | 16 | 0.921 | 2022-07-26 | 15 | 0.258 | 1.047 | 0.80797 | 97.65%
430 Low Mass Ext. Shortwave Absorptance | 1.493 | 1993-08-16 | 14 | 1.772 | 2022-08-26 | 14 | 1.427 | 2022-08-16 | 14 | 1.762 | 2022-07-26 | 15 |  | 1.575 | 2022-07-26 | 15 | 1.7983 | 2009-09-05 | 13 | 2.578 | 2022-09-05 | 12 | 1.427 | 2.578 | 1.7722 | 64.95%
440 Low Mass Cavity Albedo | 4.546 | 1993-10-17 | 13 | 4.424 | 2022-10-16 | 14 |  |  |  | 5.053 | 2022-10-16 | 14 |  |  |  |  | 4.6861 | 2009-10-16 | 14 | 5.278 | 2022-10-17 | 14 | 4.424 | 5.278 | 4.7974 | 17.8%
800 High Mass Opaque Windows | 0.585 | 1993-07-27 | 14 | 0.967 | 2022-08-16 | 14 | 0.743 | 2022-07-28 | 14 | 1.352 | 2022-07-27 | 14 |  | 1.028 | 2022-07-27 | 15 | 0.98278 | 2009-08-16 | 14 | 1.358 | 2022-09-05 | 12 | 0.585 | 1.358 | 1.0023 | 77.13%
810 High Mass Cavity Albedo | 1.852 | 1993-09-02 | 14 | 2.357 | 2022-08-26 | 14 |  |  |  | 2.991 | 2022-09-02 | 14 |  |  |  |  | 2.3436 | 2009-09-02 | 14 | 2.862 | 2022-09-02 | 14 | 1.852 | 2.991 | 2.4811 | 45.91%
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-5. Free-Float Temperature Output
MAXIMUM ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Organization or Country: Case: Simulation Model:; DMU kW: ESP; US-IT kW: BLAST; NREL kW: DOE21D; NREL kW: SRES-SUN | SRES | S3PAS |  |  | TSYS |  |  | TASE |  |  | Example Result Statistics |  |  |  | HAP
Organization or Country: Case: Organization or Country:; DMU kW: DMU; US-IT kW: US-IT; NREL kW: NREL; NREL kW: NREL | BRE* | SPAIN |  |  | BEL-BRE |  |  | FINLAND |  |  | Min | Max | Mean | (Max-Min)/ | Carrier
Case | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | Date | Hr |  | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Date | Hr
600FF - Low Mass with S. Windows | 64.929 | 1993-10-17 | 15 | 65.11 | 2022-10-16 | 15 | 69.5 | 2022-10-17 | 15 | 68.6 | 2022-10-16 | 15 |  | 64.9 | 2022-10-16 | 16 | 65.25 | 2022-10-17 | 16 | 65.25 | 2022-10-15 | 16 | 64.9 | 69.5 | 66.2199 | 6.947% | 61.72 | 2023-10-17 | 16
900FF - High Mass with S. Windows | 41.812 | 1993-10-17 | 15 | 43.44 | 2022-09-02 | 16 | 42.7 | 2022-09-02 | 15 | 44.8 | 2022-09-02 | 15 |  | 43 | 2022-09-02 | 15 | 42.46 | 2022-10-17 | 15 | 43.17 | 2022-09-15 | 15 | 41.812 | 44.8 | 43.0546 | 6.94% | 45.61 | 2023-09-02 | 15
650FF Case 600FF with Night Ventilation | 63.236 | 1993-10-17 | 15 | 63.45 | 2022-10-16 | 15 | 68.2 | 2022-10-17 | 15 | 67 | 2022-10-16 | 15 |  | 63.3 | 2022-10-16 | 16 | 63.74 | 2022-10-17 | 16 | 63.82 | 2022-10-16 | 16 | 63.236 | 68.2 | 64.678 | 7.675% | 63.22 | 2023-10-17 | 15
950FF Case 900FF with Night Ventilation | 35.54 | 1993-09-02 | 16 | 36.23 | 2022-09-02 | 16 | 35.9 | 2022-09-02 | 16 | 38.5 | 2022-09-02 | 15 |  | 36.1 | 2022-09-02 | 16 | 35.67 | 2022-09-02 | 15 | 37.58 | 2022-09-15 | 16 | 35.54 | 38.5 | 36.5029 | 8.109% | 35.975 | 2023-09-02 | 16
960 Sunspace | 48.943 | 1993-10-17 | 15 | 48.88 | 2022-10-06 | 15 | 49 | 2022-10-17 | 15 | 51 | 2022-10-17 | 15 |  | 50.2 | 2022-10-17 | 15 | 55.34 | 2022-10-17 | 15 | 48.92 | 2022-10-15 | 15 | 48.88 | 55.34 | 50.3261 | 12.84% | 74.28 | 2023-10-17 | 14
MINIMUM ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Organization or Country: Case: Simulation Model:; DMU kW: ESP; US-IT kW: BLAST; NREL kW: DOE21D; NREL kW: SRES-SUN | SRES | S3PAS |  |  | TSYS |  |  | TASE |  |  | Example Result Statistics |  |  |  | HAP
Organization or Country: Case: Organization or Country:; DMU kW: DMU; US-IT kW: US-IT; NREL kW: NREL; NREL kW: NREL | BRE* | SPAIN |  |  | BEL-BRE |  |  | FINLAND |  |  | Min | Max | Mean | (Max-Min)/ | Carrier
Case | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | Date | Hr |  | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | Date | Hr | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C) | Date | Hr
600FF - Low Mass with S. Windows | -15.565 | 1993-01-04 | 7 | -17.05 | 2022-01-04 | 8 | -18.8 | 2022-01-04 | 8 | -18 | 2022-01-04 | 7 |  | -17.8 | 2022-01-04 | 8 | -17.81 | 2022-01-04 | 7 | -18.47 | 2022-01-08 | 9 | -18.8 | -15.565 | -17.6421 | 18.34% | -15.227 | 2023-01-04 | 8
900FF - High Mass with S. Windows | -1.647 | 1993-01-04 | 8 | -3.15 | 2022-01-04 | 8 | -4.3 | 2022-01-04 | 8 | -4.5 | 2022-01-04 | 8 |  | -4 | 2022-01-04 | 8 | -6.38 | 2022-01-04 | 8 | -5.64 | 2022-01-08 | 9 | -6.38 | -1.647 | -4.231 | 111.9% | -3.295 | 2023-01-04 | 8
650FF Case 600FF with Night Ventilation | -22.564 | 1993-01-04 | 6 | -22.96 | 2022-01-04 | 7 | -21.6 | 2022-01-04 | 2 | -23 | 2022-01-04 | 2 |  | -22.9 | 2022-01-04 | 2 | -22.83 | 2022-01-04 | 7 | -22.91 | 2022-01-02 | 23 | -23 | -21.6 | -22.6806 | 6.173% | -23.06 | 2023-01-04 | 7
950FF Case 900FF with Night Ventilation | -19.484 | 1993-01-04 | 6 | -20.04 | 2022-01-04 | 7 | -18.6 | 2022-01-04 | 7 | -19.7 | 2022-01-04 | 7 |  | -20.2 | 2022-01-04 | 7 | -19.34 | 2022-01-04 | 7 | -19.96 | 2022-01-07 | 22 | -20.2 | -18.6 | -19.6177 | 8.156% | -19.97 | 2023-01-04 | 7
960 Sunspace | 2.729 | 1993-02-06 | 6 | 1.63 | 2022-02-06 | 7 | 3.9 | 2022-02-06 | 7 | 3.1 | 2022-02-06 | 7 |  | 1.4 | 2022-02-06 | 6 | -2.82 | 2022-01-04 | 8 | -0.39 | 2022-02-05 | 7 | -2.82 | 3.9 | 1.3641 | 492.6% | -2.799 | 2023-02-06 | 6
AVERAGE ANNUAL HOURLY INTEGRATED ZONE TEMPERATURE
Organization or Country: Case: Simulation Model:; DMU kW: ESP; US-IT kW: BLAST; NREL kW: DOE21D; NREL kW: SRES-SUN | SRES | S3PAS |  |  | TSYS |  |  | TASE |  |  | Example Result Statistics |  |  |  | HAP
Organization or Country: Case: Organization or Country:; DMU kW: DMU; US-IT kW: US-IT; NREL kW: NREL; NREL kW: NREL | BRE | SPAIN |  |  | BEL-BRE |  |  | FINLAND |  |  | Min | Max | Mean | (Max-Min)/ | Carrier
Organization or Country: Case: Case; DMU kW: T (°C); US-IT kW: T (°C); NREL kW: T (°C); NREL kW: T (°C) | T (°C) | T (°C) |  |  | T (°C) |  |  | T (°C) |  |  | T (°C) | T (°C) | T (°C) | Mean** (%) | T (°C)
Organization or Country: Case: 600FF - Low Mass with S. Windows; DMU kW: 25.126; US-IT kW: 25.43; NREL kW: 24.6; NREL kW: 25.48 | 25.93 | 25.2 |  |  | 24.49 |  |  | 24.22 |  |  | 24.22 | 25.93 | 25.0595 | 6.824% | 28.05
Organization or Country: Case: 900FF - High Mass with S. Windows; DMU kW: 25.453; US-IT kW: 25.93; NREL kW: 24.7; NREL kW: 25.49 | 25.72 | 25.2 |  |  | 24.47 |  |  | 24.45 |  |  | 24.45 | 25.93 | 25.1766 | 5.878% | 27.08
Organization or Country: Case: 650FF Case 600FF with Night Ventilation; DMU kW: 18.234; US-IT kW: 18.69; NREL kW: 19.1; NREL kW: 18.96 | 19.62 | 18.4 |  |  | 17.99 |  |  | 18.36 |  |  | 17.99 | 19.62 | 18.6693 | 8.731% | 19.23
Organization or Country: Case: 950FF Case 900FF with Night Ventilation; DMU kW: 14.14; US-IT kW: 14.26; NREL kW: 14.3; NREL kW: 14.97 | 14.29 | 14 |  |  | 14.53 |  |  | 14.64 |  |  | 14 | 14.97 | 14.3913 | 6.74% | 14.18
Organization or Country: Case: 960 Sunspace; DMU kW: 27.49; US-IT kW: 27.72; NREL kW: 28; NREL kW: 28.69 | 28.54 | 28 |  |  | 28.96 |  |  | 26.43 |  |  | 26.43 | 28.96 | 27.9788 | 9.043% | 30.62
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 3
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-6. Low Mass Basic Sensitivity Tests
ANNUAL HEATING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
Case | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
610-600 Heat, S. Shade | 0.059 | 0.033 | 0.077 | 0.054 | 0.024 | 0.089 | 0.098 | 0.021 | 0.021 | 0.098 | 0.056875 | 135.4% | 0.003
620-600 Heat, E&W Orient. | 0.317 | 0.276 | 0.235 | 0.328 | 0.138 | 0.682 | 0.201 | 0.366 | 0.138 | 0.682 | 0.31788 | 171.1% | -0.013
630-620 Heat, E&W Shade | 0.437 | 0.31 | 0.525 | 0.329 | 0.267 | 0.531 | 0.551 |  | 0.267 | 0.551 | 0.42143 | 67.39% | 0.258
640-600 Heat, Htg. Setback | -1.545 | -1.885 | -2.166 | -1.971 | -1.793 | -1.817 | -1.829 | -2.053 | -2.166 | -1.545 | -1.8824 | 32.99% | -1.155
ANNUAL SENSIBLE COOLING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
Case | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
610-600 Cool, S. Shade | -2.222 | -1.582 | -2.227 | -1.83 | -2.186 | -1.728 | -1.891 | -1.272 | -2.227 | -1.272 | -1.8672 | 51.14% | -2.211
620-600 Cool, E&W Orient. | -2.72 | -2.341 | -2.745 | -2.645 | -2.96 | -2.481 | -2.591 | -2.427 | -2.96 | -2.341 | -2.6138 | 23.68% | -2.821
630-620 Cool, E&W Shade | -1.288 | -0.984 | -1.845 | -1.14 | -1.303 | -1.522 | -1.485 |  | -1.845 | -0.984 | -1.3667 | 63% | -1.587
640-600 Cool, Htg. Setback | -0.185 | -0.25 | -0.32 | -0.252 | -0.153 | -0.245 | -0.246 | -0.27 | -0.32 | -0.153 | -0.24012 | 69.55% | -0.282
650-600 Cool, Night Vent | -1.321 | -1.293 | -1.284 | -1.384 | -1.419 | -1.404 | -1.373 | -1.322 | -1.419 | -1.284 | -1.35 | 10% | -2.733
PEAK HEATING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
Case | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
610-600 Heat, S. Shade | 0 | 0.001 | -0.011 | 0 |  | 0 | -0.0083333 | 0 | -0.011 | 0.001 | -0.002619 | 458.2% | -0.034
620-600 Heat, E&W Orient. | 0.154 | 0.001 | 0.001 | 0.019 |  | 0.24 | -0.0083333 | 0.025 | -0.0083333 | 0.24 | 0.061667 | 402.7% | -0.156
630-620 Heat, E&W Shade | 0.001 | 0 | -0.021 | 0.003 |  | 0.001 | 0 |  | -0.021 | 0.003 | -0.0026667 | 900% | -0.025
640-600 Heat, Htg. Setback | 1.795 | 1.546 | 1.898 | 2.272 |  | 2.31 | 1.7917 | 2.6 | 1.546 | 2.6 | 2.0304 | 51.91% | 3.353
PEAK SENSIBLE COOLING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
Case | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
610-600 Cool, S. Shade | -0.525 | -0.141 | -0.592 | -0.456 |  | -0.116 | -0.81111 | -0.666 | -0.81111 | -0.116 | -0.47244 | 147.1% | -0.387
620-600 Cool, E&W Orient. | -2.56 | -1.89 | -2.226 | -2.234 |  | -1.989 | -2.2111 | -1.716 | -2.56 | -1.716 | -2.118 | 39.85% | -2.731
630-620 Cool, E&W Shade | -0.562 | -0.371 | -0.842 | -0.477 |  | -0.632 | -0.66667 |  | -0.842 | -0.371 | -0.59178 | 79.59% | -0.681
640-600 Cool, Htg. Setback | -0.033 | -0.073 | -0.08 | -0.051 |  | -0.036 | -0.044444 | -0.041 | -0.08 | -0.033 | -0.051206 | 91.79% | -0.008
650-600 Cool, Night Vent | -0.163 | -0.134 | -0.14 | -0.156 |  | -0.143 | -0.10833 | -0.133 | -0.163 | -0.10833 | -0.13962 | 39.15% | -0.177
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-7. High Mass Basic Sensitivity Tests
ANNUAL HEATING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
900-600 Mass, Heat | -3.126 | -3.163 | -3.837 | -3.329 | -3.608 | -3.152 | -3.217 | -3.321 | -3.837 | -3.126 | -3.3441 | 21.26% | -2.724
910-900 Heat, S. Shade | 0.405 | 0.252 | 0.382 | 0.277 | 0.294 | 0.333 | 0.442 | 0.179 | 0.179 | 0.442 | 0.3205 | 82.06% | 0.221
920-900 Heat, E&W Orient. | 2.143 | 2.142 | 2.383 | 2.196 | 2.07 | 2.505 | 2.121 | 2.259 | 2.07 | 2.505 | 2.2274 | 19.53% | 1.684
930-920 Heat, E&W Shade | 0.83 | 0.595 | 1.08 | 0.662 | 0.67 | 0.933 | 0.964 |  | 0.595 | 1.08 | 0.81914 | 59.21% | 0.689
940-900 Heat, Htg. Setback | -0.377 | -0.589 | -0.633 | -0.666 | -0.577 | -0.551 | -0.575 | -0.718 | -0.718 | -0.377 | -0.58575 | 58.22% | -0.441
960-900 Heat, Sunspace | 1.141 | 1.054 | 1.056 | 0.987 | 0.863 | 1.213 | 1.718 | 0.775 | 0.775 | 1.718 | 1.1009 | 85.66% | 0.689
ANNUAL SENSIBLE COOLING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
900-600 Mass, Cool | -4.005 | -3.833 | -4.624 | -4.113 | -4.549 | -3.92 | -4.007 | -4.179 | -4.624 | -3.833 | -4.1537 | 19.04% | -3.964
910-900 Cool, S. Shade | -1.311 | -1.067 | -1.479 | -1.293 | -1.561 | -1.144 | -1.159 | -0.832 | -1.561 | -0.832 | -1.2308 | 59.23% | -1.689
920-900 Cool, E&W Orient. | -0.292 | 0.016 | -0.015 | -0.222 | -0.323 | -0.115 | -0.067 | 0.014 | -0.323 | 0.016 | -0.1255 | 270.1% | -0.544
930-920 Cool, E&W Shade | -0.801 | -0.682 | -1.174 | -0.77 | -0.854 | -1.018 | -1.002 |  | -1.174 | -0.682 | -0.90014 | 54.66% | -1.091
940-900 Cool, Htg. Setback | -0.053 | -0.064 | -0.115 | -0.129 | -0.174 | -0.083 | -0.102 | -0.083 | -0.174 | -0.053 | -0.10038 | 120.5% | -0.401
950-900 Cool, Night Vent | -1.745 | -2.074 | -1.917 | -2.244 | -2.826 | -2.021 | -1.9244 | -1.828 | -2.826 | -1.745 | -2.0724 | 52.16% | -3.576
960-900 Cool, Sunspace | -1.644 | -1.934 | -2.027 | -2.362 | -2.697 | -1.929 | -2.0737 | -1.813 | -2.697 | -1.644 | -2.06 | 51.12% | -2.974
PEAK HEATING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
900-600 Mass, Heat | -0.587 | -0.487 | -0.488 | -0.498 |  | -0.429 | -0.41389 | -0.557 | -0.587 | -0.41389 | -0.49427 | 35.02% | -0.13
910-900 Heat, S. Shade | 0.008 | 0.003 | 0.007 | 0.004 |  | 0.01 | 0.019444 | 0.004 | 0.003 | 0.019444 | 0.0079206 | 207.6% | -0.022
920-900 Heat, E&W Orient. | 0.458 | 0.25 | 0.248 | 0.253 |  | 0.421 | 0.19167 | 0.264 | 0.19167 | 0.458 | 0.29795 | 89.39% | 0.043
930-920 Heat, E&W Shade | 0.047 | 0.029 | 0.027 | 0.029 |  | 0.035 | 0.036111 |  | 0.027 | 0.047 | 0.033852 | 59.08% | -0.015
940-900 Heat, Htg. Setback | 1.13 | 1.575 | 2.108 | 2.356 |  | 2.509 | 1.6056 | 2.631 | 1.13 | 2.631 | 1.9878 | 75.51% | 1.547
960-900 Heat, Sunspace | -0.44 | -0.702 | -0.83 | -0.897 |  | -0.756 | -0.99467 | -1.018 | -1.018 | -0.44 | -0.80538 | 71.77% | -1.068
PEAK SENSIBLE COOLING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
900-600 Mass, Cool | -3.306 | -2.81 | -3.198 | -2.956 |  | -2.952 | -2.9194 | -3.355 | -3.355 | -2.81 | -3.0709 | 17.75% | -2.42
910-900 Cool, S. Shade | -0.992 | -0.655 | -1.122 | -0.594 |  | -0.548 | -0.775 | -0.31 | -1.122 | -0.31 | -0.71371 | 113.8% | -0.801
920-900 Cool, E&W Orient. | -0.503 | -0.222 | -0.349 | -0.384 |  | -0.263 | -0.51667 | 0.048 | -0.51667 | 0.048 | -0.31281 | 180.5% | -1.199
930-920 Cool, E&W Shade | -0.512 | -0.387 | -0.721 | -0.407 |  | -0.585 | -0.55167 |  | -0.721 | -0.387 | -0.52728 | 63.34% | -0.423
940-900 Cool, Htg. Setback | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | ----- | 0.059
950-900 Cool, Night Vent | -0.855 | -0.534 | -0.794 | -0.701 |  | -0.657 | -0.88056 | -0.59 | -0.88056 | -0.534 | -0.71594 | 48.41% | -1.431
960-900 Cool, Sunspace | -1.935 | -2.011 | -2.401 | -2.501 |  | -2.155 | -2.1887 | -2.054 | -2.501 | -1.935 | -2.178 | 25.99% | -3.498
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 4
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-8. Low Mass In-Depth (Cases 195 thru 320) Sensitivity Tests
ANNUAL HEATING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES* | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
200-195 Surface Convection | 1.085 | [7 empty] | 1.085 | 1.085 | 1.085 | 0%
210-200 Ext IR (Int IR "off") | 1.204 | [7 empty] | 1.204 | 1.204 | 1.204 | 0%
220-215 Ext IR (Int IR "on") | 1.397 | [7 empty] | 1.397 | 1.397 | 1.397 | 0%
215-200 Int IR (Ext IR "off") | 0.295 | [7 empty] | 0.295 | 0.295 | 0.295 | 0%
220-210 Int IR (Ext IR "on") | 0.488 | 0.656 |  |  |  |  | 0.743 | 0.47 | 0.47 | 0.743 | 0.58925 | 46.33%
230-220 Infiltration | 3.432 | 3.525 | 3.456 | 3.531 | 3.522 | 3.615 | 3.543 | 3.527 | 3.432 | 3.615 | 3.5189 | 5.201%
240-220 Internal Gains | -1.295 | -1.206 | -1.339 | -1.333 | -1.341 | -1.228 | -1.221 | -1.203 | -1.341 | -1.203 | -1.2708 | 10.86%
250-220 Ext Solar Abs. | -2.193 | -1.476 | -1.763 | -1.494 | -1.474 | -1.448 | -1.533 | -1.699 | -2.193 | -1.448 | -1.635 | 45.57%
270-220 South Windows | -2.434 | -2.285 |  | -2.761 | -2.207 |  | -2.25 | -1.948 | -2.761 | -1.948 | -2.3142 | 35.13%
280-270 Cavity Albedo | 0.165 | 0.195 |  | 0.596 | 0.228 |  | 0.232 | 0.352 | 0.165 | 0.596 | 0.29467 | 146.3%
320-270 Thermostat | -0.651 | -0.721 |  | -0.714 | -0.779 |  | -0.699 | -0.649 | -0.779 | -0.649 | -0.70217 | 18.51%
290-270 South Shading | 0.067 | 0.029 |  | 0.065 | 0.022 |  | 0.085 | 0.02 | 0.02 | 0.085 | 0.048 | 135.4%
300-270 E&W Windows | 0.251 | 0.147 |  | 0.246 | 0.044 |  | 0.077 | 0.297 | 0.044 | 0.297 | 0.177 | 142.9%
310-300 E&W Shading | 0.46 | 0.25 |  | 0.263 | 0.201 |  | 0.486 |  | 0.201 | 0.486 | 0.332 | 85.84%
ANNUAL SENSIBLE COOLING [MWh]
| ESP | BLAST | DOE21D | SRES-SUN | SRES* | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
200-195 Surface Convection | 0.156 | [7 empty] | 0.156 | 0.156 | 0.156 | 0%
210-200 Ext IR (Int IR "off") | -0.408 | [7 empty] | -0.408 | -0.408 | -0.408 | 0%
220-215 Ext IR (Int IR "on") | -0.453 | [7 empty] | -0.453 | -0.453 | -0.453 | 0%
215-200 Int IR (Ext IR "off") | 0.069 | [7 empty] | 0.069 | 0.069 | 0.069 | 0%
220-210 Int IR (Ext IR "on") | 0.024 | 0.088 |  |  |  |  | 0.0689 | 0.042 | 0.024 | 0.088 | 0.055725 | 114.8%
230-220 Infiltration | 0.268 | 0.275 | 0.293 | 0.304 | 0.304 | 0.286 | 0.3032 | 0.302 | 0.268 | 0.304 | 0.2919 | 12.33%
240-220 Internal Gains | 0.229 | 0.371 | 0.261 | 0.412 | 0.411 | 0.374 | 0.3772 | 0.362 | 0.229 | 0.412 | 0.34965 | 52.34%
250-220 Ext Solar Abs. | 3.027 | 1.844 | 1.778 | 2.097 | 2.096 | 1.752 | 1.9472 | 2.697 | 1.752 | 3.027 | 2.1548 | 59.17%
270-220 South Windows | 7.342 | 7.969 |  | 9.001 | 9.515 |  | 8.0272 | 8.031 | 7.342 | 9.515 | 8.3142 | 26.14%
280-270 Cavity Albedo | -2.655 | -2.775 |  | -3.317 | -3.236 |  | -3.003 | -2.457 | -3.317 | -2.457 | -2.9072 | 29.58%
320-270 Thermostat | -2.467 | -2.764 |  | -3.103 | -3.046 |  | -2.808 | -3.051 | -3.103 | -2.467 | -2.8732 | 22.14%
290-270 South Shading | -2.324 | -1.659 |  | -1.957 | -2.261 |  | -2.065 | -1.283 | -2.324 | -1.283 | -1.9248 | 54.08%
300-270 E&W Windows | -3.226 | -2.834 |  | -3.163 | -3.25 |  | -3.043 | -2.933 | -3.25 | -2.834 | -3.0748 | 13.53%
310-300 E&W Shading | -1.57 | -1.266 |  | -1.42 | -1.629 |  | -1.994 |  | -1.994 | -1.266 | -1.5758 | 46.2%
PEAK HEATING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES* | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
200-195 Surface Convection | 0.647 | [7 empty] | 0.647 | 0.647 | 0.647 | 0%
210-200 Ext IR (Int IR "off") | 0.05 | [7 empty] | 0.05 | 0.05 | 0.05 | 0%
220-215 Ext IR (Int IR "on") | 0.08 | [7 empty] | 0.08 | 0.08 | 0.08 | 0%
215-200 Int IR (Ext IR "off") | 0.136 | [7 empty] | 0.136 | 0.136 | 0.136 | 0%
220-210 Int IR (Ext IR "on") | 0.166 | 0.307 |  |  |  |  | 0.35556 | 0.195 | 0.166 | 0.35556 | 0.25589 | 74.08%
230-220 Infiltration | 1.519 | 1.704 | 1.529 | 1.584 |  | 1.811 | 1.5556 | 1.587 | 1.519 | 1.811 | 1.6128 | 18.11%
240-220 Internal Gains | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.189 | -0.18333 | -0.187 | -0.2 | -0.18 | -0.18633 | 10.73%
250-220 Ext Solar Abs. | -0.001 | -0.001 | 0 | 0 |  | -0.007 | 0 | 0.005 | -0.007 | 0.005 | -0.00057143 | 2100%
270-220 South Windows | -0.004 | -0.003 |  | -0.034 |  |  | 0 | 0.218 | -0.034 | 0.218 | 0.0354 | 711.9%
280-270 Cavity Albedo | 0.001 | 0.001 |  | 0.024 |  |  | 0 | 0.021 | 0 | 0.024 | 0.0094 | 255.3%
320-270 Thermostat | -0.002 | -0.002 |  | -0.01 |  |  | 0 | -0.003 | -0.01 | 0 | -0.0034 | 294.1%
290-270 South Shading | 0 | 0 |  | 0 |  |  | -0.0083333 | 0 | -0.0083333 | 0 | -0.0016667 | 500%
300-270 E&W Windows | 0.151 | -0.001 |  | 0.02 |  |  | -0.0083333 | 0.032 | -0.0083333 | 0.151 | 0.038733 | 411.4%
310-300 E&W Shading | 0.001 | 0.001 |  | -0.012 |  |  | 0 |  | -0.012 | 0.001 | -0.0025 | 520%
PEAK SENSIBLE COOLING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES* | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
200-195 Surface Convection | 0.212 | [7 empty] | 0.212 | 0.212 | 0.212 | 0%
210-200 Ext IR (Int IR "off") | -0.387 | [7 empty] | -0.387 | -0.387 | -0.387 | 0%
220-215 Ext IR (Int IR "on") | -0.447 | [7 empty] | -0.447 | -0.447 | -0.447 | 0%
215-200 Int IR (Ext IR "off") | 0.144 | [7 empty] | 0.144 | 0.144 | 0.144 | 0%
220-210 Int IR (Ext IR "on") | 0.084 | 0.149 |  |  |  |  | 0.11111 | 0.071 | 0.071 | 0.149 | 0.10378 | 75.16%
230-220 Infiltration | 0.499 | 0.48 | 0.518 | 0.535 |  | 0.485 | 0.52889 | 0.536 | 0.48 | 0.536 | 0.5117 | 10.94%
240-220 Internal Gains | 0.179 | 0.181 | 0.182 | 0.2 |  | 0.183 | 0.1825 | 0.184 | 0.179 | 0.2 | 0.1845 | 11.38%
250-220 Ext Solar Abs. | 2.8 | 1.87 | 1.668 | 1.25 |  | 1.043 | 2.0489 | 3.699 | 1.043 | 3.699 | 2.0541 | 129.3%
270-220 South Windows | 5.796 | 5.475 |  | 5.894 |  |  | 5.585 | 5.654 | 5.475 | 5.894 | 5.6808 | 7.376%
280-270 Cavity Albedo | -1.912 | -2.01 |  | -2.014 |  |  | -1.9778 | -1.631 | -2.014 | -1.631 | -1.909 | 20.06%
320-270 Thermostat | -0.655 | -0.695 |  | -0.681 |  |  | -0.58611 | -0.726 | -0.726 | -0.58611 | -0.66862 | 20.92%
290-270 South Shading | -0.087 | -0.086 |  | -0.258 |  |  | -0.56111 | -0.246 | -0.56111 | -0.086 | -0.24762 | 191.9%
300-270 E&W Windows | -2.952 | -2.548 |  | -2.577 |  |  | -2.4861 | -1.938 | -2.952 | -1.938 | -2.5002 | 40.56%
310-300 E&W Shading | -0.556 | -0.344 |  | -0.493 |  |  | -0.68889 |  | -0.68889 | -0.344 | -0.52047 | 66.26%
* SRES-BRE (SERIRES 1.2) simulations for cases with interior solar absorptance = 0.9 have an input error that likely affects annual heating and cooling load sensitivities by
<0.2 MWh/y. (<6% for heating, <3% for cooling); see Annex B7, Section B7.1.1. Affected results involving Cases 270 and 290 throiugh 320 are indicated with italics.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 5
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-9. Low Mass In-Depth (Cases 395 thru 440) Sensitivity Tests
ANNUAL HEATING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
400-395 Surf. Conv. & IR | 1.916 | 2.276 | 2.935 | 2.767 | 2.772 | 2.32 | 2.311 | 2.487 | 1.916 | 2.935 | 2.473 | 41.21%
410-400 Infiltration | 1.696 | 1.798 | 1.736 | 1.76 | 1.761 | 1.732 | 1.77 | 1.759 | 1.696 | 1.798 | 1.7515 | 5.824%
420-410 Internal Gains | -1.298 | -1.263 | -1.355 | -1.361 | -1.361 | -1.245 | -1.239 | -1.222 | -1.361 | -1.222 | -1.293 | 10.75%
430-420 Ext Solar Abs. | -1.869 | -1.122 | -1.324 | -1.187 | -1.187 | -1.112 | -1.197 | -1.353 | -1.869 | -1.112 | -1.2939 | 58.51%
600-430 South Windows | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 | -2.118 | -1.133 | -1.633 | 60.32%
440-600 Cavity Albedo | 0.153 | 0.214 |  | 0.426 | 0.215 |  | 0.226 | 0.28 | 0.153 | 0.426 | 0.25233 | 108.2%
ANNUAL SENSIBLE COOLING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
400-395 Surf. Conv. & IR | 0 | 0.029 | 0.002 | 0.045 | 0.044 | 0.032 | 0.03439 | 0.033 | 0 | 0.045 | 0.027424 | 164.1%
410-400 Infiltration | 0 | 0.019 | 0.008 | 0.023 | 0.026 | 0.021 | 0.02239 | 0.021 | 0 | 0.026 | 0.017549 | 148.2%
420-410 Internal Gains | 0.011 | 0.088 | 0.041 | 0.105 | 0.104 | 0.091 | 0.09043 | 0.078 | 0.011 | 0.105 | 0.076054 | 123.6%
430-420 Ext Solar Abs. | 0.531 | 0.47 | 0.371 | 0.515 | 0.496 | 0.409 | 0.4599 | 0.732 | 0.371 | 0.732 | 0.49799 | 72.49%
600-430 South Windows | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 | 5.595 | 7.28 | 6.2036 | 27.16%
440-600 Cavity Albedo | -2.17 | -2.261 |  | -2.604 | -2.76 |  | -2.517 | -2.094 | -2.76 | -2.094 | -2.401 | 27.74%
PEAK HEATING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
400-395 Surf. Conv. & IR | 0.805 | 1.071 | 1.148 | 1.31 |  | 1.079 | 1.115 | 1.25 | 0.805 | 1.31 | 1.1111 | 45.45%
410-400 Infiltration | 0.758 | 0.844 | 0.757 | 0.792 |  | 0.885 | 0.77778 | 0.794 | 0.757 | 0.885 | 0.80111 | 15.98%
420-410 Internal Gains | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.183 | -0.18333 | -0.188 | -0.2 | -0.18 | -0.18562 | 10.77%
430-420 Ext Solar Abs. | -0.001 | 0 | 0 | 0 |  | 0 | 0 | 0.011 | -0.001 | 0.011 | 0.0014286 | 840%
600-430 South Windows | -0.005 | -0.004 | -0.005 | -0.029 |  | -0.007 | 0 | 0.217 | -0.029 | 0.217 | 0.023857 | 1031%
440-600 Cavity Albedo | 0.002 | 0.002 |  | 0.019 |  |  | 0 | 0.022 | 0 | 0.022 | 0.009 | 244.4%
PEAK SENSIBLE COOLING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
400-395 Surf. Conv. & IR | 0 | 0.219 | 0.265 | 0.272 |  | 0.256 | 0.25083 | 0.227 | 0 | 0.272 | 0.21283 | 127.8%
410-400 Infiltration | 0.035 | 0.118 | 0.148 | 0.148 |  | 0.112 | 0.12972 | 0.138 | 0.035 | 0.148 | 0.11839 | 95.45%
420-410 Internal Gains | 0.223 | 0.224 | 0.218 | 0.233 |  | 0.214 | 0.19472 | 0.211 | 0.19472 | 0.233 | 0.21682 | 17.65%
430-420 Ext Solar Abs. | 1.235 | 0.849 | 0.796 | 0.715 |  | 0.637 | 0.86056 | 1.657 | 0.637 | 1.657 | 0.96422 | 105.8%
600-430 South Windows | 4.701 | 4.193 | 5.229 | 5.065 |  | 4.711 | 4.6878 | 4.234 | 4.193 | 5.229 | 4.6887 | 22.1%
440-600 Cavity Albedo | -1.648 | -1.541 |  | -1.774 |  |  | -1.8 | -1.534 | -1.8 | -1.534 | -1.6594 | 16.03%
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-10. High Mass Basic and In-Depth Sensitivity Tests
ANNUAL HEATING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
800-430 Mass, w/ Op. Win. | -0.561 | -0.535 | -0.599 | -0.567 | -0.586 | -0.501 | -0.56 | -0.649 | -0.649 | -0.501 | -0.56975 | 25.98%
900-800 Himass, S. Win. | -3.698 | -4.343 | -5.356 | -4.714 | -4.612 | -4.431 | -4.285 | -3.82 | -5.356 | -3.698 | -4.4074 | 37.62%
900-810 Himass, Int. Sol. Abs. | -0.669 | -0.836 |  | -1.107 | -0.84 |  | -0.912 | -0.921 | -1.107 | -0.669 | -0.88083 | 49.73%
910-610 Mass, w/ S. Shade | -2.78 | -2.944 | -3.532 | -3.106 | -3.338 | -2.908 | -2.873 | -3.163 | -3.532 | -2.78 | -3.0805 | 24.41% | -2.506
920-620 Mass, w/ E&W Win. | -1.3 | -1.297 | -1.689 | -1.461 | -1.676 | -1.329 | -1.297 | -1.428 | -1.689 | -1.297 | -1.4346 | 27.32% | -1.027
930-630 Mass w/ E&W Shade | -0.907 | -1.012 | -1.134 | -1.128 | -1.273 | -0.927 | -0.884 |  | -1.273 | -0.884 | -1.0379 | 37.48% | -0.596
940-640 Mass, w/ Htg. Setback | -1.958 | -1.867 | -2.304 | -2.024 | -2.392 | -1.886 | -1.963 | -1.986 | -2.392 | -1.867 | -2.0475 | 25.64% | -2.01
ANNUAL SENSIBLE COOLING [MWh] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
800-430 Mass, w/ Op. Win. | -0.429 | -0.393 | -0.367 | -0.432 | -0.462 | -0.368 | -0.4101 | -0.55 | -0.55 | -0.367 | -0.42639 | 42.92%
900-800 Himass, S. Win. | 2.019 | 2.376 | 2.4 | 2.893 | 3.193 | 2.377 | 2.2777 | 2.274 | 2.019 | 3.193 | 2.4762 | 47.41%
900-810 Himass, Int. Sol. Abs. | 1.08 | 1.195 |  | 1.454 | 1.707 |  | 1.294 | 0.975 | 0.975 | 1.707 | 1.2842 | 57%
910-610 Mass, w/ S. Shade | -3.094 | -3.318 | -3.876 | -3.576 | -3.924 | -3.336 | -3.275 | -3.739 | -3.924 | -3.094 | -3.5173 | 23.6% | -3.442
920-620 Mass, w/ E&W Win. | -1.577 | -1.476 | -1.894 | -1.69 | -1.912 | -1.554 | -1.483 | -1.738 | -1.912 | -1.476 | -1.6655 | 26.18% | -1.687
930-630 Mass w/ E&W Shade | -1.09 | -1.174 | -1.223 | -1.32 | -1.463 | -1.05 | -1 |  | -1.463 | -1 | -1.1886 | 38.95% | -1.191
940-640 Mass, w/ Htg. Setback | -3.873 | -3.647 | -4.419 | -3.99 | -4.57 | -3.758 | -3.863 | -3.992 | -4.57 | -3.647 | -4.014 | 22.99% | -4.083
950-650 Mass, w/ Night Vent | -4.429 | -4.614 | -5.257 | -4.973 | -5.956 | -4.537 | -4.5584 | -4.685 | -5.956 | -4.429 | -4.8762 | 31.32% | -4.807
PEAK HEATING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
800-430 Mass, w/ Op. Win. | -0.215 | -0.151 | -0.141 | -0.149 |  | -0.142 | -0.14444 | -0.198 | -0.215 | -0.141 | -0.16292 | 45.42%
900-800 Himass, S. Win. | -0.377 | -0.34 | -0.352 | -0.378 |  | -0.294 | -0.26944 | -0.142 | -0.378 | -0.142 | -0.30749 | 76.75%
900-810 Himass, Int. Sol. Abs. | -0.129 | -0.113 |  | -0.155 |  |  | -0.088889 | -0.166 | -0.166 | -0.088889 | -0.13038 | 59.14%
910-610 Mass, w/ S. Shade | -0.579 | -0.485 | -0.47 | -0.494 |  | -0.419 | -0.38611 | -0.553 | -0.579 | -0.38611 | -0.48373 | 39.88% | -0.118
920-620 Mass, w/ E&W Win. | -0.283 | -0.238 | -0.241 | -0.264 |  | -0.248 | -0.21389 | -0.318 | -0.318 | -0.21389 | -0.25798 | 40.36% | 0.069
930-630 Mass w/ E&W Shade | -0.237 | -0.209 | -0.193 | -0.238 |  | -0.214 | -0.17778 |  | -0.238 | -0.17778 | -0.21146 | 28.48% | 0.079
940-640 Mass, w/ Htg. Setback | -1.252 | -0.458 | -0.278 | -0.414 |  | -0.23 | -0.6 | -0.526 | -1.252 | -0.23 | -0.53686 | 190.4% | -1.936
PEAK SENSIBLE COOLING [kW] | [8 empty] | Statistics for Example Results
| ESP | BLAST | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE |  |  |  | (Max-Min)/ | HAP
CASES | DMU | US-IT | NREL | NREL | BRE* | SPAIN | BEL-BRE | FINLAND | Min | Max | Mean | Mean** (%) | Carrier
800-430 Mass, w/ Op. Win. | -0.908 | -0.805 | -0.684 | -0.41 |  | -0.547 | -0.81556 | -1.22 | -1.22 | -0.41 | -0.76994 | 105.2%
900-800 Himass, S. Win. | 2.303 | 2.188 | 2.715 | 2.519 |  | 2.306 | 2.5839 | 2.099 | 2.099 | 2.715 | 2.3877 | 25.8%
900-810 Himass, Int. Sol. Abs. | 1.036 | 0.798 |  | 0.88 |  |  | 1.2231 | 0.595 | 0.595 | 1.2231 | 0.90641 | 69.29%
910-610 Mass, w/ S. Shade | -3.773 | -3.324 | -3.728 | -3.094 |  | -3.384 | -2.8833 | -2.999 | -3.773 | -2.8833 | -3.3122 | 26.86% | -2.834
920-620 Mass, w/ E&W Win. | -1.249 | -1.142 | -1.321 | -1.106 |  | -1.226 | -1.225 | -1.591 | -1.591 | -1.106 | -1.2657 | 38.32% | -0.888
930-630 Mass w/ E&W Shade | -1.199 | -1.158 | -1.2 | -1.036 |  | -1.179 | -1.11 |  | -1.2 | -1.036 | -1.147 | 14.3% | -0.63
940-640 Mass, w/ Htg. Setback | -3.273 | -2.737 | -3.118 | -2.905 |  | -2.916 | -2.875 | -3.314 | -3.314 | -2.737 | -3.0197 | 19.11% | -2.353
950-650 Mass, w/ Night Vent | -3.998 | -3.21 | -3.852 | -3.501 |  | -3.466 | -3.6917 | -3.812 | -3.998 | -3.21 | -3.6472 | 21.61% | -3.674
* SRES-BRE (SERIRES 1.2) simulations did not produce output for this variable.
** ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## Tables 6
ASHRAE Standard 140-2017, Informative Annex B8, Section B8.1
Example Results for Section 5.2 - Building Thermal Envelope and Fabric Load Cases 195-960 & 600FF-950FF
Note: The statistics in the tables below are based on the Standard 140 informative example results.
These statistics do not have any substantial importance and are not to be interpreted as acceptance criteria.
Table B8-11. Annual Transmissivity Coefficient of Windows
(ANNUAL UNSHADED TRANSMITTED SOLAR RADIATION)/(ANNUAL UNSHADED INCIDENT SOLAR RADIATION)
Simulation Model: | ESP | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND |  |  |  | (Max-Min)/ | Carrier
Case | [7 empty] | Min | Max | Mean | Mean* (%)
620 West | 0.67403 | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.65382 | 0.64771 | 0.64072 | 0.68694 | 0.6631 | 6.97% | 0.63006
600 South | 0.64973 | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.64663 | 0.62262 | 0.62262 | 0.67114 | 0.64576 | 7.514% | 0.61652
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-12. Annual Shading Coefficient of Window Shading Devices: Overhangs & Fins
(1-(ANNUAL SHADED TRANSMITTED SOLAR RADIATION)/(ANNUAL UNSHADED TRANSMITTED SOLAR RADIATION))
Simulation Model: | ESP | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND |  |  |  | (Max-Min)/ | Carrier
Case | [7 empty] | Min | Max | Mean | Mean* (%)
630/620 West | 0.18169 | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 0.33879 |  | 0.18169 | 0.34558 | 0.2678 | 61.2% | 0.27609
610/600 South | 0.17019 | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.20542 | 0.11488 | 0.11488 | 0.20932 | 0.17652 | 53.5% | 0.19593
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-13. Case 600 Annual Incident Solar Radiation (kWh/m2)
Simulation Model: | ESP | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND |  |  |  | (Max-Min)/ | Carrier
Case | [7 empty] | Min | Max | Mean | Mean* (%)
North | 427 | 434 | 456 | 407.3 | 457 | 367.4 | 453 | 367.4 | 457 | 428.8143 | 20.89% | 431.46
East | 959 | 1155 | 1083 | 1217.3 | 1082 | 1101 | 962 | 959 | 1217.3 | 1079.9 | 23.92% | 1177.84
West | 1086 | 1079 | 1003 | 856.5 | 1002 | 1012 | 1090 | 856.5 | 1090 | 1018.3571 | 22.93% | 1039.59
South | 1456 | 1566 | 1476 | 1467.7 | 1474 | 1522 | 1468 | 1456 | 1566 | 1489.9571 | 7.383% | 1545.41
Horizontal | 1797 | 1831 | 1832 | 1831.8 | 1832 | 1832 | 1832 | 1797 | 1832 | 1826.8286 | 1.916% | 1839.29
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-14. Case 600 Annual Transmitted Solar Radiation - Unshaded (kWh/m2)
Simulation Model: | ESP | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND |  |  |  | (Max-Min)/ | Carrier
Case | [7 empty] | Min | Max | Mean | Mean* (%)
West | 732 | 735 | 689 | 562.96 | 642 | 661.67 | 706 | 562.96 | 735 | 675.5186 | 25.47% | 655
South | 946 | 1051 | 962 | 954.3 | 926 | 984.17 | 914 | 914 | 1051 | 962.4957 | 14.23% | 952.78
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]
Table B8-15. Case 600 Annual Transmitted Solar Radiation - Shaded (kWh/m2)
Simulation Model: | ESP | DOE21D | SRES-SUN | SRES | S3PAS | TSYS | TASE | Statistics for Example Results |  |  |  | HAP
Organization or Country: | DMU | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND |  |  |  | (Max-Min)/ | Carrier
Case | [7 empty] | Min | Max | Mean | Mean* (%)
West | 599 | 481 | 554 | 441.3 | 431 | 437.5 |  | 431 | 599 | 490.6333 | 34.24% | 474.16
South | 785 | 831 | 803 | 774.86 | 757 | 782 | 809 | 757 | 831 | 791.6943 | 9.347% | 766.1
* ABS[ (Max-Min) / (Mean of Example Simulation Results) ]

## data for charts
Unformatted results for use in creating charts
ANNUAL LOADS | [13 empty] | LOW MASS QUALIFICATION TESTS
ANNUAL HEATING [MWH] | [13 empty] | ANNUAL HEATING [MWH]
| DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier | MIN | MAX |  | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier | MIN | MAX
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE
395 Solid Conduction | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839 |  | 4.799 | 5.835 | 5.0849 | 610-600 Low Mass, Heating S. Shade | 0.059 | 0.033 | 0.077 | 0.054 | 0.024 | 0.089 | 0.098 | 0.021 | 0.003 | 0.021 | 0.098
430 Opaque Windows | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51 |  | 5.429 | 7.827 | 6.7225 | 620-600 Low Mass, Heating E&W Orientation | 0.317 | 0.276 | 0.235 | 0.328 | 0.138 | 0.682 | 0.201 | 0.366 | -0.013 | 0.138 | 0.682
600 South Windows | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 4.872 | 5.362 | 4.467 | 4.296 | 5.709 | 5.0895 | 630-620 Low Mass, Heating E&W Shade | 0.437 | 0.31 | 0.525 | 0.329 | 0.267 | 0.531 | 0.551 |  | 0.258 | 0.267 | 0.551
610 S. Windows + Overhang | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 4.97 | 5.383 | 4.47 | 4.355 | 5.786 | 5.1464 | 640-600 Low Mass, Heating Heating Setback | -1.545 | -1.885 | -2.166 | -1.971 | -1.793 | -1.817 | -1.829 | -2.053 | -1.155 | -2.166 | -1.545
620 East & West Windows | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.073 | 5.728 | 4.454 | 4.613 | 5.944 | 5.4074
630 E&W Windows + Overhang & Fins | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 | 5.624 |  | 4.712 | 5.05 | 6.469 | 5.783
640 Case 600 with Htg. Temp. Setback | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.043 | 3.309 | 3.312 | 2.751 | 3.803 | 3.2071
650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 | 0 | 4.171e-06 | 5.2138e-07 | ANNUAL COOLING [MWH] | [9 empty] | RANGE | RANGE
[10 empty] | MIN | MAX |  | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 610-600 Low Mass, Cooling S. Shade | -2.222 | -1.582 | -2.227 | -1.83 | -2.186 | -1.728 | -1.891 | -1.272 | -2.211 | -2.227 | -1.272
800 Opaque Windows | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861 |  | 4.868 | 7.228 | 6.1527 | 620-600 Low Mass, Cooling E&W Orientation | -2.72 | -2.341 | -2.745 | -2.645 | -2.96 | -2.481 | -2.591 | -2.427 | -2.821 | -2.96 | -2.341
900 South Windows | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 1.655 | 2.041 | 1.743 | 1.17 | 2.041 | 1.7454 | 630-620 Low Mass, Cooling E&W Shade | -1.288 | -0.984 | -1.845 | -1.14 | -1.303 | -1.522 | -1.485 |  | -1.587 | -1.845 | -0.984
910 S. Windows + Overhang | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.097 | 2.22 | 1.964 | 1.575 | 2.282 | 2.0659 | 640-600 Low Mass, Cooling Heating Setback | -0.185 | -0.25 | -0.32 | -0.252 | -0.153 | -0.245 | -0.246 | -0.27 | -0.282 | -0.32 | -0.153
920 East & West Windows | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 3.776 | 4.3 | 3.427 | 3.313 | 4.3 | 3.9728 | 650-600 Low Mass, Cooling Night Ventilation | -1.321 | -1.293 | -1.284 | -1.384 | -1.419 | -1.404 | -1.373 | -1.322 | -2.733 | -1.419 | -1.284
930 E&W Windows + Overhang & Fins | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 | 4.74 |  | 4.116 | 4.143 | 5.335 | 4.7451
940 Case 900 with Htg. Temp. Setback | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.08 | 1.323 | 1.302 | 0.793 | 1.411 | 1.1596
950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 | 0 | 7.801e-06 | 9.7513e-07 | PEAK HEATING [KW] | [9 empty] | RANGE | RANGE
960 Sunspace | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 3.373 | 2.816 | 2.432 | 2.311 | 3.373 | 2.8462 | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
[13 empty] | 610-600 Low Mass, Heating S. Shade | 0 | 0.001 | -0.011 | 0 |  | 0 | -0.0083333 | 0 | -0.034 | -0.011 | 0.001
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 620-600 Low Mass, Heating E&W Orientation | 0.154 | 0.001 | 0.001 | 0.019 |  | 0.24 | -0.0083333 | 0.025 | -0.156 | -0.0083333 | 0.24
195 Solid Conduction | 4.167 | [8 empty] | 4.167 | 4.167 | 4.167 | 630-620 Low Mass, Heating E&W Shade | 0.001 | 0 | -0.021 | 0.003 |  | 0.001 | 0 |  | -0.025 | -0.021 | 0.003
200 Surface Convection Int IR="off" Ext IR="off" | 5.252 | [8 empty] | 5.252 | 5.252 | 5.252 | 640-600 Low Mass, Heating Heating Setback | 1.795 | 1.546 | 1.898 | 2.272 |  | 2.31 | 1.7917 | 2.6 | 3.353 | 1.546 | 2.6
210 Infrared Radiation Int IR="off" Ext IR="on" | 6.456 | 6.559 |  |  |  |  | 6.554 | 6.967 |  | 6.456 | 6.967 | 6.634
215 Infrared Radiation Int IR="on" Ext IR="off" | 5.547 | [8 empty] | 5.547 | 5.547 | 5.547 | PEAK COOLING [KW] | [9 empty] | RANGE | RANGE
220 In-Depth Base Case | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.297 | 7.437 |  | 6.944 | 8.787 | 7.6664 | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
230 Infiltration | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.84 | 10.964 |  | 10.376 | 12.243 | 11.1853 | [10 empty] | RANGE | RANGE
240 Internal Gains | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.076 | 6.234 |  | 5.649 | 7.448 | 6.3956 | 610-600 Low Mass, Cooling S. Shade | -0.525 | -0.141 | -0.592 | -0.456 |  | -0.116 | -0.81111 | -0.666 | -0.387 | -0.81111 | -0.116
250 Exterior Solar Absorptance | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.764 | 5.738 |  | 4.751 | 7.024 | 6.0314 | 620-600 Low Mass, Cooling E&W Orientation | -2.56 | -1.89 | -2.226 | -2.234 |  | -1.989 | -2.2111 | -1.716 | -2.731 | -2.56 | -1.716
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 630-620 Low Mass, Cooling E&W Shade | -0.562 | -0.371 | -0.842 | -0.477 |  | -0.632 | -0.66667 |  | -0.681 | -0.842 | -0.371
270 South Windows | 4.51 | 4.93 |  | 5.341 | 5.92 |  | 5.047 | 5.489 |  | 4.51 | 5.92 | 5.2062 | 640-600 Low Mass, Cooling Heating Setback | [9 empty] | 0 | 0
280 Cavity Albedo | 4.675 | 5.125 |  | 5.937 | 6.148 |  | 5.279 | 5.841 |  | 4.675 | 6.148 | 5.5008 | 650-600 Low Mass, Cooling Night Ventilation | -0.163 | -0.134 | -0.14 | -0.156 |  | -0.143 | -0.10833 | -0.133 | -0.177 | -0.163 | -0.10833
290 South Shading | 4.577 | 4.959 |  | 5.406 | 5.942 |  | 5.132 | 5.509 |  | 4.577 | 5.942 | 5.2542
300 East/West Windows | 4.761 | 5.077 |  | 5.587 | 5.964 |  | 5.124 | 5.786 |  | 4.761 | 5.964 | 5.3832
310 East/West Shading | 5.221 | 5.327 |  | 5.85 | 6.165 |  | 5.61 |  |  | 5.221 | 6.165 | 5.6346
320 Thermostat | 3.859 | 4.209 |  | 4.627 | 5.141 |  | 4.348 | 4.84 |  | 3.859 | 5.141 | 4.504 | High Mass QUALIFICATION TESTS
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | ANNUAL HEATING [MWH] | [9 empty] | RANGE | RANGE
395 Low Mass Solid Conduction | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839 |  | 4.799 | 5.835 | 5.0849 | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
400 Low Mass Opaque Windows | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.166 | 7.326 |  | 6.9 | 8.77 | 7.5579 | 900-600 Mass, Heating | -3.126 | -3.163 | -3.837 | -3.329 | -3.608 | -3.152 | -3.217 | -3.321 | -2.724 | -3.837 | -3.126
410 Low Mass Infiltration | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 8.936 | 9.085 |  | 8.596 | 10.506 | 9.3094 | 920-900 High Mass, Heating E&W Orientation | 2.143 | 2.142 | 2.383 | 2.196 | 2.07 | 2.505 | 2.121 | 2.259 | 1.684 | 2.07 | 2.505
420 Low Mass Internal Gains | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.697 | 7.863 |  | 7.298 | 9.151 | 8.0164 | 910-900 High Mass, Heating S. Shade | 0.405 | 0.252 | 0.382 | 0.277 | 0.294 | 0.333 | 0.442 | 0.179 | 0.221 | 0.179 | 0.442
430 Low Mass Ext. Shortwave Absorptance | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51 |  | 5.429 | 7.827 | 6.7225 | 930-920 High Mass, Heating E&W Shade | 0.83 | 0.595 | 1.08 | 0.662 | 0.67 | 0.933 | 0.964 |  | 0.689 | 0.595 | 1.08
440 Low Mass Cavity Albedo | 4.449 | 4.987 |  | 5.652 | 5.811 |  | 5.098 | 5.642 |  | 4.449 | 5.811 | 5.2732 | 940-900 High Mass, Heating Heating Setback | -0.377 | -0.589 | -0.633 | -0.666 | -0.577 | -0.551 | -0.575 | -0.718 | -0.441 | -0.718 | -0.377
800 High Mass Opaque Windows | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861 |  | 4.868 | 7.228 | 6.1527
810 High Mass Cavity Albedo | 1.839 | 2.446 |  | 3.004 | 2.828 |  | 2.567 | 2.962 |  | 1.839 | 3.004 | 2.6077
ANNUAL COOLING [MWH] | [12 empty] | 960-900 High Mass, Heating Sunspace | 1.141 | 1.054 | 1.056 | 0.987 | 0.863 | 1.213 | 1.718 | 0.775 | 0.689 | 0.775 | 1.718
CASE# | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier | MIN | MAX |  | ANNUAL COOLING [MWH] | [9 empty] | RANGE | RANGE
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
395 Solid Conduction | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011 |  | 0 | 0.016 | 0.0090363 | 900-600 Mass, Cooling | -4.005 | -3.833 | -4.624 | -4.113 | -4.549 | -3.92 | -4.007 | -4.179 | -3.964 | -4.624 | -3.833
430 Opaque Windows | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875 |  | 0.422 | 0.875 | 0.62805 | 910-900 High Mass, Cooling S. Shade | -1.311 | -1.067 | -1.479 | -1.293 | -1.561 | -1.144 | -1.159 | -0.832 | -1.689 | -1.561 | -0.832
600 South Windows | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.492 | 6.778 | 7.93 | 6.137 | 7.964 | 6.8316 | 920-900 High Mass, Cooling E&W Orientation | -0.292 | 0.016 | -0.015 | -0.222 | -0.323 | -0.115 | -0.067 | 0.014 | -0.544 | -0.323 | 0.016
610 S. Windows + Overhang | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 4.601 | 5.506 | 5.719 | 3.915 | 5.778 | 4.9644 | [10 empty] | 0 | 0
620 East & West Windows | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 3.901 | 4.351 | 5.109 | 3.417 | 5.004 | 4.2179 | 960-900 High Mass, Cooling Sunspace | -1.644 | -1.934 | -2.027 | -2.362 | -2.697 | -1.929 | -2.0737 | -1.813 | -2.974 | -2.697 | -1.644
630 E&W Windows + Overhang & Fins | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 | 2.416 |  | 3.522 | 2.129 | 3.701 | 2.8321 | 930-920 High Mass, Cooling E&W Shade | -0.801 | -0.682 | -1.174 | -0.77 | -0.854 | -1.018 | -1.002 |  | -1.091 | -1.174 | -0.682
640 Case 600 with Htg. Temp. Setback | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.246 | 6.508 | 7.648 | 5.952 | 7.811 | 6.5915 | 940-900 High Mass, Cooling Heating Setback | -0.053 | -0.064 | -0.115 | -0.129 | -0.174 | -0.083 | -0.102 | -0.083 | -0.401 | -0.174 | -0.053
650 Case 600 with Night Ventilation | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.119 | 5.456 | 5.197 | 4.816 | 6.545 | 5.4816 | 950-900 High Mass, Cooling Night Ventilation | -1.745 | -2.074 | -1.917 | -2.244 | -2.826 | -2.021 | -1.9244 | -1.828 | -3.576 | -2.826 | -1.745
[10 empty] | MIN | MAX |  | 960-900 High Mass, Cooling Sunspace | -1.644 | -1.934 | -2.027 | -2.362 | -2.697 | -1.929 | -2.0737 | -1.813 | -2.974 | -2.697 | -1.644
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE
800 Opaque Windows | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325 |  | 0.055 | 0.325 | 0.20166
900 South Windows | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.485 | 2.599 | 3.966 | 2.132 | 3.415 | 2.6779 | PEAK HEATING [KW] | [9 empty] | RANGE | RANGE
910 S. Windows + Overhang | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.326 | 1.767 | 2.277 | 0.821 | 1.872 | 1.4471 | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
920 East & West Windows | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.418 | 2.613 | 3.422 | 1.84 | 3.092 | 2.5524 | [10 empty] | RANGE | RANGE
930 E&W Windows + Overhang & Fins | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 | 1.416 |  | 2.331 | 1.039 | 2.238 | 1.6436 | 900-600 Mass, Heating | -0.587 | -0.487 | -0.488 | -0.498 |  | -0.429 | -0.41389 | -0.557 | -0.13 | -0.587 | -0.41389
940 Case 900 with Htg. Temp. Setback | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.383 | 2.516 | 3.565 | 2.079 | 3.241 | 2.5775 | 910-900 High Mass, Heating S. Shade | 0.008 | 0.003 | 0.007 | 0.004 |  | 0.01 | 0.019444 | 0.004 | -0.022 | 0.003 | 0.019444
950 Case 900 with Night Ventilation | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.5606 | 0.771 | 0.39 | 0.387 | 0.921 | 0.60545 | 920-900 High Mass, Heating E&W Orientation | 0.458 | 0.25 | 0.248 | 0.253 |  | 0.421 | 0.19167 | 0.264 | 0.043 | 0.19167 | 0.458
960 Sunspace | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.4113 | 0.786 | 0.992 | 0.4113 | 0.803 | 0.61791 | 930-920 High Mass, Heating E&W Shade | 0.047 | 0.029 | 0.027 | 0.029 |  | 0.035 | 0.036111 |  | -0.015 | 0.027 | 0.047
[13 empty] | 940-900 High Mass, Heating Heating Setback | 1.13 | 1.575 | 2.108 | 2.356 |  | 2.509 | 1.6056 | 2.631 | 1.547 | 1.13 | 2.631
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 960-900 High Mass, Heating Sunspace | -0.44 | -0.702 | -0.83 | -0.897 |  | -0.756 | -0.99467 | -1.018 | -1.068 | -1.018 | -0.44
195 Solid Conduction | 0.414 | [8 empty] | 0.414 | 0.414 | 0.414
200 Surface Convection Int IR="off" Ext IR="off" | 0.57 | [8 empty] | 0.57 | 0.57 | 0.57
210 Infrared Radiation Int IR="off" Ext IR="on" | 0.162 | 0.613 |  |  |  |  | 0.6679 | 0.641 |  | 0.162 | 0.6679 | 0.52097 | [10 empty] | RANGE | RANGE
215 Infrared Radiation Int IR="on" Ext IR="off" | 0.639 | [8 empty] | 0.639 | 0.639 | 0.639 | PEAK COOLING [KW] | [9 empty] | RANGE | RANGE
220 In-Depth Base Case | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.7368 | 0.683 |  | 0.186 | 0.835 | 0.63772 | CASES | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX
230 Infiltration | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 1.04 | 0.985 |  | 0.454 | 1.139 | 0.92963 | 900-600 Mass, Cooling | -3.306 | -2.81 | -3.198 | -2.956 |  | -2.952 | -2.9194 | -3.355 | -2.42 | -3.355 | -2.81
240 Internal Gains | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.114 | 1.045 |  | 0.415 | 1.246 | 0.98738 | 910-900 High Mass, Cooling S. Shade | -0.992 | -0.655 | -1.122 | -0.594 |  | -0.548 | -0.775 | -0.31 | -0.801 | -1.122 | -0.31
250 Exterior Solar Absorptance | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 2.684 | 3.38 |  | 2.177 | 3.38 | 2.7925 | 920-900 High Mass, Cooling E&W Orientation | -0.503 | -0.222 | -0.349 | -0.384 |  | -0.263 | -0.51667 | 0.048 | -1.199 | -0.51667 | 0.048
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 930-920 High Mass, Cooling E&W Shade | -0.512 | -0.387 | -0.721 | -0.407 |  | -0.585 | -0.55167 |  | -0.423 | -0.721 | -0.387
270 South Windows | 7.528 | 8.67 |  | 9.828 | 10.35 |  | 8.764 | 8.714 |  | 7.528 | 10.35 | 8.9757
280 Cavity Albedo | 4.873 | 5.895 |  | 6.511 | 7.114 |  | 5.761 | 6.257 |  | 4.873 | 7.114 | 6.0685 | 940-900 High Mass, Cooling Heating Setback | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0.059 | 0 | 0
290 South Shading | 5.204 | 7.011 |  | 7.871 | 8.089 |  | 6.699 | 7.431 |  | 5.204 | 8.089 | 7.0508 | 950-900 High Mass, Cooling Night Ventilation | -0.855 | -0.534 | -0.794 | -0.701 |  | -0.657 | -0.88056 | -0.59 | -1.431 | -0.88056 | -0.534
300 East/West Windows | 4.302 | 5.836 |  | 6.665 | 7.1 |  | 5.721 | 5.781 |  | 4.302 | 7.1 | 5.9008 | 960-900 High Mass, Cooling Sunspace | -1.935 | -2.011 | -2.401 | -2.501 |  | -2.155 | -2.1887 | -2.054 | -3.498 | -2.501 | -1.935
310 East/West Shading | 2.732 | 4.57 |  | 5.245 | 5.471 |  | 3.727 |  |  | 2.732 | 5.471 | 4.349
320 Thermostat | 5.061 | 5.906 |  | 6.725 | 7.304 |  | 5.956 | 5.663 |  | 5.061 | 7.304 | 6.1025
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Low Mass Solid Conduction | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011 |  | 0 | 0.016 | 0.0090363
400 Low Mass Opaque Windows | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.04468 | 0.044 |  | 0 | 0.061 | 0.03646
410 Low Mass Infiltration | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.06707 | 0.065 |  | 0 | 0.084 | 0.054009
420 Low Mass Internal Gains | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.1575 | 0.143 |  | 0.011 | 0.189 | 0.13006 | Low Mass PRIMITIVE DIAGNOSTIC TESTS
430 Low Mass Ext. Shortwave Absorptance | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875 |  | 0.422 | 0.875 | 0.62805
440 Low Mass Cavity Albedo | 3.967 | 4.172 |  | 4.674 | 5.204 |  | 3.975 | 4.684 |  | 3.967 | 5.204 | 4.446 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
800 High Mass Opaque Windows | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325 |  | 0.055 | 0.325 | 0.20166 | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
810 High Mass Cavity Albedo | 1.052 | 1.405 |  | 1.711 | 1.708 |  | 1.191 | 1.624 |  | 1.052 | 1.711 | 1.4485 | ANNUAL HEATING [MWH]
[13 empty] | 200-195 Heating Surface Convection | 1.085 | [8 empty] | 1.085 | 1.085
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [12 empty] | 210-200 Heating Ext IR (Int IR "off") | 1.204 | [8 empty] | 1.204 | 1.204
[13 empty] | 220-215 Heating Ext IR (Int IR "on") | 1.397 | [8 empty] | 1.397 | 1.397
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier | RANGE | RANGE |  | 215-200 Heating Int IR (Ext IR "off") | 0.295 | [8 empty] | 0.295 | 0.295
CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | AVERAGE | 220-210 Heating Int IR (Ext IR "on") | 0.488 | 0.656 |  |  |  |  | 0.743 | 0.47 |  | 0.47 | 0.743
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Solid Conduction | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.2211 | 2.27 |  | 2.062 | 2.385 | 2.2483
430 Opaque Windows | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.137 |  | 3.442 | 4.287 | 3.9764 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
600 South Windows | 3.437 | 3.94 | 4.045 | 4.258 |  | 4.037 | 3.9306 | 4.354 | 3.945 | 3.437 | 4.354 | 4.0002 | 230-220 Heating Infiltration | 3.432 | 3.525 | 3.456 | 3.531 | 3.522 | 3.615 | 3.543 | 3.527 |  | 3.432 | 3.615
610 S. Windows + Overhang | 3.437 | 3.941 | 4.034 | 4.258 |  | 4.037 | 3.9222 | 4.354 | 3.911 | 3.437 | 4.354 | 3.9976 | 240-220 Heating Internal Gains | -1.295 | -1.206 | -1.339 | -1.333 | -1.341 | -1.228 | -1.221 | -1.203 |  | -1.341 | -1.203
620 East & West Windows | 3.591 | 3.941 | 4.046 | 4.277 |  | 4.277 | 3.9222 | 4.379 | 3.789 | 3.591 | 4.379 | 4.0619 | 250-220 Heating Ext Solar Absorptance | -2.193 | -1.476 | -1.763 | -1.494 | -1.474 | -1.448 | -1.533 | -1.699 |  | -2.193 | -1.448
630 E&W Windows + Overhang & Fins | 3.592 | 3.941 | 4.025 | 4.28 |  | 4.278 | 3.9222 |  | 3.764 | 3.592 | 4.28 | 4.0064 | 270-220 Heating South Windows | -2.434 | -2.285 |  | -2.761 | -2.207 |  | -2.25 | -1.948 |  | -2.761 | -1.948
640 Case 600 with Htg. Temp. Setback | 5.232 | 5.486 | 5.943 | 6.53 |  | 6.347 | 5.7222 | 6.954 | 7.298 | 5.232 | 6.954 | 6.0306 | 280-270 Heating Cavity Albedo | 0.165 | 0.195 |  | 0.596 | 0.228 |  | 0.232 | 0.352 |  | 0.165 | 0.596
650 Case 600 with Night Ventilation | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0
[13 empty] | 290-270 Heating South Shading | 0.067 | 0.029 |  | 0.065 | 0.022 |  | 0.085 | 0.02 |  | 0.02 | 0.085
[10 empty] | RANGE | RANGE |  | 300-270 Heating E&W Windows | 0.251 | 0.147 |  | 0.246 | 0.044 |  | 0.077 | 0.297 |  | 0.044 | 0.297
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX | AVERAGE |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
800 Opaque Windows | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.7861 | 3.939 |  | 3.227 | 4.138 | 3.8134 | 320-270 Heating Thermostat | -0.651 | -0.721 |  | -0.714 | -0.779 |  | -0.699 | -0.649 |  | -0.779 | -0.649
900 South Windows | 2.85 | 3.453 | 3.557 | 3.76 |  | 3.608 | 3.5167 | 3.797 | 3.815 | 2.85 | 3.797 | 3.506 | 310-300 Heating E&W Shading | 0.46 | 0.25 |  | 0.263 | 0.201 |  | 0.486 |  |  | 0.201 | 0.486
910 S. Windows + Overhang | 2.858 | 3.456 | 3.564 | 3.764 |  | 3.618 | 3.5361 | 3.801 | 3.793 | 2.858 | 3.801 | 3.5139
920 East & West Windows | 3.308 | 3.703 | 3.805 | 4.013 |  | 4.029 | 3.7083 | 4.061 | 3.858 | 3.308 | 4.061 | 3.8039 | ANNUAL COOLING [MWH]
930 E&W Windows + Overhang & Fins | 3.355 | 3.732 | 3.832 | 4.042 |  | 4.064 | 3.7444 |  | 3.843 | 3.355 | 4.064 | 3.7949 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
940 Case 900 with Htg. Temp. Setback | 3.98 | 5.028 | 5.665 | 6.116 |  | 6.117 | 5.1222 | 6.428 | 5.362 | 3.98 | 6.428 | 5.4937 | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier | MIN | MAX
950 Case 900 with Night Ventilation | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200-195 Cooling Surface Convection | 0.156 | [8 empty] | 0.156 | 0.156
960 Sunspace | 2.41 | 2.751 | 2.727 | 2.863 |  | 2.852 | 2.522 | 2.779 | 2.747 | 2.41 | 2.863 | 2.7006 | 210-200 Cooling Ext IR (Int IR "off") | -0.408 | [8 empty] | -0.408 | -0.408
[13 empty] | 220-215 Cooling Ext IR (Int IR "on") | -0.453 | [8 empty] | -0.453 | -0.453
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 215-200 Cooling Int IR (Ext IR "off") | 0.069 | [8 empty] | 0.069 | 0.069
195 Solid Conduction | 2.004 | [8 empty] | 2.004 | 2.004 | 2.004 |  | 0.024 | 0.088 |  |  |  |  | 0.0689 | 0.042 |  | 0.024 | 0.088
200 Surface Convection Int IR="off" Ext IR="off" | 2.651 | [8 empty] | 2.651 | 2.651 | 2.651
210 Infrared Radiation Int IR="off" Ext IR="on" | 2.701 | 2.973 |  |  |  |  | 2.9806 | 3.325 |  | 2.701 | 3.325 | 2.9949 | 230-220 Cooling Infiltration | 0.268 | 0.275 | 0.293 | 0.304 | 0.304 | 0.286 | 0.3032 | 0.302 |  | 0.268 | 0.304
215 Infrared Radiation Int IR="on" Ext IR="off" | 2.787 | [8 empty] | 2.787 | 2.787 | 2.787 | 240-220 Cooling Internal Gains | 0.229 | 0.371 | 0.261 | 0.412 | 0.411 | 0.374 | 0.3772 | 0.362 |  | 0.229 | 0.412
220 In-Depth Base Case | 2.867 | 3.28 | 3.465 | 3.695 |  | 3.348 | 3.3361 | 3.52 |  | 2.867 | 3.695 | 3.3587 | 250-220 Cooling Ext Solar Abs. | 3.027 | 1.844 | 1.778 | 2.097 | 2.096 | 1.752 | 1.9472 | 2.697 |  | 1.752 | 3.027
230 Infiltration | 4.386 | 4.984 | 4.994 | 5.279 |  | 5.159 | 4.8917 | 5.107 |  | 4.386 | 5.279 | 4.9715 | 270-220 Cooling South Windows | 7.342 | 7.969 |  | 9.001 | 9.515 |  | 8.0272 | 8.031 |  | 7.342 | 9.515
240 Internal Gains | 2.685 | 3.1 | 3.282 | 3.495 |  | 3.159 | 3.1528 | 3.333 |  | 2.685 | 3.495 | 3.1724 | 280-270 Cooling Cavity Albedo | -2.655 | -2.775 |  | -3.317 | -3.236 |  | -3.003 | -2.457 |  | -3.317 | -2.457
250 Exterior Solar Absorptance | 2.866 | 3.279 | 3.465 | 3.695 |  | 3.341 | 3.3361 | 3.525 |  | 2.866 | 3.695 | 3.3582 | 320-270 Cooling Thermostat | -2.467 | -2.764 |  | -3.103 | -3.046 |  | -2.808 | -3.051 |  | -3.103 | -2.467
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | RANGE | RANGE | AVERAGE | 290-270 Cooling South Shading | -2.324 | -1.659 |  | -1.957 | -2.261 |  | -2.065 | -1.283 |  | -2.324 | -1.283
270 South Windows | 2.863 | 3.277 |  | 3.661 |  |  | 3.3361 | 3.738 |  | 2.863 | 3.738 | 3.375 | 300-270 Cooling E&W Windows | -3.226 | -2.834 |  | -3.163 | -3.25 |  | -3.043 | -2.933 |  | -3.25 | -2.834
280 Cavity Albedo | 2.864 | 3.278 |  | 3.685 |  |  | 3.3361 | 3.759 |  | 2.864 | 3.759 | 3.3844 | 310-300 Cooling E&W Shading | -1.57 | -1.266 |  | -1.42 | -1.629 |  | -1.994 |  |  | -1.994 | -1.266
290 South Shading | 2.863 | 3.277 |  | 3.661 |  |  | 3.3278 | 3.738 |  | 2.863 | 3.738 | 3.3734 | PEAK HEATING [KW]
300 East/West Windows | 3.014 | 3.276 |  | 3.681 |  |  | 3.3278 | 3.77 |  | 3.014 | 3.77 | 3.4138 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
310 East/West Shading | 3.015 | 3.277 |  | 3.669 |  |  | 3.3278 |  |  | 3.015 | 3.669 | 3.015 | 200-195 Heating Surface Convection | 0.647 | [8 empty] | 0.647 | 0.647
320 Thermostat | 2.861 | 3.275 |  | 3.651 |  |  | 3.3361 | 3.735 |  | 2.861 | 3.735 | 2.861 | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
395 Low Mass Solid Conduction | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.2211 | 2.27 |  | 2.062 | 2.385 | 2.2483 | 210-200 Heating Ext IR (Int IR "off") | 0.05 | [8 empty] | 0.05 | 0.05
400 Low Mass Opaque Windows | 2.867 | 3.28 | 3.476 | 3.695 |  | 3.342 | 3.3361 | 3.52 |  | 2.867 | 3.695 | 3.3594 | 220-215 Heating Ext IR (Int IR "on") | 0.08 | [8 empty] | 0.08 | 0.08
410 Low Mass Infiltration | 3.625 | 4.124 | 4.233 | 4.487 |  | 4.227 | 4.1139 | 4.314 |  | 3.625 | 4.487 | 4.1606 | 220-210 Heating Int IR (Ext IR "on") | 0.166 | 0.307 |  |  |  |  | 0.35556 | 0.195 |  | 0.166 | 0.35556
420 Low Mass Internal Gains | 3.443 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.126 |  | 3.443 | 4.287 | 3.9749 | 215-200 Heating Int IR (Ext IR "off") | 0.136 | [8 empty] | 0.136 | 0.136
430 Low Mass Ext. Shortwave Absorptance | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.137 |  | 3.442 | 4.287 | 3.9764 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
440 Low Mass Cavity Albedo | 3.439 | 3.942 |  | 4.277 |  |  | 3.9306 | 4.376 |  | 3.439 | 4.376 | 3.9929 | 230-220 Heating Infiltration | 1.519 | 1.704 | 1.529 | 1.584 |  | 1.811 | 1.5556 | 1.587 |  | 1.519 | 1.811
800 High Mass Opaque Windows | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.7861 | 3.939 |  | 3.227 | 4.138 | 3.8134 | 240-220 Heating Internal Gains | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.189 | -0.18333 | -0.187 |  | -0.2 | -0.18
810 High Mass Cavity Albedo | 2.979 | 3.566 |  | 3.915 |  |  | 3.6056 | 3.963 |  | 2.979 | 3.963 | 3.6057 | 250-220 Heating Ext Solar Absorpance | -0.001 | -0.001 | 0 | 0 |  | -0.007 | 0 | 0.005 |  | -0.007 | 0.005
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [12 empty] | 270-220 Heating South Windows | -0.004 | -0.003 |  | -0.034 |  |  | 0 | 0.218 |  | -0.034 | 0.218
[13 empty] | 280-270 Heating Cavity Albedo | 0.001 | 0.001 |  | 0.024 |  |  | 0 | 0.021 |  | 0 | 0.024
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier | RANGE | RANGE |  | 320-270 Heating Thermostat | -0.002 | -0.002 |  | -0.01 |  |  | 0 | -0.003 |  | -0.01 | 0
CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | AVERAGE | 290-270 Heating South Shading | 0 | 0 |  | 0 |  |  | -0.0083333 | 0 |  | -0.0083333 | 0
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Solid Conduction | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.3625 | 0.345 |  | 0 | 0.394 | 0.25993
430 Opaque Windows | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 1.7983 | 2.578 |  | 1.427 | 2.578 | 1.7722 | 215-210 | 0.086 | [8 empty] | 0.086 | 0.086
600 South Windows | 6.194 | 5.965 | 6.656 | 6.827 |  | 6.286 | 6.4861 | 6.812 | 7.346 | 5.965 | 6.827 | 6.4609 | 300-270 Heating E&W Windows | 0.151 | -0.001 |  | 0.02 |  |  | -0.0083333 | 0.032 |  | -0.0083333 | 0.151
610 S. Windows + Overhang | 5.669 | 5.824 | 6.064 | 6.371 |  | 6.17 | 5.675 | 6.146 | 6.959 | 5.669 | 6.371 | 5.9884 | 310-300 Heating E&W Shading | 0.001 | 0.001 |  | -0.012 |  |  | 0 |  |  | -0.012 | 0.001
620 East & West Windows | 3.634 | 4.075 | 4.43 | 4.593 |  | 4.297 | 4.275 | 5.096 | 4.615 | 3.634 | 5.096 | 4.3429 | PEAK COOLING [KW]
630 E&W Windows + Overhang & Fins | 3.072 | 3.704 | 3.588 | 4.116 |  | 3.665 | 3.6083 |  | 3.934 | 3.072 | 4.116 | 3.6256 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
640 Case 600 with Htg. Temp. Setback | 6.161 | 5.892 | 6.576 | 6.776 |  | 6.25 | 6.4417 | 6.771 | 7.338 | 5.892 | 6.776 | 6.4097 | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
650 Case 600 with Night Ventilation | 6.031 | 5.831 | 6.516 | 6.671 |  | 6.143 | 6.3778 | 6.679 | 7.169 | 5.831 | 6.679 | 6.3213 | 200-195 Cooling Surface Convection | 0.212 | [8 empty] | 0.212 | 0.212
[13 empty] | 210-200 Cooling Ext IR (Int IR "off") | -0.387 | [8 empty] | -0.387 | -0.387
[13 empty] | 220-215 Cooling Ext IR (Int IR on) | -0.447 | [8 empty] | -0.447 | -0.447
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | [13 empty] | 0 | 0
800 Opaque Windows | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 0.98278 | 1.358 |  | 0.585 | 1.358 | 1.0023 | 215-200 Cooling Int IR (Ext IR "off") | 0.144 | [8 empty] | 0.144 | 0.144
900 South Windows | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 4.926 | 2.888 | 3.871 | 3.39 | 220-210 Cooling Int IR (Ext IR "on") | 0.084 | 0.149 |  |  |  |  | 0.11111 | 0.071 |  | 0.071 | 0.149
910 S. Windows + Overhang | 1.896 | 2.5 | 2.336 | 3.277 |  | 2.786 | 2.7917 | 3.147 | 4.125 | 1.896 | 3.277 | 2.6762 | 230-220 Cooling Infiltration | 0.499 | 0.48 | 0.518 | 0.535 |  | 0.485 | 0.52889 | 0.536 |  | 0.48 | 0.536
920 East & West Windows | 2.385 | 2.933 | 3.109 | 3.487 |  | 3.071 | 3.05 | 3.505 | 3.727 | 2.385 | 3.505 | 3.0771 | 240-220 Cooling Internal Gains | 0.179 | 0.181 | 0.182 | 0.2 |  | 0.183 | 0.1825 | 0.184 |  | 0.179 | 0.2
930 E&W Windows + Overhang & Fins | 1.873 | 2.546 | 2.388 | 3.08 |  | 2.486 | 2.4983 |  | 3.304 | 1.873 | 3.08 | 2.4786 | 250-220 Cooling Ext Solar Absorpance | 2.8 | 1.87 | 1.668 | 1.25 |  | 1.043 | 2.0489 | 3.699 |  | 1.043 | 3.699
940 Case 900 with Htg. Temp. Setback | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 4.985 | 2.888 | 3.871 | 3.39 | 270-220 Cooling South Windows | 5.796 | 5.475 |  | 5.894 |  |  | 5.585 | 5.654 |  | 5.475 | 5.894
950 Case 900 with Night Ventilation | 2.033 | 2.621 | 2.664 | 3.17 |  | 2.677 | 2.6861 | 2.867 | 3.495 | 2.033 | 3.17 | 2.674 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
960 Sunspace | 0.953 | 1.144 | 1.057 | 1.37 |  | 1.179 | 1.378 | 1.403 | 1.428 | 0.953 | 1.403 | 1.212 | 280-270 Cavity Albedo | -1.912 | -2.01 |  | -2.014 |  |  | -1.9778 | -1.631 |  | -2.014 | -1.631
[13 empty] | 320-270 Thermostat | -0.655 | -0.695 |  | -0.681 |  |  | -0.58611 | -0.726 |  | -0.726 | -0.58611
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX | AVERAGE | 290-270 South Shading | -0.087 | -0.086 |  | -0.258 |  |  | -0.56111 | -0.246 |  | -0.56111 | -0.086
195 Solid Conduction | 0.651 | [8 empty] | 0.651 | 0.651 | 0.651 | 300-270 E&W Windows | -2.952 | -2.548 |  | -2.577 |  |  | -2.4861 | -1.938 |  | -2.952 | -1.938
200 Surface Convection Int IR="off" Ext IR="off" | 0.863 | [8 empty] | 0.863 | 0.863 | 0.863 | 310-300 E&W Shading | -0.556 | -0.344 |  | -0.493 |  |  | -0.68889 |  |  | -0.68889 | -0.344
210 Infrared Radiation Int IR="off" Ext IR="on" | 0.476 | 1.017 |  |  |  |  | 1.0678 | 1.142 |  | 0.476 | 1.142 | 0.92569
215 Infrared Radiation Int IR="on" Ext IR="off" | 1.007 | [8 empty] | 1.007 | 1.007 | 1.007 | Low Mass REALISTIC DIAGNOSTIC TESTS
220 In-Depth Base Case | 0.56 | 1.166 | 0.937 | 1.34 |  | 1.215 | 1.1789 | 1.213 |  | 0.56 | 1.34 | 1.0871 | ANNUAL HEATING [MWH]
230 Infiltration | 1.059 | 1.646 | 1.455 | 1.875 |  | 1.7 | 1.7078 | 1.749 |  | 1.059 | 1.875 | 1.5988
240 Internal Gains | 0.739 | 1.347 | 1.119 | 1.54 |  | 1.398 | 1.3614 | 1.397 |  | 0.739 | 1.54 | 1.2716 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
250 Exterior Solar Absorptance | 3.36 | 3.036 | 2.605 | 2.59 |  | 2.258 | 3.2278 | 4.912 |  | 2.258 | 4.912 | 3.1413 | 400-395 Low Mass, Heating Surf. Conv. & IR | 1.916 | 2.276 | 2.935 | 2.767 | 2.772 | 2.32 | 2.311 | 2.487 |  | 1.916 | 2.935
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | MIN | MAX | AVERAGE | 410-400 Low Mass, Heating Infiltration | 1.696 | 1.798 | 1.736 | 1.76 | 1.761 | 1.732 | 1.77 | 1.759 |  | 0.011 | 0.105
270 South Windows | 6.356 | 6.641 |  | 7.234 |  |  | 6.7639 | 6.867 |  | 6.356 | 7.234 | 6.7724 | 420-410 Low Mass, Heating Int. Gains | -1.298 | -1.263 | -1.355 | -1.361 | -1.361 | -1.245 | -1.239 | -1.222 |  | -1.361 | -1.222
280 Cavity Albedo | 4.444 | 4.631 |  | 5.22 |  |  | 4.7861 | 5.236 |  | 4.444 | 5.236 | 4.8634 | 600-430 Low Mass, Heating S. Window | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 |  | -2.118 | -1.133
290 South Shading | 6.269 | 6.555 |  | 6.976 |  |  | 6.2028 | 6.621 |  | 6.2028 | 6.976 | 6.5248 | 430-420 Low Mass, Heating Ext. Solar Abs. | -1.869 | -1.122 | -1.324 | -1.187 | -1.187 | -1.112 | -1.197 | -1.353 |  | -1.869 | -1.112
300 East/West Windows | 3.404 | 4.093 |  | 4.657 |  |  | 4.2778 | 4.929 |  | 3.404 | 4.929 | 4.2722 | 440-600 Low Mass, Heating Cavity Albedo | 0.153 | 0.214 |  | 0.426 | 0.215 |  | 0.226 | 0.28 |  | 0.153 | 0.426
310 East/West Shading | 2.848 | 3.749 |  | 4.164 |  |  | 3.5889 |  |  | 2.848 | 4.164 | 3.5875 | ANNUAL COOLING [MWH]
320 Thermostat | 5.701 | 5.946 |  | 6.553 |  |  | 6.1778 | 6.141 |  | 5.701 | 6.553 | 6.1038 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Low Mass Solid Conduction | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.3625 | 0.345 |  | 0 | 0.394 | 0.25993 | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
400 Low Mass Opaque Windows | 0 | 0.581 | 0.265 | 0.666 |  | 0.612 | 0.61333 | 0.572 |  | 0 | 0.666 | 0.47276 | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0 | 0.029 | 0.002 | 0.045 | 0.044 | 0.032 | 0.03439 | 0.033 |  | 0 | 0.045
410 Low Mass Infiltration | 0.035 | 0.699 | 0.413 | 0.814 |  | 0.724 | 0.74306 | 0.71 |  | 0.035 | 0.814 | 0.59115 | 410-400 Low Mass, Cooling Infiltration | 0 | 0.019 | 0.008 | 0.023 | 0.026 | 0.021 | 0.02239 | 0.021 |  | 0 | 0.026
420 Low Mass Internal Gains | 0.258 | 0.923 | 0.631 | 1.047 |  | 0.938 | 0.93778 | 0.921 |  | 0.258 | 1.047 | 0.80797
430 Low Mass Ext. Shortwave Absorptance | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 1.7983 | 2.578 |  | 1.427 | 2.578 | 1.7722
440 Low Mass Cavity Albedo | 4.546 | 4.424 |  | 5.053 |  |  | 4.6861 | 5.278 |  | 4.424 | 5.278 | 4.7974 | 215-200 | 0.069 | [8 empty] | 0.069 | 0.069
800 High Mass Opaque Windows | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 0.98278 | 1.358 |  | 0.585 | 1.358 | 1.0023 | 420-410 Low Mass, Cooling Int. Gains | 0.011 | 0.088 | 0.041 | 0.105 | 0.104 | 0.091 | 0.09043 | 0.078 |  | 0.011 | 0.105
810 High Mass Cavity Albedo | 1.852 | 2.357 |  | 2.991 |  |  | 2.3436 | 2.862 |  | 1.852 | 2.991 | 2.4811 | 430-420 Low Mass, Cooling Ext Solar Abs. | 0.531 | 0.47 | 0.371 | 0.515 | 0.496 | 0.409 | 0.4599 | 0.732 |  | 0.371 | 0.732
FREE-FLOAT TEMPERATURE OUTPUT | [12 empty] | 600-430 Low Mass, Cooling S. Window | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 |  | 5.595 | 7.28
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [12 empty] | 440-600 Low Mass, Cooling Cavity Albedo | -2.17 | -2.261 |  | -2.604 | -2.76 |  | -2.517 | -2.094 |  | -2.76 | -2.094
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | PEAK HEATING [KW]
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C)
[10 empty] | MIN | MAX | AVERAGE |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
600FF - Low Mass Building with South Windows | 64.929 | 65.11 | 69.5 | 68.6 |  | 64.9 | 65.25 | 65.25 | 61.72 | 64.9 | 69.5 | 66.2199 | 400-395 Low Mass, Heating Surf. Conv. & IR | 0.805 | 1.071 | 1.148 | 1.31 |  | 1.079 | 1.115 | 1.25 |  | 0.805 | 1.31
900FF - High Mass Building with South Windows | 41.812 | 43.44 | 42.7 | 44.8 |  | 43 | 42.46 | 43.17 | 45.61 | 41.812 | 44.8 | 43.0546 | 410-400 Low Mass, Heating Infiltration | 0.758 | 0.844 | 0.757 | 0.792 |  | 0.885 | 0.77778 | 0.794 |  | 0.757 | 0.885
650FF Case 600FF with Night Ventilation | 63.236 | 63.45 | 68.2 | 67 |  | 63.3 | 63.74 | 63.82 | 63.22 | 63.236 | 68.2 | 64.678
950FF Case 900FF with Night Ventilation | 35.54 | 36.23 | 35.9 | 38.5 |  | 36.1 | 35.67 | 37.58 | 35.975 | 35.54 | 38.5 | 36.5029
960 Sunspace | 48.943 | 48.88 | 49 | 51 |  | 50.2 | 55.34 | 48.92 | 74.28 | 48.88 | 55.34 | 50.3261 | 215-200 | 0.136 | [8 empty] | 0.136 | 0.136
[13 empty] | 420-410 Low Mass, Heating Int. Gains | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.183 | -0.18333 | -0.188 |  | -0.2 | -0.18
[13 empty] | 430-420 Low Mass, Heating Ext Solar Abs. | -0.001 | 0 | 0 | 0 |  | 0 | 0 | 0.011 |  | -0.001 | 0.011
[13 empty] | 600-430 Low Mass, Heating S. Window | -0.005 | -0.004 | -0.005 | -0.029 |  | -0.007 | 0 | 0.217 |  | -0.029 | 0.217
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [12 empty] | 440-600 Low Mass, Heating Cavity Albedo | 0.002 | 0.002 |  | 0.019 |  |  | 0 | 0.022 |  | 0 | 0.022
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | PEAK COOLING [KW]
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) |  |  |  | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
[13 empty] | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0 | 0.219 | 0.265 | 0.272 |  | 0.256 | 0.25083 | 0.227 |  | 0 | 0.272
[10 empty] | MIN | MAX | AVERAGE | 410-400 Low Mass, Cooling Infiltration | 0.035 | 0.118 | 0.148 | 0.148 |  | 0.112 | 0.12972 | 0.138 |  | 0.035 | 0.148
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 420-410 Low Mass, Cooling Int. Gains | 0.223 | 0.224 | 0.218 | 0.233 |  | 0.214 | 0.19472 | 0.211 |  | 0.19472 | 0.233
600FF - Low Mass Building with South Windows | -15.565 | -17.05 | -18.8 | -18 |  | -17.8 | -17.81 | -18.47 | -15.227 | -18.8 | -15.565 | -17.6421 | 430-420 Low Mass, Cooling Ext. Solar Abs. | 1.235 | 0.849 | 0.796 | 0.715 |  | 0.637 | 0.86056 | 1.657 |  | 0.637 | 1.657
900FF - High Mass Building with South Windows | -1.647 | -3.15 | -4.3 | -4.5 |  | -4 | -6.38 | -5.64 | -3.295 | -6.38 | -1.647 | -4.231 | 600-430 Low Mass, Cooling S. Window | 4.701 | 4.193 | 5.229 | 5.065 |  | 4.711 | 4.6878 | 4.234 |  | 4.193 | 5.229
650FF Case 600FF with Night Ventilation | -22.564 | -22.96 | -21.6 | -23 |  | -22.9 | -22.83 | -22.91 | -23.06 | -23 | -21.6 | -22.6806 | 440-600 Low Mass, Cooling Cavity Albedo | -1.648 | -1.541 |  | -1.774 |  |  | -1.8 | -1.534 |  | -1.8 | -1.534
950FF Case 900FF with Night Ventilation | -19.484 | -20.04 | -18.6 | -19.7 |  | -20.2 | -19.34 | -19.96 | -19.97 | -20.2 | -18.6 | -19.6177
960 Sunspace | 2.729 | 1.63 | 3.9 | 3.1 |  | 1.4 | -2.82 | -0.39 | -2.799 | -2.82 | 3.9 | 1.3641 | High Mass DIAGNOSTIC TESTS
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [12 empty] | ANNUAL HEATING [MWH]
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
CASE# | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) | TMP (C) |  |  |  | 800-430 Mass, Heating w/ Op. Win. | -0.561 | -0.535 | -0.599 | -0.567 | -0.586 | -0.501 | -0.56 | -0.649 |  | -0.649 | -0.501
600FF - Low Mass Building with South Windows | 25.126 | 25.43 | 24.6 | 25.48 | 25.93 | 25.2 | 24.49 | 24.22 | 28.05 | 24.22 | 25.93 | 25.0595 | 900-800 High Mass, Heating S. Window | -3.698 | -4.343 | -5.356 | -4.714 | -4.612 | -4.431 | -4.285 | -3.82 |  | -5.356 | -3.698
900FF - High Mass Building with South Windows | 25.453 | 25.93 | 24.7 | 25.49 | 25.72 | 25.2 | 24.47 | 24.45 | 27.08 | 24.45 | 25.93 | 25.1766 | 900-810 High Mass, Heating Int. Sol. Abs. | -0.669 | -0.836 |  | -1.107 | -0.84 |  | -0.912 | -0.921 |  | -1.107 | -0.669
650FF Case 600FF with Night Ventilation | 18.234 | 18.69 | 19.1 | 18.96 | 19.62 | 18.4 | 17.99 | 18.36 | 19.23 | 17.99 | 19.62 | 18.6693 | 910-610 Mass, Heating w/ S. Shade | -2.78 | -2.944 | -3.532 | -3.106 | -3.338 | -2.908 | -2.873 | -3.163 | -2.506 | -3.532 | -2.78
950FF Case 900FF with Night Ventilation | 14.14 | 14.26 | 14.3 | 14.97 | 14.29 | 14 | 14.53 | 14.64 | 14.18 | 14 | 14.97 | 14.3913
960 Sunspace | 27.49 | 27.72 | 28 | 28.69 | 28.54 | 28 | 28.96 | 26.43 | 30.62 | 26.43 | 28.96 | 27.9788 | 920-620 Mass, Heating w/ E&W Window | -1.3 | -1.297 | -1.689 | -1.461 | -1.676 | -1.329 | -1.297 | -1.428 | -1.027 | -1.689 | -1.297
[13 empty] | 930-630 Mass, Heating w/ E&W Shade | -0.907 | -1.012 | -1.134 | -1.128 | -1.273 | -0.927 | -0.884 |  | -0.596 | -1.273 | -0.884
SOLAR RADIATION | [12 empty] | 940-640 Mass, Heating w/ Heating Setback | -1.958 | -1.867 | -2.304 | -2.024 | -2.392 | -1.886 | -1.963 | -1.986 | -2.01 | -2.392 | -1.867
ANNUAL INCIDENT TOTAL | [12 empty] | ANNUAL COOLING [MWH]
CASE 600 | [13 empty] | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
[13 empty] | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 800-430 Mass, Cooling w/ Op. Win. | -0.429 | -0.393 | -0.367 | -0.432 | -0.462 | -0.368 | -0.4101 | -0.55 |  | -0.55 | -0.367
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | 900-800 High Mass, Cooling S. Window | 2.019 | 2.376 | 2.4 | 2.893 | 3.193 | 2.377 | 2.2777 | 2.274 |  | 2.019 | 3.193
SURFACE | [12 empty] | 900-810 High Mass, Cooling Int. Sol. Abs. | 1.08 | 1.195 |  | 1.454 | 1.707 |  | 1.294 | 0.975 |  | 0.975 | 1.707
= | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 910-610 Mass, Cooling w/ S. Shade | -3.094 | -3.318 | -3.876 | -3.576 | -3.924 | -3.336 | -3.275 | -3.739 | -3.442 | -3.924 | -3.094
600 NORTH | 427 |  | 434 | 456 | 407.3 | 457 | 367.4 | 453 | 431.46 | 367.4 | 457 | 428.8143 | 920-620 Mass, Cooling w/ E&W Window | -1.577 | -1.476 | -1.894 | -1.69 | -1.912 | -1.554 | -1.483 | -1.738 | -1.687 | -1.912 | -1.476
600 EAST | 959 |  | 1155 | 1083 | 1217.3 | 1082 | 1101 | 962 | 1177.84 | 959 | 1217.3 | 1079.9 | 930-630 Mass, Cooling w/ E&W Shade | -1.09 | -1.174 | -1.223 | -1.32 | -1.463 | -1.05 | -1 |  | -1.191 | -1.463 | -1
600 WEST | 1086 |  | 1079 | 1003 | 856.5 | 1002 | 1012 | 1090 | 1039.59 | 856.5 | 1090 | 1018.3571 | 940-640 Mass, Cooling w/ Heating Setback | -3.873 | -3.647 | -4.419 | -3.99 | -4.57 | -3.758 | -3.863 | -3.992 | -4.083 | -4.57 | -3.647
600 SOUTH | 1456 |  | 1566 | 1476 | 1467.7 | 1474 | 1522 | 1468 | 1545.41 | 1456 | 1566 | 1489.9571 | 950-650 Mass, Cooling w/ Night Vent | -4.429 | -4.614 | -5.257 | -4.973 | -5.956 | -4.537 | -4.5584 | -4.685 | -4.807 | -5.956 | -4.429
600 HORZ. | 1797 |  | 1831 | 1832 | 1831.8 | 1832 | 1832 | 1832 | 1839.29 |  |  |  | PEAK HEATING [KW] | [9 empty] | 0 | 0
= | [13 empty] | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
[13 empty] | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
SOLAR RADIATION | [12 empty] | 800-430 Mass, Heating w/ Op. Win. | -0.215 | -0.151 | -0.141 | -0.149 |  | -0.142 | -0.14444 | -0.198 |  | -0.215 | -0.141
UNSHADED ANNUAL TRANSMITTED | [12 empty] | 900-800 High Mass, Heating S. Window | -0.377 | -0.34 | -0.352 | -0.378 |  | -0.294 | -0.26944 | -0.142 |  | -0.378 | -0.142
[13 empty] | 900-810 High Mass, Heating Int. Sol. Abs. | -0.129 | -0.113 |  | -0.155 |  |  | -0.088889 | -0.166 |  | -0.166 | -0.088889
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 910-610 Mass, Heating w/ S. Shade | -0.579 | -0.485 | -0.47 | -0.494 |  | -0.419 | -0.38611 | -0.553 | -0.118 | -0.579 | -0.38611
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | 920-620 Mass, Heating w/ E&W Window | -0.283 | -0.238 | -0.241 | -0.264 |  | -0.248 | -0.21389 | -0.318 | 0.069 | -0.318 | -0.21389
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | MIN | MAX |  | 930-630 Mass, Heating w/ E&W Shade | -0.237 | -0.209 | -0.193 | -0.238 |  | -0.214 | -0.17778 |  | 0.079 | -0.238 | -0.17778
= | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 940-640 Mass, Heating w/ Heating Setback | -1.252 | -0.458 | -0.278 | -0.414 |  | -0.23 | -0.6 | -0.526 | -1.936 | -1.252 | -0.23
620 WEST | 732 |  | 735 | 689 | 562.96 | 642 | 661.67 | 706 | 655 | 562.96 | 735 | 675.5186 | PEAK COOLING [KW]
600 SOUTH | 946 |  | 1051 | 962 | 954.3 | 926 | 984.17 | 914 | 952.78 | 914 | 1051 | 962.4957 |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
[13 empty] | CASES | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
[13 empty] | 800-430 Mass, Cooling w/ Op. Win. | -0.908 | -0.805 | -0.684 | -0.41 |  | -0.547 | -0.81556 | -1.22 |  | -1.22 | -0.41
SOLAR RADIATION | [12 empty] | 900-800 High Mass, Cooling S. Window | 2.303 | 2.188 | 2.715 | 2.519 |  | 2.306 | 2.5839 | 2.099 |  | 2.099 | 2.715
SHADED ANNUAL TRANSMITTED | [12 empty] | 900-810 High Mass, Cooling Int. Sol. Abs. | 1.036 | 0.798 |  | 0.88 |  |  | 1.2231 | 0.595 |  | 0.595 | 1.2231
[13 empty] | 910-610 Mass, Cooling w/ S. Shade | -3.773 | -3.324 | -3.728 | -3.094 |  | -3.384 | -2.8833 | -2.999 | -2.834 | -3.773 | -2.8833
CODENAME: | [12 empty] | 920-620 Mass, Cooling w/ E&W Window | -1.249 | -1.142 | -1.321 | -1.106 |  | -1.226 | -1.225 | -1.591 | -0.888 | -1.591 | -1.106
COUNTRY: | [12 empty] | 930-630 Mass, Cooling w/ E&W Shade | -1.199 | -1.158 | -1.2 | -1.036 |  | -1.179 | -1.11 |  | -0.63 | -1.2 | -1.036
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | MIN | MAX |  | 940-640 Mass, Cooling w/ Heating Setback | [9 empty] | 0 | 0
= | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 950-650 Mass, Cooling w/ Night Vent | -3.998 | -3.21 | -3.852 | -3.501 |  | -3.466 | -3.6917 | -3.812 | -3.674 | -3.998 | -3.21
630 WEST | 599 |  | 481 | 554 | 441.3 | 431 | 437.5 |  | 474.16 | 431 | 599 | 490.6333
610 SOUTH | 785 |  | 831 | 803 | 774.86 | 757 | 782 | 809 | 766.1 | 757 | 831 | 791.6943
SOLAR RADIATION
ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
CODENAME:
COUNTRY:
CASE# | [9 empty] | MIN | MAX |  | NOT USED TO GENERATE CHARTS |  |  |  |  | NOT USED TO GENERATE CHARTS |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS |  |  |  | NOT USED TO GENERATE CHARTS
= | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier | [15 empty] | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
620 WEST | 0.67403 |  | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.65382 | 0.64771 | 0.63006 | 0.64072 | 0.68694 | 0.6631 | ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [11 empty] | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | RANGE | RANGE
600 SOUTH | 0.64973 |  | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.64663 | 0.62262 | 0.61652 | 0.62262 | 0.67114 | 0.64576 | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | MIN | MAX
[13 empty] | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | JAN 04 | 2 | 4.307 | 1904-01-01 | 2 | 4.037 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.354 | JAN 04 | 2 |  |  |  | 3.437 | 4.354
SOLAR RADIATION | [12 empty] | CASE# | KW | DATE | HR | HR | KW | DATE | HR | KW | DATE | HR | KW | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.037 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.354 | JAN 04 | 2 |  |  |  | 3.437 | 4.354
ANNUAL OVERHANG AND FIN SHADING COEFFICIENT | [12 empty] | 600 | 3.437 | 1993-01-04 | 5 | 5 | 3.94 | JAN 04 | 5 | 4.045 | JAN 04 | 5 | 4.258 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.277 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 |  |  |  | 3.591 | 4.379
[13 empty] | 610 | 3.437 | 1993-01-04 | 5 | 5 | 3.941 | JAN 04 | 5 | 4.034 | JAN 04 | 5 | 4.258 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.278 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 |  |  |  | 3.592 | 4.278
CODENAME: | [12 empty] | 620 | 3.591 | 1993-01-04 | 6 | 6 | 3.941 | JAN 04 | 5 | 4.046 | JAN 04 | 5 | 4.277 | JAN 04 | 8 | 8.078 | 1904-01-01 | 8 | 6.347 | JAN 04 | 8 | 5.7222 | Jan-04 | 8 | 6.954 | JAN 04 | 8 |  |  |  | 5.232 | 6.954
COUNTRY: | [12 empty] | 630 | 3.592 | 1993-01-04 | 7 | 7 | 3.941 | JAN 04 | 5 | 4.025 | JAN 04 | 5 | 4.28 | USA KW: 0; UK-BRE KW: 0; SPAIN KW: 0; BEL/UK KW: 0
CASE# | [9 empty] | MIN | MAX |  | 640 | 5.232 | 1993-01-04 | 7 | 7 | 5.486 | JAN 04 | 8 | 5.943 | JAN 04 | 8 | 6.53 | JAN 04 | 7 | 4.081 | 1904-01-01 | 7 | 3.608 | JAN 04 | 8 | 3.5167 | Jan-04 | 7 | 3.797 | JAN 04 | 7 |  |  |  | 2.85 | 3.797
test | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 650 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 | JAN 04 | 7 | 4.083 | 1904-01-01 | 7 | 3.618 | JAN 04 | 8 | 3.5361 | Jan-04 | 7 | 3.801 | JAN 04 | 7 |  |  |  | 2.858 | 3.801
630/620 WEST | 0.18169 |  | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 0.33879 |  | 0.27609 |  |  |  | 900 | 2.85 | 1993-01-04 | 7 | 7 | 3.453 | JAN 04 | 7 | 3.557 | JAN 04 | 7 | 3.76 | JAN 04 | 7 | 4.156 | 1904-01-01 | 7 | 4.029 | JAN 04 | 7 | 3.7083 | Jan-04 | 7 | 4.061 | JAN 04 | 7 |  |  |  | 3.308 | 4.061
610/600 SOUTH | 0.17019 |  | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.20542 | 0.11488 | 0.19593 |  |  |  | 910 | 2.858 | 1993-01-04 | 7 | 7 | 3.456 | JAN 04 | 7 | 3.564 | JAN 04 | 7 | 3.764 | JAN 04 | 7 | 4.165 | 1904-01-01 | 7 | 4.064 | JAN 04 | 7 | 3.7444 | Jan-04 | 7 | 4.188 | JAN 04 | 8 |  |  |  | 3.355 | 4.064
[13 empty] | 920 | 3.308 | 1993-01-04 | 7 | 7 | 3.703 | JAN 04 | 7 | 3.805 | JAN 04 | 7 | 4.013 | JAN 04 | 8 | 9.923 | 1904-01-01 | 8 | 6.117 | JAN 04 | 8 | 5.1222 | Jan-03 | 9 | 6.428 | JAN 04 | 8 |  |  |  | 3.98 | 6.428
[13 empty] | 930 | 3.355 | 1993-01-04 | 7 | 7 | 3.732 | JAN 04 | 7 | 3.832 | JAN 04 | 7 | 4.042 | USA KW: 0; UK-BRE KW: 0; SPAIN KW: 0; BEL/UK KW: 0
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5 | [12 empty] | 940 | 3.98 | 1993-01-04 | 7 | 7 | 5.028 | JAN 04 | 8 | 5.665 | JAN 04 | 8 | 6.116 | JAN 04 | 8 | 2.896 | 1904-01-01 | 8 | 2.852 | JAN 04 | 8 | 2.522 | Jan-04 | 8 | 2.779 | JAN 04 | 8 |  |  |  | 2.41 | 2.896
CASE 600 OR 900 | [12 empty] | 950 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 | USA DATE: JAN 04; USA HR: 7; USA KW: 3.738; UK-BRE DATE: Feb-06; UK-BRE HR: 2; UK-BRE KW: 3.799; SPAIN DATE: JAN 04; SPAIN HR: 8; BEL/UK KW: 4.296; FINLAND DATE: JAN 04; FINLAND HR: 7
SOUTH SURFACE | [12 empty] | 960 | 2.41 | 1993-01-04 | 7 | 7 | 2.751 | JAN 04 | 8 | 2.727 | JAN 04 | 8 | 2.863 | JAN 04 | 3 | 2.235 | 1904-01-01 | 3 | 2.221 | JAN 04 | 4 | 2.1856 | Jan-04 | 3 | 2.263 | JAN 04 | 3
(USE COLUMN B ONLY) | [12 empty] | 990 | 2.769 | 1993-02-06 | 2 | 2 | 3.734 | JAN 04 | 7 | 3.427 | JAN 04 | 7 | 3.681 |  |  | 3.047 | 1904-01-01 | 3 | 2.999 | JAN 04 | 2 | 2.9694 | Jan-04 | 5 | 3.382 | JAN 04 | 2
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 195 | 2.004 | 1993-01-04 | 2 | 2 | 2.186 | JAN 04 | 8 | 2.32 | JAN 04 | 3 | 2.385 |  |  | 3.077 | 1904-01-01 | 3 | 3.02 | JAN 04 | 2 | 2.9806 | Jan-04 | 5 | 3.325 | JAN 04 | 2
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | 200 | 2.651 | 1993-01-04 | 5 | 5 | 2.973 | JAN 04 | 5 | [6 empty] | 3.65 | 1904-01-01 | 2 | 3.307 | JAN 04 | 6 | 3.2944 | Jan-04 | 6 | 3.458 | JAN 04 | 8
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210 | 2.701 | 1993-01-04 | 5 | 5 | 2.973 | JAN 04 | 5 |  |  |  |  | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.348 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2
= | = | = | = | = | = | = | = | = | = |  |  |  | 215 | 2.787 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 |  |  |  |  | JAN 04 | 2 | 5.293 | 1904-01-01 | 2 | 5.159 | JAN 04 | 2 | 4.8917 | Jan-04 | 6 | 5.107 | JAN 04 | 2
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 220 | 2.867 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 3.509 | 1904-01-01 | 2 | 3.159 | JAN 04 | 8 | 3.1528 | Jan-04 | 6 | 3.333 | JAN 04 | 8
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 230 | 4.386 | 1993-01-04 | 5 | 5 | 4.984 | JAN 04 | 2 | 4.994 | JAN 04 | 2 | 5.279 | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.525 | JAN 04 | 2
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 240 | 2.685 | 1993-01-04 | 5 | 5 | 3.1 | JAN 04 | 5 | 3.282 | JAN 04 | 5 | 3.495 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.738 | JAN 04 | 2
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 250 | 2.866 | 1993-01-04 | 5 | 5 | 3.279 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.759 | JAN 04 | 2
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 270 | 2.863 | 1993-01-04 | 5 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.67 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3278 | Jan-04 | 6 | 3.738 | JAN 04 | 2
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 280 | 2.864 | 1993-01-04 | 5 | 5 | 3.278 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.599 | JAN 04 | 5 | 3.3278 | Jan-04 | 6 | 3.77 | JAN 04 | 2
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 290 | 2.863 | 1993-01-04 | 5 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.67 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.599 | JAN 04 | 5 | 3.3278 | Jan-04 | 6 | 3.771 | JAN 04 | 2
7 | 1.6 |  | 1.5 | 3.0447 | 3.02 | 3 | 3.05 | 3 | 3.8168 |  |  |  | 300 | 3.014 | 1993-01-04 | 6 | 6 | 3.276 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | 3.714 | 1904-01-01 | 2 | 3.34 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.735 | JAN 04 | 3
8 | 13.8 |  | 12.59 | 20.6464 | 20.59 | 21 | 20.69 | 20.68 | 19.2215 |  |  |  | 310 | 3.015 | 1993-01-04 | 6 | 6 | 3.277 | JAN 04 | 5 |  |  |  | 3.672 | JAN 04 | 3 | 2.391 | 1904-01-01 | 3 | 2.263 | JAN 04 | 4 | 2.2211 | Jan-04 | 8 | 2.27 | JAN 04 | 3
9 | 31.6 |  | 30.01 | 38.8836 | 38.83 | 39 | 38.94 | 38.94 | 34.7925 |  |  |  | 320 | 2.861 | 1993-01-04 | 5 | 5 | 3.275 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | 3.709 | 1904-01-01 | 2 | 3.342 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2
10 | 48.3 |  | 46.23 | 54.5664 | 54.53 | 55 | 54.67 | 54.56 | 48.4197 |  |  |  | 395 | 2.062 | 1993-01-04 | 7 | 7 | 2.209 | JAN 04 | 8 | 2.328 | JAN 04 | 3 | 2.385 | JAN 04 | 2 | 4.501 | 1904-01-01 | 2 | 4.227 | JAN 04 | 2 | 4.1139 | Jan-04 | 6 | 4.314 | JAN 04 | 2
11 | 61.6 |  | 59.31 | 65.9733 | 54.77 | 66 | 66.08 | 65.99 | 58.0502 |  |  |  | 400 | 2.867 | 1993-01-04 | 5 | 5 | 3.28 | JAN 04 | 5 | 3.476 | JAN 04 | 5 | 3.695 | JAN 04 | 2 | 4.301 | 1904-01-01 | 2 | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.126 | JAN 04 | 2
12 | 69.3 |  | 65.05 | 71.7839 | 59.65 | 72 | 71.92 | 71.74 | 63.4937 |  |  |  | 410 | 3.625 | 1993-01-04 | 5 | 5 | 4.124 | JAN 04 | 5 | 4.233 | JAN 04 | 5 | 4.487 | JAN 04 | 2 | 4.301 | 1904-01-01 | 2 | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.137 | JAN 04 | 2
13 | 71.7 |  | 66.98 | 72.2839 | 60.1 | 72 | 72.42 | 72.3 | 63.4812 |  |  |  | 420 | 3.443 | 1993-01-04 | 5 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 | 4.306 | 1904-01-01 | 2 | 4.041 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.376 | JAN 04 | 2
14 | 68.1 |  | 63.11 | 66.4075 | 55.24 | 66 | 66.53 | 66.38 | 57.4075
15 | 58.9 |  | 51.79 | 54.8997 | 45.68 | 55 | 55 | 54.8 | 46.5834 |  |  |  | 430 | 3.442 | 1993-01-04 | 5 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 | 4.188 | 1904-01-01 | 8 | 3.902 | JAN 04 | 8 | 3.7861 | Jan-04 | 7 | 3.939 | JAN 04 | 7
16 | 44.4 |  | 37.13 | 38.8836 | 32.37 | 39 | 38.94 | 38.84 | 32.2993 |  |  |  | 440 | 3.439 | 1993-01-04 | 5 | 5 | 3.942 | JAN 04 | 5 |  |  |  | 4.277 | JAN 04 | 7 | 4.115 | 1904-01-01 | 7 | 3.709 | JAN 04 | 8 | 3.6056 | Jan-04 | 7 | 3.963 | JAN 04 | 7
17 | 26.9 |  | 19.14 | 20.4797 | 17.06 | 20 | 20.52 | 20.46 | 16.2611 |  |  |  | 800 | 3.227 | 1993-01-04 | 5 | 5 | 3.793 | JAN 04 | 7 | 3.909 | JAN 04 | 7 | 4.138
18 | 8.7 |  | 4.62 | 3.0447 | 2.54 | 3 | 3.05 | 0 | 3.1327 |  |  |  | 810 | 2.979 | 1993-01-04 | 7 | 7 | 3.566 | JAN 04 | 7 |  |  |  | 3.915 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA; RANGE MIN: RANGE; RANGE MAX: RANGE
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | KW | DATE | HR | KW | DATE | HR | MIN | MAX
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | OCT 16 | 14 | 7.551 | 1916-10-01 | 13 | 6.286 | NOV 25 | -6.194 | 6.4861 | Oct-16 | 14 | 6.812 | OCT 17 | 14 |  |  |  | 5.965 | 6.812
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CASE# | KW | DATE | HR | HR | KW | DATE | HR | KW | DATE | HR | KW | NOV 25 | 14 | 7.215 | 1925-11-01 | 13 | 6.17 | NOV 25 | -5.669 | 5.675 | 1992-11-25 | 14 | 6.146 | OCT 17 | 14 |  |  |  | 5.669 | 6.146
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 600 | 6.194 | 1993-10-17 | 13 | 13 | 5.965 | OCT 16 | 14 | 6.656 | OCT 16 | 13 | 6.827 | JUL 26 | 17 | 4.959 | 1902-07-01 | 10 | 4.297 | JUL 26 | -3.634 | 4.275 | 1992-07-26 | 17 | 5.096 | JUL 26 | 16 |  |  |  | 3.634 | 5.096
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 610 | 5.669 | 1993-11-25 | 13 | 13 | 5.824 | NOV 25 | 14 | 6.064 | JAN 13 | 14 | 6.371 | JUL 26 | 17 | 4.4 | 1902-07-01 | 9 | 3.665 | JUL 26 | -3.072 | 3.6083 | 1992-07-26 | 17 | 3.546 | JUN 30 | 17 |  |  |  | 3.072 | 3.704
= | = | = | = | = | = | = | = | = |  |  |  |  | 620 | 3.634 | 1993-07-26 | 16 | 16 | 4.075 | JUL 26 | 17 | 4.43 | JUL 26 | 17 | 4.593 | OCT 16 | 14 | 7.537 | 1916-10-01 | 13 | 6.25 | NOV 25 | -6.161 | 6.4417 | Oct-16 | 14 | 6.771 | OCT 17 | 14
[13 empty] | 630 | 3.072 | 1993-07-26 | 16 | 16 | 3.704 | JUL 26 | 17 | 3.588 | JUL 26 | 17 | 4.116 | OCT 16 | 14 | 7.458 | 1916-10-01 | 13 | 6.143 | NOV 25 | -6.031 | 6.3778 | Oct-17 | 14 | 6.679 | OCT 17 | 14 |  |  |  | 5.831 | 6.679
[13 empty] | 640 | 6.161 | 1993-10-17 | 13 | 13 | 5.892 | OCT 16 | 14 | 6.576 | OCT 16 | 14 | 6.776 | OCT 17 | 14 | 4.901 | 1917-10-01 | 14 | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 |  |  |  | 2.888 | 3.5667
[13 empty] | 650 | 6.031 | 1993-10-17 | 13 | 13 | 5.831 | OCT 16 | 14 | 6.516 | OCT 16 | 14 | 6.671 | OCT 17 | 15 | 3.973 | 1917-10-01 | 15 | 2.786 | OCT 17 | -1.896 | 2.7917 | Oct-17 | 15 | 3.147 | OCT 17 | 15 |  |  |  | 1.896 | 3.147
[13 empty] | 900 | 2.888 | 1993-10-17 | 14 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | JUL 26 | 17 | 3.777 | 1926-07-01 | 17 | 3.071 | JUL 26 | -2.385 | 3.05 | 1992-07-26 | 17 | 3.505 | JUL 26 | 17 |  |  |  | 2.385 | 3.505
[13 empty] | 910 | 1.896 | 1993-10-17 | 15 | 15 | 2.5 | OCT 21 | 15 | 2.336 | OCT 17 | 15 | 3.277 | JUL 26 | 17 | 3.203 | 1926-07-01 | 17 | 2.486 | JUL 26 | -1.873 | 2.4983 | 1992-07-26 | 17 | 2.304 | JUN 30 | 17 |  |  |  | 1.873 | 2.546
[13 empty] | 920 | 2.385 | 1993-07-26 | 16 | 16 | 2.933 | JUL 26 | 17 | 3.109 | JUL 26 | 17 | 3.487 | OCT 17 | 14 | 4.901 | 1917-10-01 | 14 | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15
[13 empty] | 930 | 1.873 | 1993-07-26 | 17 | 17 | 2.546 | JUL 26 | 17 | 2.388 | JUL 26 | 18 | 3.08 | SEP 02 | 14 | 3.848 | 1902-09-01 | 15 | 2.677 | SEP 02 | -2.033 | 2.6861 | Sep-02 | 15 | 2.867 | SEP 02 | 14 |  |  |  | 2.033 | 2.867
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5 | [12 empty] | 940 | 2.888 | 1993-10-17 | 14 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | JUL 26 | 16 | 1.306 | 1926-07-01 | 16 | 1.179 | JUL 26 | 16 | 1.378 | 1992-07-26 | 16 | 1.403 | JUL 26 | 16 |  |  |  | 0.953 | 1.403
CASE 600 OR 900 | [12 empty] | 950 | 2.033 | 1993-09-02 | 14 | 14 | 2.621 | SEP 02 | 15 | 2.664 | SEP 2 | 15 | 3.17 | USA DATE: SEP 02; USA HR: 14; USA KW: 3.525; UK-BRE DATE: 1917-10-01; UK-BRE HR: 14; UK-BRE KW: 1.859; SPAIN DATE: NOV 25; SPAIN HR: 14; BEL/UK KW: 2.779; FINLAND DATE: SEP 02; FINLAND HR: 14
WEST SURFACE | [12 empty] | 960 | 0.953 | 1993-08-16 | 16 | 16 | 1.144 | JUL 26 | 16 | 1.057 | JUL 26 | 16 | 1.37 | JUL 26 | 16 | 0.806 | 1926-07-01 | 16 | 0.799 | JUL 26 | -0.651 | 0.79139 | 1992-07-26 | 16 | 0.79 | JUL 26 | 16
(USE COLUMN B ONLY) | [12 empty] | 990 | 2.422 | 1993-10-17 | 14 | 14 | 2.912 | SEP 02 | 14 | 3.436 | OCT 17 | 13 | 2.819 |  |  | 1.111 | 1926-07-01 | 15 | 1.105 | JUL 26 | -0.863 | 1.1006 | 1992-07-26 | 16 | 1.126 | JUL 26 | 15
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 195 | 0.651 | 1993-07-26 | 15 | 15 | 0.728 | JUL 26 | 16 | 0.616 | JUL 27 | 15 | 0.853 |  |  | 1.101 | 1926-07-01 | 15 | 1.097 | JUL 26 | -0.476 | 1.0678 | 1992-07-26 | 16 | 1.142 | JUL 26 | 15
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | 200 | 0.863 | 1993-08-16 | 14 | 14 | 1.017 | JUL 26 | 15 | [6 empty] | 1.347 | 1926-07-01 | 15 | 1.216 | JUL 26 | -1.007 | 1.1836 | 1992-07-26 | 16 | 1.192 | JUL 26 | 15
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210 | 0.476 | 1993-08-16 | 16 | 16 | 1.017 | JUL 26 | 15 |  |  |  |  | JUL 26 | 15 | 1.342 | 1926-07-01 | 15 | 1.215 | JUL 26 | -0.56 | 1.1789 | 1992-07-26 | 16 | 1.213 | JUL 26 | 15
= | = | = | = | = | = | = | = | = | = |  |  |  | 215 | 1.007 | 1993-08-11 | 14 | 14 | 1.166 | JUL 26 | 15 |  |  |  |  | JUL 26 | 15 | 1.878 | 1926-07-01 | 15 | 1.7 | JUL 26 | -1.059 | 1.7078 | 1992-07-26 | 16 | 1.749 | JUL 26 | 15
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 220 | 0.56 | 1993-07-27 | 15 | 15 | 1.166 | JUL 26 | 15 | 0.937 | JUL 27 | 14 | 1.34 | JUL 26 | 15 | 1.542 | 1926-07-01 | 15 | 1.398 | JUL 26 | -0.739 | 1.3614 | 1992-07-26 | 16 | 1.397 | JUL 26 | 15
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 230 | 1.059 | 1993-07-27 | 15 | 15 | 1.646 | JUL 26 | 15 | 1.455 | JUL 27 | 14 | 1.875 | AUG 26 | 14 | 2.582 | 1911-08-01 | 12 | 2.258 | AUG 26 | -3.36 | 3.2278 | Sep-05 | 13 | 4.912 | SEP 05 | 12
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 240 | 0.739 | 1993-07-27 | 15 | 15 | 1.347 | JUL 26 | 15 | 1.119 | JUL 27 | 14 | 1.54 | OCT 16 | 14 | 7.967 | 1925-11-01 | 13 | 6.819 | NOV 25 | -6.356 | 6.7639 | Oct-17 | 14 | 6.867 | OCT 16 | 14
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 250 | 3.36 | 1993-09-05 | 12 | 12 | 3.036 | SEP 05 | 12 | 2.605 | SEP 5 | 11 | 2.59 | OCT 16 | 14 | 5.759 | 1916-10-01 | 13 | 4.63 | NOV 25 | -4.444 | 4.7861 | Oct-16 | 14 | 5.236 | OCT 16 | 14
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 270 | 6.356 | 1993-11-25 | 13 | 13 | 6.641 | NOV 25 | 14 |  |  |  | 7.163 | NOV 25 | 14 | 7.793 | 1923-12-01 | 13 | 6.7 | NOV 25 | -6.269 | 6.2028 | 1992-11-25 | 14 | 6.621 | NOV 25 | 14
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 280 | 4.444 | 1993-10-17 | 13 | 13 | 4.631 | NOV 25 | 13 |  |  |  | 5.22 | JUL 26 | 17 | 5.072 | 1902-07-01 | 10 | 4.336 | JUL 26 | -3.404 | 4.2778 | 1992-07-26 | 17 | 4.929 | JUL 26 | 17
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 290 | 6.269 | 1993-01-13 | 13 | 13 | 6.555 | NOV 25 | 14 |  |  |  | 6.91 | JUL 26 | 17 | 4.666 | 1902-07-01 | 9 | 3.669 | JUL 26 | -2.848 | 3.5889 | 1992-07-26 | 17 | 3.425 | JUN 30 | 17
7 | 1.6 |  | 1.8 | 2.9967 | 3 | 3 | 2.99 | 3 | 3.7882 |  |  |  | 300 | 3.404 | 1993-07-26 | 16 | 16 | 4.093 | JUL 26 | 17 |  |  |  | 4.642 | OCT 16 | 14 | 7.332 | 1925-11-01 | 13 | 6.183 | NOV 25 | -5.701 | 6.1778 | Oct-17 | 14 | 6.141 | OCT 16 | 14
8 | 13.5 |  | 13.92 | 20.1831 | 20.24 | 20 | 20.17 | 20.15 | 18.9029 |  |  |  | 310 | 2.848 | 1993-07-26 | 16 | 16 | 3.749 | JUN 30 | 17 |  |  |  | 4.186 | JUL 26 | 17 | 0.421 | 1926-07-01 | 16 | 0.356 | JUL 26 | 18 | 0.3625 | 1992-07-26 | 18 | 0.345 | JUL 26 | 18
9 | 31 |  | 31.75 | 37.955 | 38.01 | 38 | 37.92 | 37.9 | 33.9683 |  |  |  | 320 | 5.701 | 1993-11-25 | 13 | 13 | 5.946 | NOV 25 | 14 |  |  |  | 6.484 | JUL 26 | 16 | 0.712 | 1926-07-01 | 15 | 0.612 | JUL 26 | 17 | 0.61333 | 1992-07-26 | 17 | 0.572 | JUL 26 | 17
10 | 47.1 |  | 45.24 | 53.2444 | 53.27 | 53 | 53.17 | 53.15 | 47.3243 |  |  |  | 395 | 0 |  |  |  | 0.362 | JUL 26 | 18 | 0 |  |  | 0.394 | JUL 26 | 15 | 0.863 | 1926-07-01 | 15 | 0.724 | JUL 26 | -0.035 | 0.74306 | 1992-07-26 | 17 | 0.71 | JUL 26 | 17
11 | 59.7 |  | 56.63 | 64.4672 | 53.37 | 64 | 64.39 | 64.4 | 56.6638 |  |  |  | 400 | 0 |  |  |  | 0.581 | JUL 26 | 17 | 0.265 | JUL 27 | 17 | 0.666 | JUL 26 | 15 | 1.078 | 1926-07-01 | 15 | 0.938 | JUL 26 | -0.258 | 0.93778 | 1992-07-26 | 16 | 0.921 | JUL 26 | 15
12 | 67.4 |  | 61.58 | 69.9819 | 57.91 | 70 | 69.89 | 69.95 | 61.2148 |  |  |  | 410 | 0.035 | 1993-07-27 | 16 | 16 | 0.699 | JUL 26 | 17 | 0.413 | JUL 27 | 17 | 0.814 | JUL 26 | 15 | 1.779 | 1911-08-01 | 13 | 1.575 | JUL 26 | -1.493 | 1.7983 | 1992-09-05 | 13 | 2.578 | SEP 05 | 12
13 | 70.1 |  | 63.7 | 70.8061 | 58.3 | 71 | 70.75 | 71.16 | 61.5117 |  |  |  | 420 | 0.258 | 1993-07-27 | 15 | 15 | 0.923 | JUL 26 | 15 | 0.631 | JUL 27 | 15 | 1.047 | OCT 16 | 14 | 5.615 | 1916-10-01 | 13 | 4.465 | OCT 16 | -4.546 | 4.6861 | Oct-16 | 14 | 5.278 | OCT 17 | 14
14 | 67.3 |  | 61.46 | 65.6633 | 54.15 | 66 | 65.69 | 66.02 | 56.5965
15 | 58.9 |  | 51.67 | 54.9214 | 45.38 | 55 | 55.03 | 55.16 | 46.6302 |  |  |  | 430 | 1.493 | 1993-08-16 | 14 | 14 | 1.772 | AUG 26 | 14 | 1.427 | AUG 16 | 14 | 1.762 | JUL 27 | 14 | 1.382 | 1927-07-01 | 14 | 1.028 | JUL 27 | -0.585 | 0.98278 | Aug-16 | 14 | 1.358 | SEP 05 | 12
16 | 44.9 |  | 37.2 | 39.4869 | 32.7 | 40 | 39.61 | 39.73 | 32.8882 |  |  |  | 440 | 4.546 | 1993-10-17 | 13 | 13 | 4.424 | OCT 16 | 14 |  |  |  | 5.053 | SEP 02 | 14 | 3.624 | 1902-09-01 | 14 | 2.432 | SEP 02 | -1.852 | 2.3436 | Sep-02 | 14 | 2.862 | SEP 02 | 14
17 | 27.6 |  | 16.72 | 21.2906 | 17.7 | 21 | 21.42 | 21.6 | 16.7956 |  |  |  | 800 | 0.585 | 1993-07-27 | 14 | 14 | 0.967 | AUG 16 | 14 | 0.743 | JUL 28 | 14 | 1.352
18 | 9 |  | 2.52 | 3.27 | 2.73 | 3 | 3.28 | 0 | 3.1962 |  |  |  | 810 | 1.852 | 1993-09-02 | 14 | 14 | 2.357 | AUG 26 | 14 |  |  |  | 2.991
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | FREE-FLOAT TEMPERATURE OUTPUT | [11 empty] | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | OCT 16 | 15 | 69.81 | 1916-10-01 | 16 | 64.9 | OCT 16 | 16 | 65.25 | Oct-17 | 16 | 65.25 | OCT 15 | 16
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CASE# | TMP (C) | DATE | HR | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | SEP 02 | 15 | 43.44 | 1902-09-01 | 16 | 43 | SEP 02 | 15 | 42.46 | Oct-17 | 15 | 43.17 | SEP 15 | 15
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 600FF | 64.929 | 1993-10-17 | 15 | 15 | 65.11 | OCT 16 | 15 | 69.5 | OCT 17 | 15 | 68.6 | OCT 16 | 15 | 68.49 | 1916-10-01 | 16 | 63.3 | OCT 16 | 16 | 63.74 | Oct-17 | 16 | 63.82 | OCT 16 | 16
= | = | = | = | = | = | = | = | = | = |  |  |  | 900FF | 41.812 | 1993-10-17 | 15 | 15 | 43.44 | SEP 02 | 16 | 42.7 | SEP 02 | 15 | 44.8 | SEP 02 | 15 | 35.65 | 1902-09-01 | 16 | 36.1 | SEP 02 | 16 | 35.67 | Sep-02 | 15 | 37.58 | SEP 15 | 16
[13 empty] | 650FF | 63.236 | 1993-10-17 | 15 | 15 | 63.45 | OCT 16 | 15 | 68.2 | OCT 17 | 15 | 67 | OCT 17 | 15 | 51.21 | 1917-10-01 | 16 | 50.2 | OCT 17 | 15 | 55.34 | Oct-17 | 15 | 48.92 | OCT 15 | 15
[13 empty] | 950FF | 35.54 | 1993-09-02 | 16 | 16 | 36.23 | SEP 02 | 16 | 35.9 | SEP 02 | 16 | 38.5
[13 empty] | 960 | 48.943 | 1993-10-17 | 15 | 15 | 48.88 | OCT 06 | 15 | 49 | OCT 17 | 15 | 51 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
[13 empty] | MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
[13 empty] | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR
[13 empty] | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | JAN 04 | 7 | -9.96 | 1920-01-01 | 24 | -17.8 | JAN 04 | 8 | -17.81 | Jan-04 | 7 | -18.47 | JAN 08 | 9
[13 empty] | CASE# | TMP (C) | DATE | HR | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | JAN 04 | 8 | -3.94 | 1904-01-01 | 8 | -4 | JAN 04 | 8 | -6.38 | Jan-04 | 8 | -5.64 | JAN 08 | 9
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27 | [12 empty] | 600FF | -15.565 | 1993-01-04 | 7 | 7 | -17.05 | JAN 04 | 8 | -18.8 | JAN 04 | 8 | -18 | JAN 04 | 2 | -9.97 | 1916-01-01 | 6 | -22.9 | JAN 04 | 2 | -22.83 | Jan-04 | 7 | -22.91 | JAN 02 | 23
CASE 600 | [12 empty] | 900FF | -1.647 | 1993-01-04 | 8 | 8 | -3.15 | JAN 04 | 8 | -4.3 | JAN 04 | 8 | -4.5 | JAN 04 | 7 | -9.83 | 1908-12-01 | 1 | -20.2 | JAN 04 | 7 | -19.34 | Jan-04 | 7 | -19.96 | JAN 07 | 22
SOUTH SURFACE | [12 empty] | 650FF | -22.564 | 1993-01-04 | 6 | 6 | -22.96 | JAN 04 | 7 | -21.6 | JAN 04 | 2 | -23 | FEB 06 | 7 | 2.22 | 1906-02-01 | 7 | 1.4 | FEB 06 | 6 | -2.82 | Jan-04 | 8 | -0.39 | FEB 05 | 7
(USE COLUMN B ONLY) | [12 empty] | 950FF | -19.484 | 1993-01-04 | 6 | 6 | -20.04 | JAN 04 | 7 | -18.6 | JAN 04 | 7 | -19.7
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 960 | 2.729 | 1993-02-06 | 6 | 6 | 1.63 | FEB 06 | 7 | 3.9 | FEB 06 | 7 | 3.1 | USA DATE: SRES/SUN; UK-BRE DATE: SERIRES; SPAIN DATE: S3PAS; BEL/UK DATE: TRNSYS; FINLAND DATE: TASE; DATA DATE: YOUR
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | USA DATE: USA; UK-BRE DATE: UK-BRE; SPAIN DATE: SPAIN; BEL/UK DATE: BEL/UK; FINLAND DATE: FINLAND; DATA DATE: DATA
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | CODENAME: |  | ESP |  |  |  | BLAST |  |  | DOE2 |  |  | USA KW: TMP (C); UK-BRE KW: TMP (C); SPAIN KW: TMP (C); BEL/UK KW: TMP (C); FINLAND KW: TMP (C)
= | = | = | = | = | = | = | = | = | = |  |  |  | COUNTRY: |  | UK-DMU |  |  |  | USA/ITALY |  |  | USA |  |  | USA KW: 25.93; UK-BRE KW: 25.2; SPAIN KW: 24.49; BEL/UK KW: 24.22
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | CASE# | TMP (C) |  |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) | USA KW: 25.72; UK-BRE KW: 25.2; SPAIN KW: 24.47; BEL/UK KW: 24.45
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 600FF | 25.126 |  |  |  | 25.43 |  |  | 24.6 |  |  | 25.48 | USA KW: 19.62; UK-BRE KW: 18.4; SPAIN KW: 17.99; BEL/UK KW: 18.36
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 900FF | 25.453 |  |  |  | 25.93 |  |  | 24.7 |  |  | 25.49 | USA KW: 14.29; UK-BRE KW: 14; SPAIN KW: 14.53; BEL/UK KW: 14.64
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 650FF | 18.234 |  |  |  | 18.69 |  |  | 19.1 |  |  | 18.96 | USA KW: 28.54; UK-BRE KW: 28; SPAIN KW: 28.96; BEL/UK KW: 26.43
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 950FF | 14.14 |  |  |  | 14.26 |  |  | 14.3 |  |  | 14.97
5 | 0.5 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 1.9091 |  |  |  | 960 | 27.49 |  |  |  | 27.72 |  |  | 28 |  |  | 28.69
6 | 17.9 |  | 20.11 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 33.7081
7 | 58.6 |  | 70.22 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 88.5197
8 | 100.4 |  | 108.13 | 99.9892 | 112.85 | 104 | 71.22 | 107.47 | 136.7472 |  |  |  | BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - ANNUAL
9 | 205.9 |  | 219.58 | 211.0064 | 164.86 | 217 | 187.72 | 232.33 | 258.4548 |  |  |  | ANNUAL HEATING AND ANNUAL SENSIBLE COOLING [MWH]
10 | 326 |  | 343.67 | 331.0058 | 291.84 | 336 | 314.17 | 349.16 | 381.7547 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
11 | 415.1 |  | 435.54 | 418.1717 | 389.26 | 423 | 404.44 | 430.22 | 457.8998 |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
12 | 454.8 |  | 475.37 | 454.9942 | 437.2 | 459 | 443.61 | 459.85 | 478.0129 |  |  |  | 800-430 Mass, Heating w/ Op. Win. | -0.561 | -0.535 | -0.599 | -0.567 | -0.586 | -0.501 | -0.56 | -0.649 |  | -0.649 | -0.501
13 | 455.6 |  | 488.49 | 464.5689 | 455.75 | 469 | 452.5 | 462.28 | 469.2892 |  |  |  | 800-430 Mass, Cooling w/ Op. Win. | -0.429 | -0.393 | -0.367 | -0.432 | -0.462 | -0.368 | -0.4101 | -0.55 |  | -0.55 | -0.367
14 | 408.6 |  | 443.66 | 413.6364 | 413.67 | 418 | 400.56 | 404.57 | 408.1205 |  |  |  | 900-600 Mass, Heating | -3.126 | -3.163 | -3.837 | -3.329 | -3.608 | -3.152 | -3.217 | -3.321 | -2.724 | -3.837 | -3.126
15 | 321.2 |  | 367.07 | 334.2839 | 341.53 | 340 | 316.94 | 319.26 | 311.6345 |  |  |  | 900-600 Mass, Cooling | -4.005 | -3.833 | -4.624 | -4.113 | -4.549 | -3.92 | -4.007 | -4.179 | -3.964 | -4.624 | -3.833
16 | 200.6 |  | 246.71 | 211.9439 | 223.71 | 218 | 188.89 | 193.61 | 182.8382 |  |  |  | 940-640 Mass, Heating w/ Heating Setback | -1.958 | -1.867 | -2.304 | -2.024 | -2.392 | -1.886 | -1.963 | -1.986 | -2.01 | -2.392 | -1.867
17 | 102.3 |  | 119.19 | 111.7408 | 105.72 | 115 | 86.03 | 132.3 | 83.567 |  |  |  | 950-650 Mass, Cooling w/ Night Vent | -4.429 | -4.614 | -5.257 | -4.973 | -5.956 | -4.537 | -4.5584 | -4.685 | -4.807 | -5.956 | -4.429
18 | 78.8 |  | 68.86 | 73.0792 | 68.47 | 74 | 69.78 | 76.6 | 53.6695
19 | 37.1 |  | 19.75 | 17.7025 | 14.35 | 18 | 17.61 | 18.05 | 16.3694
20 | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.80671 |  |  |  | BASIC AND IN-DEPTH MASS EFFECT DELTA CHART - PEAK
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | PEAK HEATING AND SENSIBLE COOLING [MWH]
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 800-430 Mass, Heating w/ Op. Win. | -0.215 | -0.151 | -0.141 | -0.149 |  | -0.142 | -0.14444 | -0.198 |  | -0.215 | -0.141
= | = | = | = | = | = | = | = | = | = |  |  |  | 800-430 Mass, Cooling w/ Op. Win. | -0.908 | -0.805 | -0.684 | -0.41 |  | -0.547 | -0.81556 | -1.22 |  | -1.22 | -0.41
[13 empty] | 900-600 Mass, Heating | -0.587 | -0.487 | -0.488 | -0.498 |  | -0.429 | -0.41389 | -0.557 | -0.13 | -0.587 | -0.41389
[13 empty] | 900-600 Mass, Cooling | -3.306 | -2.81 | -3.198 | -2.956 |  | -2.952 | -2.9194 | -3.355 | -2.42 | -3.355 | -2.81
[13 empty] | 940-640 Mass, Heating w/ Heating Setback | -1.252 | -0.458 | -0.278 | -0.414 |  | -0.23 | -0.6 | -0.526 | -1.936 | -1.252 | -0.23
[13 empty] | 950-650 Mass, Cooling w/ Night Vent | -3.998 | -3.21 | -3.852 | -3.501 |  | -3.466 | -3.6917 | -3.812 | -3.674 | -3.998 | -3.21
BESTEST IN-DEPTH CASES 195 TO 220 DELTA CHART - ANNUAL
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27 | [12 empty] | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
CASE 600 | [13 empty] | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
WEST SURFACE | [12 empty] | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
(USE COLUMN B ONLY) | [12 empty] | 200-195 Heating Surface Convection | 1.085 | [8 empty] | 1.085 | 1.085
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 200-195 Cooling Surface Convection | 0.156 | [8 empty] | 0.156 | 0.156
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | 210-200 Heating Ext IR (Int IR "off") | 1.204 | [8 empty] | 1.204 | 1.204
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 210-200 Cooling Ext IR (Int IR "off") | -0.408 | [8 empty] | -0.408 | -0.408
= | = | = | = | = | = | = | = | = | = |  |  |  | 220-215 Heating Ext IR (Int IR "on") | 1.397 | [8 empty] | 1.397 | 1.397
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 220-215 Cooling Ext IR (Int IR "on") | -0.453 | [8 empty] | -0.453 | -0.453
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 215-200 Heating Int IR (Ext IR "off") | 0.295 | [8 empty] | 0.295 | 0.295
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 220-210 Heating Int IR (Ext IR "on") | 0.488 | 0.656 |  |  |  |  | 0.743 | 0.47 |  | 0.47 | 0.743
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.4 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 1.9091 |  |  |  | BESTEST IN-DEPTH CASES 195 TO 220 DELTA CHART - PEAK
6 | 17.9 |  | 19.96 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 33.7081 |  |  |  | PEAK HEATING AND SENSIBLE COOLING [MWH]
7 | 58.5 |  | 65.86 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 88.5197 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
8 | 91.8 |  | 97.11 | 99.9892 | 112.85 | 104 | 71.22 | 72 | 128.0895 |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
9 | 113.7 |  | 116.89 | 120.0506 | 121.41 | 125 | 85.58 | 92.6 | 146.0308 |  |  |  | 200-195 Heating Surface Convection | 0.647 | [8 empty] | 0.647 | 0.647
10 | 131.2 |  | 128.97 | 134.9631 | 123.51 | 140 | 98.03 | 112.8 | 152.3023 |  |  |  | 200-195 Cooling Surface Convection | 0.212 | [8 empty] | 0.212 | 0.212
11 | 145.7 |  | 138.05 | 149.5847 | 125.06 | 154 | 109.14 | 136.75 | 149.8995 |  |  |  | 210-200 Cooling Ext IR (Int IR "off") | -0.387 | [8 empty] | -0.387 | -0.387
12 | 153.8 |  | 141.34 | 153.1336 | 121.07 | 157 | 113.06 | 150.9 | 142.9895 |  |  |  | 220-215 Cooling Ext IR (Int IR on) | -0.447 | [8 empty] | -0.447 | -0.447
13 | 267.7 |  | 243.51 | 266.4489 | 117.94 | 270 | 235.17 | 382.5 | 249.3785 |  |  |  | 215-200 Heating Int IR (Ext IR "off") | 0.136 | [8 empty] | 0.136 | 0.136
14 | 464.8 |  | 462.83 | 461.2772 | 333.68 | 463 | 453.89 | 576.81 | 451.1566 |  |  |  | 215-200 Cooling Int IR (Ext IR "off") | 0.144 | [8 empty] | 0.144 | 0.144
15 | 635.1 |  | 664.62 | 635.5103 | 525.35 | 635 | 652.5 | 744.52 | 613.5218 |  |  |  | 220-210 Heating Int IR (Ext IR "on") | 0.166 | 0.307 |  |  |  |  | 0.35556 | 0.195 |  | 0.166 | 0.35556
16 | 738.3 |  | 786.35 | 719.3256 | 634.59 | 715 | 762.78 | 807.29 | 671.4247 |  |  |  | 220-210 Cooling Int IR (Ext IR "on") | 0.084 | 0.149 |  |  |  |  | 0.11111 | 0.071 |  | 0.071 | 0.149
17 | 623.9 |  | 649.05 | 502.7889 | 478.44 | 497 | 568.33 | 541.68 | 522.2558
18 | 296.9 |  | 243.11 | 141.2425 | 140.3 | 139 | 158 | 145.25 | 172.7792
19 | 68.8 |  | 43.19 | 25.2472 | 21.96 | 24 | 26.6 | 24.9 | 30.1416 |  |  |  | BESTEST IN-DEPTH CASES 220 TO 270 DELTA CHART - ANNUAL
20 | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1.2111 |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 230-220 Heating Infiltration | 3.432 | 3.525 | 3.456 | 3.531 | 3.522 | 3.615 | 3.543 | 3.527 |  | 3.432 | 3.615
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 230-220 Cooling Infiltration | 0.268 | 0.275 | 0.293 | 0.304 | 0.304 | 0.286 | 0.3032 | 0.302 |  | 0.268 | 0.304
= | = | = | = | = | = | = | = | = | = |  |  |  | 240-220 Heating Internal Gains | -1.295 | -1.206 | -1.339 | -1.333 | -1.341 | -1.228 | -1.221 | -1.203 |  | -1.341 | -1.203
[13 empty] | 240-220 Cooling Internal Gains | 0.229 | 0.371 | 0.261 | 0.412 | 0.411 | 0.374 | 0.3772 | 0.362 |  | 0.229 | 0.412
[13 empty] | 250-220 Heating Ext Solar Absorptance | -2.193 | -1.476 | -1.763 | -1.494 | -1.474 | -1.448 | -1.533 | -1.699 |  | -2.193 | -1.448
[13 empty] | 250-220 Cooling Ext Solar Abs. | 3.027 | 1.844 | 1.778 | 2.097 | 2.096 | 1.752 | 1.9472 | 2.697 |  | 1.752 | 3.027
[13 empty] | 270-220 Heating South Windows | -2.434 | -2.285 |  | -2.761 | -2.207 |  | -2.25 | -1.948 |  | -2.761 | -1.948
[13 empty] | 270-220 Cooling South Windows | 7.342 | 7.969 |  | 9.001 | 9.515 |  | 8.0272 | 8.031 |  | 7.342 | 9.515
HOURLY FREE FLOAT TEMPERATURE DATA | [12 empty] | BESTEST IN-DEPTH CASES 220 TO 270 DELTA CHART - PEAK
CASE 600FF JAN 4 | [12 empty] | PEAK HEATING AND SENSIBLE COOLING [MWH]
(USE COLUMN B ONLY) | [13 empty] | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | 230-220 Heating Infiltration | 1.519 | 1.704 | 1.529 | 1.584 |  | 1.811 | 1.5556 | 1.587 |  | 1.519 | 1.811
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 230-220 Cooling Infiltration | 0.499 | 0.48 | 0.518 | 0.535 |  | 0.485 | 0.52889 | 0.536 |  | 0.48 | 0.536
= | = | = | = | = | = | = | = | = | = |  |  |  | 240-220 Heating Internal Gains | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.189 | -0.18333 | -0.187 |  | -0.2 | -0.18
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 240-220 Cooling Internal Gains | 0.179 | 0.181 | 0.182 | 0.2 |  | 0.183 | 0.1825 | 0.184 |  | 0.179 | 0.2
1 | -8.88 | -12.0409 | -12.3 | -12.21 |  | -12.1 | -12.02 | -13.04 | -7.7028 |  |  |  | 250-220 Cooling Ext Solar Absorpance | 2.8 | 1.87 | 1.668 | 1.25 |  | 1.043 | 2.0489 | 3.699 |  | 1.043 | 3.699
2 | -10.48 | -13.523 | -14.1 | -13.8 |  | -13.7 | -13.5 | -14.59 | -9.2047 |  |  |  | 270-220 Cooling South Windows | 5.796 | 5.475 |  | 5.894 |  |  | 5.585 | 5.654 |  | 5.475 | 5.894
3 | -11.76 | -14.4018 | -15.4 | -14.9 |  | -14.7 | -14.7 | -15.65 | -10.6232
4 | -12.75 | -15.2598 | -16.3 | -15.79 |  | -15.6 | -15.65 | -16.46 | -11.849
5 | -13.69 | -15.9988 | -17.1 | -16.55 |  | -16.4 | -16.47 | -17.16 | -12.917 |  |  |  | BESTEST IN-DEPTH CASES 270 TO 320 DELTA CHART - ANNUAL
6 | -14.49 | -16.3983 | -17.9 | -17.2 |  | -17 | -17.14 | -17.79 | -13.866 |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
7 | -15.15 | -17.0108 | -18.5 | -17.74 |  | -17.6 | -17.7 | -18.32 | -14.7205 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
8 | -15.63 | -17.0531 | -18.8 | -17.85 |  | -17.8 | -17.59 | -18.47 | -15.2271 |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
9 | -14.63 | -13.7364 | -14.7 | -14.88 |  | -14.6 | -13.46 | -15.47 | -13.1183 |  |  |  | 280-270 Cooling Cavity Albedo | -2.655 | -2.775 |  | -3.317 | -3.236 |  | -3.003 | -2.457 |  | -3.317 | -2.457
10 | -10.03 | -7.9937 | -7.8 | -9.07 |  | -8.9 | -7.099 | -9.56 | -8.2162 |  |  |  | 320-270 Heating Thermostat | -0.651 | -0.721 |  | -0.714 | -0.779 |  | -0.699 | -0.649 |  | -0.779 | -0.649
11 | -2.2 | 2.6043 | 3.2 | 1.01 |  | 1 | 3.657 | 0.49 | -0.46838 |  |  |  | 320-270 Cooling Thermostat | -2.467 | -2.764 |  | -3.103 | -3.046 |  | -2.808 | -3.051 |  | -3.103 | -2.467
12 | 8.84 | 12.2151 | 13.4 | 11.21 |  | 10.7 | 13.49 | 10.39 | 8.1674 |  |  |  | 290-270 Cooling South Shading | -2.324 | -1.659 |  | -1.957 | -2.261 |  | -2.065 | -1.283 |  | -2.324 | -1.283
13 | 18.96 | 20.8602 | 22.3 | 20.03 |  | 19.2 | 21.77 | 18.75 | 15.7391 |  |  |  | 300-270 Cooling E&W Windows | -3.226 | -2.834 |  | -3.163 | -3.25 |  | -3.043 | -2.933 |  | -3.25 | -2.834
14 | 27.19 | 27.532 | 29.5 | 27.27 |  | 26.1 | 28.26 | 25.48 | 21.864 |  |  |  | 310-300 Heating E&W Shading | 0.46 | 0.25 |  | 0.263 | 0.201 |  | 0.486 |  |  | 0.201 | 0.486
15 | 33.22 | 31.3289 | 33.8 | 31.34 |  | 29.8 | 32.09 | 29.21 | 26.0163 |  |  |  | 310-300 Cooling E&W Shading | -1.57 | -1.266 |  | -1.42 | -1.629 |  | -1.994 |  |  | -1.994 | -1.266
16 | 35.51 | 31.0594 | 33.5 | 31.47 |  | 29.7 | 32.16 | 28.97 | 27.415
17 | 31.46 | 24.2801 | 27 | 25.96 |  | 23.9 | 25.71 | 22.58 | 25.1433
18 | 23.99 | 17.4634 | 19.7 | 18.96 |  | 17.6 | 18.84 | 15.59 | 20.9741
19 | 18.08 | 12.0529 | 13.7 | 13.04 |  | 12.2 | 13.1 | 10.2 | 16.8694 |  |  |  | BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL
20 | 13.02 | 7.5727 | 8.7 | 8.31 |  | 7.8 | 8.408 | 6.02 | 13.14 |  |  |  | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
21 | 8.87 | 3.5981 | 4.4 | 4.27 |  | 4 | 4.387 | 2.39 | 9.824 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
22 | 5.12 | 0.51861 | 1 | 0.99 |  | 0.9 | 0.9659 | -0.59 | 6.8516 |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
23 | 2.03 | -1.9381 | -1.9 | -1.66 |  | -1.7 | -1.781 | -3.04 | 4.2459 |  |  |  | 400-395 Low Mass, Heating Surf. Conv. & IR | 1.916 | 2.276 | 2.935 | 2.767 | 2.772 | 2.32 | 2.311 | 2.487 |  | 1.916 | 2.935
24 | -1.03 | -4.0741 | -4.4 | -3.92 |  | -3.9 | -4.032 | -5.14 | 1.9525 |  |  |  | 410-400 Low Mass, Heating Infiltration | 1.696 | 1.798 | 1.736 | 1.76 | 1.761 | 1.732 | 1.77 | 1.759 |  | 0.011 | 0.105
= | = | = | = | = | = | = | = | = | = |  |  |  | 420-410 Low Mass, Heating Int. Gains | -1.298 | -1.263 | -1.355 | -1.361 | -1.361 | -1.245 | -1.239 | -1.222 |  | -1.361 | -1.222
[13 empty] | 430-420 Low Mass, Heating Ext. Solar Abs. | -1.869 | -1.122 | -1.324 | -1.187 | -1.187 | -1.112 | -1.197 | -1.353 |  | -1.869 | -1.112
[13 empty] | 430-420 Low Mass, Cooling Ext Solar Abs. | 0.531 | 0.47 | 0.371 | 0.515 | 0.496 | 0.409 | 0.4599 | 0.732 |  | 0.371 | 0.732
[13 empty] | 600-430 Low Mass, Heating S. Window | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 |  | -2.118 | -1.133
[13 empty] | 600-430 Low Mass, Cooling S. Window | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 |  | 5.595 | 7.28
[13 empty] | 440-600 Low Mass, Heating Cavity Albedo | 0.153 | 0.214 |  | 0.426 | 0.215 |  | 0.226 | 0.28 |  | 0.153 | 0.426
[13 empty] | 440-600 Low Mass, Cooling Cavity Albedo | -2.17 | -2.261 |  | -2.604 | -2.76 |  | -2.517 | -2.094 |  | -2.76 | -2.094
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4 | [12 empty] | BESTEST IN-DEPTH CASES 395 TO 600 DELTA CHART - ANNUAL
(USE COLUMN B ONLY) | [12 empty] | ANNUAL HEATING AND SENSIBLE COOLING [MWH]
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier |  |  |  | CASES | UK-DMU | US/IT |  | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) |  |  |  | 400-395 Low Mass, Heating Surf. Conv. & IR | 0.805 | 1.071 | 1.148 | 1.31 |  | 1.079 | 1.115 | 1.25 |  | 0.805 | 1.31
= | = | = | = | = | = | = | = | = | = |  |  |  | 400-395 Low Mass, Cooling Surf. Conv. & IR | 0 | 0.219 | 0.265 | 0.272 |  | 0.256 | 0.25083 | 0.227 |  | 0 | 0.272
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier |  |  |  | 410-400 Low Mass, Heating Infiltration | 0.758 | 0.844 | 0.757 | 0.792 |  | 0.885 | 0.77778 | 0.794 |  | 0.757 | 0.885
1 | 1.61 | -0.17002 | -0.9 | -1.31 |  | -0.7 | -3.455 | -2.68 | 0.19483 |  |  |  | 410-400 Low Mass, Cooling Infiltration | 0.035 | 0.118 | 0.148 | 0.148 |  | 0.112 | 0.12972 | 0.138 |  | 0.035 | 0.148
2 | 0.93 | -0.79333 | -1.6 | -1.97 |  | -1.4 | -3.986 | -3.33 | -0.43113 |  |  |  | 420-410 Low Mass, Heating Int. Gains | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.183 | -0.18333 | -0.188 |  | -0.2 | -0.18
3 | 0.49 | -1.0908 | -2 | -2.37 |  | -1.8 | -4.395 | -3.72 | -1.0129 |  |  |  | 420-410 Low Mass, Cooling Int. Gains | 0.223 | 0.224 | 0.218 | 0.233 |  | 0.214 | 0.19472 | 0.211 |  | 0.19472 | 0.233
4 | 0.07 | -1.6745 | -2.5 | -2.81 |  | -2.3 | -4.8 | -4.1 | -1.5269 |  |  |  | 430-420 Low Mass, Cooling Ext. Solar Abs. | 1.235 | 0.849 | 0.796 | 0.715 |  | 0.637 | 0.86056 | 1.657 |  | 0.637 | 1.657
5 | -0.41 | -2.0414 | -2.9 | -3.25 |  | -2.7 | -5.216 | -4.51 | -2.0278 |  |  |  | 600-430 Low Mass, Cooling S. Window | 4.701 | 4.193 | 5.229 | 5.065 |  | 4.711 | 4.6878 | 4.234 |  | 4.193 | 5.229
6 | -0.87 | -2.4328 | -3.4 | -3.68 |  | -3.2 | -5.604 | -4.93 | -2.5116 |  |  |  | 440-600 Low Mass, Cooling Cavity Albedo | -1.648 | -1.541 |  | -1.774 |  |  | -1.8 | -1.534 |  | -1.8 | -1.534
7 | -1.27 | -2.9702 | -3.9 | -4.1 |  | -3.6 | -5.984 | -5.34 | -2.9838
8 | -1.64 | -3.1541 | -4.3 | -4.4 |  | -4 | -6.078 | -5.64 | -3.2952 |  |  |  | BESTEST Indepth South Window Delta Annual Cooling and Heating
9 | -1.54 | -2.3938 | -3.3 | -3.45 |  | -3.2 | -4.717 | -4.59 | -2.4372 |  |  |  |  | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
10 | -0.4 | -1.0924 | -1.6 | -1.6 |  | -1.7 | -2.977 | -2.64 | -0.70055 |  |  |  | 600-430 Low Mass, Heating S. Window | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 |  | -2.118 | -1.133
11 | 1.59 | 1.5953 | 1.2 | 1.66 |  | 0.9 | 0.2494 | 0.75 | 2.0135 |  |  |  | 600-430 Low Mass, Cooling S. Window | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 |  | 5.595 | 7.28
12 | 4.4 | 3.6249 | 3.5 | 4.4 |  | 3.1 | 2.539 | 3.26 | 4.7599 |  |  |  | 900-800 High Mass, Heating S. Window | -3.698 | -4.343 | -5.356 | -4.714 | -4.612 | -4.431 | -4.285 | -3.82 |  | -5.356 | -3.698
13 | 6.72 | 5.6203 | 5.5 | 6.56 |  | 5.1 | 4.382 | 4.99 | 6.9583 |  |  |  | 900-800 High Mass, Cooling S. Window | 2.019 | 2.376 | 2.4 | 2.893 | 3.193 | 2.377 | 2.2777 | 2.274 |  | 2.019 | 3.193
14 | 8.66 | 7.3237 | 7.2 | 8.39 |  | 6.8 | 5.853 | 6.51 | 8.6582
15 | 10.02 | 8.2691 | 8 | 9.04 |  | 7.6 | 6.614 | 7.11 | 9.6605
16 | 10.4 | 8.1513 | 7.9 | 8.58 |  | 7.4 | 6.333 | 6.68 | 9.6872
17 | 9.41 | 6.5309 | 6.2 | 6.44 |  | 5.8 | 4.204 | 4.24 | 8.4813
18 | 7.66 | 5.2506 | 4.7 | 4.43 |  | 4.4 | 2.869 | 2.45 | 7.0317
19 | 6.74 | 4.5191 | 3.8 | 3.37 |  | 3.6 | 2.107 | 1.71 | 5.9548
20 | 6 | 3.8832 | 3.2 | 2.73 |  | 3 | 1.581 | 1.32 | 5.089
21 | 5.41 | 3.2206 | 2.7 | 2.11 |  | 2.4 | 1.047 | 0.82 | 4.3328
22 | 4.74 | 2.8485 | 2.2 | 1.66 |  | 1.9 | 0.5504 | 0.42 | 3.6358
23 | 4.2 | 2.4745 | 1.7 | 1.26 |  | 1.5 | 0.1517 | 0.05 | 3.0215
24 | 3.66 | 1.8994 | 1.2 | 0.83 |  | 1 | -0.238 | -0.34 | 2.4507
= | = | = | = | = | = | = | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FFV JULY 27
(USE COLUMN B ONLY)
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | =
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
1 | 22.58 | 22.223 | 21.8 | 22.37 |  | 22.4 | 22.69 | 22.26 | 23.9355
2 | 21.15 | 21.1546 | 20.8 | 21.19 |  | 21.2 | 21.33 | 21.11 | 22.1389
3 | 20.23 | 20.3068 | 19.9 | 20.33 |  | 20.4 | 20.41 | 20.28 | 20.9043
4 | 19.45 | 19.5218 | 19.1 | 19.54 |  | 19.5 | 19.61 | 19.49 | 19.9694
5 | 18.95 | 19.295 | 18.8 | 19.21 |  | 19.2 | 19.16 | 19.14 | 19.2819
6 | 19.24 | 19.9144 | 19.5 | 19.86 |  | 19.9 | 19.6 | 19.81 | 19.256
7 | 21.16 | 22.5284 | 22.2 | 22.51 |  | 22.5 | 21.68 | 22.49 | 20.6617
8 | 23.56 | 25.0275 | 24 | 24.89 |  | 24.7 | 23.47 | 24.81 | 23.4614
9 | 25.67 | 28.3327 | 27.3 | 28.29 |  | 27.9 | 26.38 | 28.04 | 27.5572
10 | 28.91 | 31.8311 | 31.5 | 32.42 |  | 31.7 | 30.35 | 32.11 | 32.4359
11 | 32.8 | 35.825 | 36.2 | 37.12 |  | 36.2 | 34.82 | 36.54 | 37.2916
12 | 37.49 | 40.1973 | 41.1 | 42.08 |  | 40.8 | 39.38 | 41.15 | 41.9333
13 | 41.94 | 43.9026 | 45.4 | 46.46 |  | 45 | 43.48 | 45.03 | 46.0799
14 | 45.43 | 46.3464 | 48.4 | 49.69 |  | 48.1 | 46.14 | 47.65 | 49.0693
15 | 47.41 | 47.6362 | 50.1 | 51.3 |  | 49.6 | 47.4 | 49.04 | 50.6371
16 | 47.84 | 47.6029 | 50.1 | 51.28 |  | 49.7 | 47.33 | 49.28 | 50.6716
17 | 47.01 | 47.3406 | 49.1 | 50.46 |  | 49.1 | 46.71 | 48.73 | 49.6563
18 | 45.53 | 45.3964 | 46.8 | 48.37 |  | 47.2 | 45.28 | 46.58 | 47.8903
19 | 37.37 | 33.7034 | 34 | 35.39 |  | 35.1 | 33.1 | 34.91 | 38.0153
20 | 31.57 | 30.8664 | 30.9 | 31.63 |  | 31.6 | 30.49 | 30.69 | 33.8908
21 | 29.05 | 28.695 | 28.5 | 29.12 |  | 29.2 | 28.55 | 28.81 | 30.6722
22 | 26.92 | 26.4968 | 26.3 | 26.83 |  | 26.9 | 26.66 | 26.66 | 28.2523
23 | 25.52 | 25.6844 | 25.4 | 25.87 |  | 25.9 | 25.55 | 25.69 | 26.4232
24 | 23.84 | 24.0543 | 23.7 | 24.19 |  | 24.2 | 24.26 | 24.1 | 25.0843
= | = | = | = | = | = | = | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FFV JULY 27
(USE COLUMN B ONLY)
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | =
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
1 | 24.36 | 24.5601 | 24.2 | 24.52 |  | 24.6 | 25.28 | 24.53 | 26.5401
2 | 23.46 | 23.8963 | 23.5 | 23.81 |  | 23.9 | 24.47 | 23.8 | 25.4593
3 | 22.86 | 23.3126 | 22.9 | 23.22 |  | 23.3 | 23.87 | 23.23 | 24.6305
4 | 22.27 | 22.6823 | 22.3 | 22.6 |  | 22.7 | 23.26 | 22.6 | 23.872
5 | 21.86 | 22.4527 | 22 | 22.32 |  | 22.4 | 22.87 | 22.27 | 23.224
6 | 22.01 | 22.8128 | 22.5 | 22.77 |  | 22.8 | 23.06 | 22.67 | 22.9861
7 | 23.32 | 24.6678 | 24.3 | 24.73 |  | 24.6 | 24.38 | 24.55 | 23.5992
8 | 25.62 | 27.3586 | 26.5 | 27.59 |  | 27.1 | 27.21 | 27.57 | 25.4089
9 | 27.59 | 28.3229 | 27.5 | 29.09 |  | 28.2 | 27.98 | 29.42 | 26.949
10 | 28.82 | 29.2074 | 28.6 | 30.5 |  | 29.3 | 29.11 | 30.68 | 28.5539
11 | 29.84 | 30.1901 | 29.8 | 31.98 |  | 30.5 | 30.31 | 31.91 | 30.0202
12 | 30.98 | 31.3352 | 31.1 | 33.56 |  | 31.7 | 31.53 | 33.27 | 31.3657
13 | 32.08 | 32.1879 | 32.2 | 34.79 |  | 32.8 | 32.55 | 34.27 | 32.5538
14 | 32.85 | 32.845 | 33 | 35.65 |  | 33.6 | 33.15 | 34.9 | 33.3357
15 | 33.33 | 33.1198 | 33.4 | 35.96 |  | 34 | 33.37 | 35.19 | 33.7302
16 | 33.55 | 33.2478 | 33.5 | 35.82 |  | 34.1 | 33.38 | 35.28 | 33.7684
17 | 33.44 | 33.3523 | 33.5 | 35.61 |  | 34.1 | 33.37 | 35.3 | 33.7276
18 | 33.23 | 32.996 | 33.1 | 34.93 |  | 33.7 | 33.16 | 34.71 | 33.5033
19 | 30.92 | 30.203 | 30 | 30.96 |  | 30.6 | 30.43 | 30.74 | 31.475
20 | 29.17 | 29.3534 | 29.1 | 29.79 |  | 29.6 | 29.61 | 29.38 | 30.6968
21 | 28.31 | 28.5416 | 28.2 | 28.83 |  | 28.7 | 28.89 | 27.64 | 29.87
22 | 27.27 | 27.3759 | 27.1 | 27.59 |  | 27.5 | 27.93 | 27.46 | 28.9545
23 | 26.62 | 27.174 | 26.8 | 27.28 |  | 27.3 | 27.42 | 27.1 | 28.1401
24 | 25.54 | 25.9805 | 25.7 | 26.1 |  | 26.1 | 26.59 | 26.02 | 27.3968
= | = | = | = | = | = | = | = | = | =
HOURLY HEATING & COOLING LOAD DATA
CASE 600 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | =
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
1 | 3.25 | 3.8018 | 3.926 | 4.127 |  | 3.925 | 3.7667 | 4.225 | 3.7574
2 | 3.409 | 3.9109 | 4.035 | 4.258 |  | 4.037 | 3.8667 | 4.354 | 3.9161
3 | 3.392 | 3.8658 | 4.013 | 4.229 |  | 4.003 | 3.9028 | 4.321 | 3.9447
4 | 3.381 | 3.9196 | 4.041 | 4.22 |  | 4.001 | 3.8944 | 4.308 | 3.9245
5 | 3.417 | 3.9401 | 4.045 | 4.22 |  | 4.001 | 3.9167 | 4.303 | 3.9233
6 | 3.432 | 3.9258 | 4.036 | 4.221 |  | 4.001 | 3.9306 | 4.307 | 3.9186
7 | 3.421 | 3.937 | 4.045 | 4.222 |  | 4.001 | 3.9306 | 4.307 | 3.9206
8 | 3.337 | 3.7023 | 3.857 | 4.09 |  | 3.898 | 3.7528 | 4.167 | 3.4557
9 | 2.767 | 2.6752 | 2.559 | 2.902 |  | 2.706 | 2.4228 | 2.912 | 0.99839
10 | 1.497 | 1.3833 | 0.843 | 1.275 |  | 1.151 | 0.79667 | 1.466 | 0
11 | 0.151 | 0 | 0 | 0 |  | 0 | -0.034833 | 0 | -0.15154
12 | -0.771 | -1.2255 | -1.552 | -1.066 |  | -1.036 | -1.435 | -0.424 | -3.8604
13 | -2.66 | -2.4871 | -2.854 | -2.586 |  | -2.498 | -2.7203 | -2.364 | -4.543
14 | -3.575 | -2.9579 | -3.398 | -3.225 |  | -3.085 | -3.1556 | -2.759 | -4.096
15 | -3.527 | -2.631 | -3.116 | -2.826 |  | -2.637 | -2.8444 | -2.431 | -2.8463
16 | -2.435 | -1.3491 | -1.82 | -1.552 |  | -1.345 | -1.7158 | -1.14 | -0.78944
17 | -0.356 | 0 | 0 | -0.001 |  | 0 | 0 | 0 | 0
18 | 0.243 | 0.95017 | 0.775 | 0.8 |  | 0.88 | 0.77306 | 1.292 | 0.20065
19 | 1.53 | 2.3779 | 2.232 | 2.34 |  | 2.331 | 2.3014 | 2.445 | 2.8773
20 | 2.321 | 2.8665 | 2.933 | 2.988 |  | 2.949 | 2.9667 | 2.941 | 3.4716
21 | 2.641 | 3.2126 | 3.323 | 3.365 |  | 3.309 | 3.2778 | 3.405 | 3.5561
22 | 2.899 | 3.2845 | 3.487 | 3.532 |  | 3.347 | 3.4611 | 3.594 | 3.5731
23 | 3.017 | 3.3307 | 3.514 | 3.605 |  | 3.494 | 3.5 | 3.696 | 3.5225
24 | 3.008 | 3.388 | 3.561 | 3.663 |  | 3.527 | 3.4722 | 3.769 | 3.4923
= | = | = | = | = | = | = | = | = | =
HOURLY HEATING & COOLING LOAD DATA
CASE 900 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | =
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
1 | 2.441 | 3.1039 | 3.101 | 3.394 |  | 3.208 | 3.0806 | 3.4 | 3.4622
2 | 2.606 | 3.1986 | 3.237 | 3.54 |  | 3.349 | 3.2028 | 3.547 | 3.6331
3 | 2.623 | 3.2044 | 3.279 | 3.557 |  | 3.382 | 3.2778 | 3.573 | 3.6882
4 | 2.667 | 3.3056 | 3.377 | 3.613 |  | 3.447 | 3.3306 | 3.629 | 3.7203
5 | 2.744 | 3.3669 | 3.446 | 3.666 |  | 3.506 | 3.4167 | 3.687 | 3.7615
6 | 2.8 | 3.3993 | 3.498 | 3.715 |  | 3.558 | 3.4694 | 3.747 | 3.7885
7 | 2.834 | 3.4532 | 3.557 | 3.76 |  | 3.605 | 3.5167 | 3.797 | 3.8151
8 | 2.837 | 3.376 | 3.516 | 3.749 |  | 3.608 | 3.4639 | 3.794 | 3.565
9 | 2.641 | 2.8981 | 2.974 | 3.17 |  | 3.08 | 2.8333 | 3.168 | 2.1402
10 | 2.12 | 2.3463 | 2.202 | 2.32 |  | 2.348 | 2.0561 | 2.449 | 0.58142
11 | 1.502 | 1.3981 | 1.034 | 0.949 |  | 1.117 | 0.79333 | 1.293 | 0
12 | 0.676 | 0.37698 | 0.232 | 0.101 |  | 0.3 | 0.037278 | 0.619 | 0
13 | 0.074 | 0 | 0 | 0 |  | 0 | 0 | 0.136 | 0
14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.088 | 0
17 | 0.027 | 0.12409 | 0 | 0.277 |  | 0.143 | 0.13494 | 1.198 | 0
18 | 0.413 | 0.76691 | 0.739 | 1.216 |  | 0.91 | 0.76444 | 1.602 | 0
19 | 0.804 | 1.3064 | 1.14 | 1.608 |  | 1.281 | 1.1986 | 1.805 | 0
20 | 1.068 | 1.613 | 1.429 | 1.816 |  | 1.543 | 1.4589 | 1.943 | 0.72571
21 | 1.269 | 1.9255 | 1.7 | 2.038 |  | 1.81 | 1.7008 | 2.121 | 1.5679
22 | 1.502 | 2.1361 | 1.894 | 2.174 |  | 1.995 | 1.9342 | 2.227 | 2.0622
23 | 1.658 | 2.2208 | 2.028 | 2.293 |  | 2.154 | 2.0922 | 2.338 | 2.3715
24 | 1.749 | 2.3111 | 2.193 | 2.423 |  | 2.311 | 2.2267 | 2.458 | 2.6037
= | = | = | = | = | = | = | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
| ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
COUNTRY: | DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
= | = | = | = | = | = | = | = | = | =
-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0
-5 | 0 | 0 | 1 | 2 | 0 | 0 | 3 | 4 | 0
-4 | 0 | 1 | 3 | 3 | 4 | 4 | 6 | 5 | 0
-3 | 0 | 3 | 7 | 5 | 2 | 3 | 6 | 7 | 1
-2 | 3 | 5 | 5 | 7 | 7 | 8 | 12 | 10 | 4
-1 | 3 | 6 | 10 | 7 | 5 | 5 | 13 | 18 | 2
0 | 8 | 10 | 18 | 19 | 18 | 18 | 12 | 20 | 6
1 | 6 | 17 | 17 | 19 | 10 | 20 | 12 | 12 | 14
2 | 18 | 14 | 18 | 13 | 20 | 14 | 20 | 16 | 11
3 | 18 | 19 | 19 | 15 | 15 | 19 | 18 | 25 | 11
4 | 17 | 14 | 20 | 23 | 20 | 21 | 20 | 24 | 16
5 | 18 | 25 | 30 | 28 | 24 | 27 | 26 | 27 | 18
6 | 22 | 19 | 25 | 29 | 27 | 30 | 34 | 35 | 18
7 | 31 | 33 | 37 | 28 | 28 | 33 | 29 | 45 | 26
8 | 30 | 34 | 51 | 46 | 33 | 46 | 44 | 59 | 29
9 | 42 | 42 | 59 | 62 | 57 | 61 | 55 | 73 | 32
10 | 51 | 54 | 84 | 69 | 53 | 71 | 57 | 118 | 40
11 | 67 | 72 | 107 | 111 | 89 | 116 | 95 | 134 | 46
12 | 90 | 115 | 139 | 137 | 112 | 127 | 127 | 138 | 61
13 | 115 | 137 | 153 | 141 | 142 | 157 | 143 | 173 | 86
14 | 156 | 159 | 158 | 154 | 151 | 160 | 162 | 183 | 108
15 | 172 | 165 | 206 | 188 | 178 | 207 | 183 | 234 | 120
16 | 215 | 198 | 239 | 232 | 195 | 224 | 234 | 274 | 163
17 | 244 | 245 | 274 | 253 | 248 | 255 | 273 | 298 | 176
18 | 293 | 277 | 350 | 301 | 266 | 315 | 296 | 342 | 212
19 | 338 | 317 | 322 | 336 | 332 | 347 | 356 | 352 | 223
20 | 387 | 365 | 375 | 342 | 344 | 352 | 346 | 331 | 253
21 | 398 | 358 | 392 | 362 | 361 | 366 | 388 | 334 | 305
22 | 385 | 372 | 364 | 329 | 376 | 349 | 380 | 343 | 335
23 | 396 | 341 | 370 | 348 | 366 | 357 | 366 | 349 | 363
24 | 380 | 368 | 381 | 352 | 341 | 341 | 401 | 338 | 336
25 | 417 | 357 | 432 | 361 | 397 | 392 | 404 | 404 | 346
26 | 455 | 389 | 431 | 373 | 426 | 399 | 436 | 393 | 347
27 | 459 | 420 | 415 | 415 | 418 | 403 | 465 | 396 | 361
28 | 445 | 463 | 452 | 390 | 446 | 440 | 412 | 411 | 380
29 | 459 | 419 | 410 | 405 | 432 | 396 | 408 | 391 | 416
30 | 415 | 396 | 404 | 418 | 422 | 395 | 398 | 362 | 431
31 | 406 | 393 | 342 | 401 | 389 | 360 | 335 | 342 | 425
32 | 369 | 348 | 349 | 341 | 334 | 337 | 348 | 322 | 410
33 | 339 | 315 | 309 | 330 | 338 | 306 | 310 | 291 | 431
34 | 277 | 321 | 242 | 285 | 311 | 306 | 297 | 266 | 327
35 | 230 | 303 | 197 | 246 | 262 | 256 | 202 | 210 | 338
36 | 191 | 254 | 185 | 213 | 203 | 217 | 197 | 169 | 331
37 | 164 | 195 | 136 | 156 | 189 | 166 | 161 | 151 | 281
38 | 108 | 175 | 92 | 146 | 137 | 138 | 97 | 132 | 257
39 | 71 | 99 | 74 | 112 | 103 | 97 | 86 | 85 | 191
40 | 37 | 66 | 35 | 90 | 71 | 57 | 48 | 59 | 157
41 | 15 | 32 | 16 | 58 | 35 | 31 | 22 | 32 | 138
42 | 0 | 25 | 5 | 36 | 18 | 10 | 11 | 20 | 86
43 | 0 | 5 | 0 | 18 | 5 | 1 | 2 | 1 | 44
44 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 29
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | = | = | = | = |  | ======== | = | = | =
= | = | = | = | = |  | ======== | = | = | =
= | = | = | = | = |  | = | = | = | =
= | = | = | = | = |  | = | = | = | =
Data Tables for Figures 47 to 50 to allow Different labels for Series
Heating
| DMU | US-IT | NREL | NREL | BRE | SPAIN | BEL-BRE | FINLAND | Carrier
Heating | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Low Mass Solid Conduction | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839
430 Low Mass Opaque Windows | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51
800 High Mass Opaque Windows | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861
Cooling | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Low Mass Solid Conduction | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011
430 Low Mass Opaque Windows | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875
800 High Mass Opaque Windows | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325
Peak Heating | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Low Mass Solid Conduction | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.2211 | 2.27
430 Low Mass Opaque Windows | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.137
800 High Mass Opaque Windows | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.7861 | 3.939
Peak Cooling | ESP/DMU | BLAST/US-IT | DOE21D/NREL | SRES-SUN/NREL | SRES/BRE | S3PAS/SPAIN | TSYS/BEL-BRE | TASE/FINLAND | HAP/Carrier
395 Low Mass Solid Conduction | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.3625 | 0.345
430 Low Mass Opaque Windows | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 1.7983 | 2.578
800 High Mass Opaque Windows | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 0.98278 | 1.358

## ESP-DMU
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
ESP-RV8
Program Version Release Date:
Program Name for Tables and Charts (short): |  |  |  | ESP
Results Submission Date:
Modeler Organization for Titles (long):
De Montfort University, U.K.
Modeler Organization for Tables and Charts (short): |  |  |  | DMU
Model / Organization Indentifier Charts (short): |  |  |  | ESP/DMU
UK-DMU
ESP-DMU
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | MWh
600 | 4.296
610 | 4.355
620 | 4.613
630 | 5.05
640 | 2.751
650 | 0
900 | 1.17
910 | 1.575
920 | 3.313
930 | 4.143
940 | 0.793
950 | 0
960 | 2.311
195 | 4.167
200 | 5.252
210 | 6.456
215 | 5.547
220 | 6.944
230 | 10.376
240 | 5.649
250 | 4.751
270 | 4.51
280 | 4.675
290 | 4.577
300 | 4.761
310 | 5.221
320 | 3.859
395 | 4.984
400 | 6.9
410 | 8.596
420 | 7.298
430 | 5.429
440 | 4.449
800 | 4.868
810 | 1.839
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | MWh
600 | 6.137
610 | 3.915
620 | 3.417
630 | 2.129
640 | 5.952
650 | 4.816
900 | 2.132
910 | 0.821
920 | 1.84
930 | 1.039
940 | 2.079
950 | 0.387
960 | 0.488
195 | 0.414
200 | 0.57
210 | 0.162
215 | 0.639
220 | 0.186
230 | 0.454
240 | 0.415
250 | 3.213
270 | 7.528
280 | 4.873
290 | 5.204
300 | 4.302
310 | 2.732
320 | 5.061
395 | 0
400 | 0
410 | 0
420 | 0.011
430 | 0.542
440 | 3.967
800 | 0.113
810 | 1.052
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | KW | DATE | TIME
600 | 3.437 | 1993-01-04 | 5
610 | 3.437 | 1993-01-04 | 5
620 | 3.591 | 1993-01-04 | 6
630 | 3.592 | 1993-01-04 | 7
640 | 5.232 | 1993-01-04 | 7
650 | 0
900 | 2.85 | 1993-01-04 | 7
910 | 2.858 | 1993-01-04 | 7
920 | 3.308 | 1993-01-04 | 7
930 | 3.355 | 1993-01-04 | 7
940 | 3.98 | 1993-01-04 | 7
950 | 0
960 | 2.41 | 1993-01-04 | 7
195 | 2.004 | 1993-01-04 | 2
200 | 2.651 | 1993-01-04 | 5
210 | 2.701 | 1993-01-04 | 5
215 | 2.787 | 1993-01-04 | 5
220 | 2.867 | 1993-01-04 | 5
230 | 4.386 | 1993-01-04 | 5
240 | 2.685 | 1993-01-04 | 5
250 | 2.866 | 1993-01-04 | 5
270 | 2.863 | 1993-01-04 | 5
280 | 2.864 | 1993-01-04 | 5
290 | 2.863 | 1993-01-04 | 5
300 | 3.014 | 1993-01-04 | 6
310 | 3.015 | 1993-01-04 | 6
320 | 2.861 | 1993-01-04 | 5
395 | 2.062 | 1993-01-04 | 7
400 | 2.867 | 1993-01-04 | 5
410 | 3.625 | 1993-01-04 | 5
420 | 3.443 | 1993-01-04 | 5
430 | 3.442 | 1993-01-04 | 5
440 | 3.439 | 1993-01-04 | 5
800 | 3.227 | 1993-01-04 | 5
810 | 2.979 | 1993-01-04 | 7
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | kW | DATE | TIME
600 | 6.194 | 1993-10-17 | 13
610 | 5.669 | 1993-11-25 | 13
620 | 3.634 | 1993-07-26 | 16
630 | 3.072 | 1993-07-26 | 16
640 | 6.161 | 1993-10-17 | 13
650 | 6.031 | 1993-10-17 | 13
900 | 2.888 | 1993-10-17 | 14
910 | 1.896 | 1993-10-17 | 15
920 | 2.385 | 1993-07-26 | 16
930 | 1.873 | 1993-07-26 | 17
940 | 2.888 | 1993-10-17 | 14
950 | 2.033 | 1993-09-02 | 14
960 | 0.953 | 1993-08-16 | 16
195 | 0.651 | 1993-07-26 | 15
200 | 0.863 | 1993-08-16 | 14
210 | 0.476 | 1993-08-16 | 16
215 | 1.007 | 1993-08-11 | 14
220 | 0.56 | 1993-07-27 | 15
230 | 1.059 | 1993-07-27 | 15
240 | 0.739 | 1993-07-27 | 15
250 | 3.36 | 1993-09-05 | 12
270 | 6.356 | 1993-11-25 | 13
280 | 4.444 | 1993-10-17 | 13
290 | 6.269 | 1993-01-13 | 13
300 | 3.404 | 1993-07-26 | 16
310 | 2.848 | 1993-07-26 | 16
320 | 5.701 | 1993-11-25 | 13
395 | 0
400 | 0
410 | 0.035 | 1993-07-27 | 16
420 | 0.258 | 1993-07-27 | 15
430 | 1.493 | 1993-08-16 | 14
440 | 4.546 | 1993-10-17 | 13
800 | 0.585 | 1993-07-27 | 14
810 | 1.852 | 1993-09-02 | 14
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | TEMP (C) | DATE | TIME
600FF | 64.929 | 1993-10-17 | 15
900FF | 41.812 | 1993-10-17 | 15
650FF | 63.236 | 1993-10-17 | 15
950FF | 35.54 | 1993-09-02 | 16
960 | 48.943 | 1993-10-17 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | ESP
VERSION: |  | UK-DMU
CASE# | TMP (C) | DATE | HR
600FF | -15.565 | 1993-01-04 | 7
900FF | -1.647 | 1993-01-04 | 8
650FF | -22.564 | 1993-01-04 | 6
950FF | -19.484 | 1993-01-04 | 6
960 | 2.729 | 1993-02-06 | 6
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | ESP
VERSION: |  | UK-DMU
CASE# | TMP (C)
600FF | 25.126
900FF | 25.453
650FF | 18.234
950FF | 14.14
960 | 27.49
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
SURFACE | kWh/m2
= | = | = | =
NORTH | 427
EAST | 959
WEST | 1086
SOUTH | 1456
HORZ. | 1797
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | kWh/m2
= | = | = | =
920WEST | 732
900SOUTH | 946
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
CASE# | kWh/m2
= | = | = | =
930WEST | 599
910SOUTH | 785
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 1.6
8 | 13.8
9 | 31.6
10 | 48.3
11 | 61.6
12 | 69.3
13 | 71.7
14 | 68.1
15 | 58.9
16 | 44.4
17 | 26.9
18 | 8.7
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 1.6
8 | 13.5
9 | 31
10 | 47.1
11 | 59.7
12 | 67.4
13 | 70.1
14 | 67.3
15 | 58.9
16 | 44.9
17 | 27.6
18 | 9
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.5
6 | 17.9
7 | 58.6
8 | 100.4
9 | 205.9
10 | 326
11 | 415.1
12 | 454.8
13 | 455.6
14 | 408.6
15 | 321.2
16 | 200.6
17 | 102.3
18 | 78.8
19 | 37.1
20 | 1.1
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.4
6 | 17.9
7 | 58.5
8 | 91.8
9 | 113.7
10 | 131.2
11 | 145.7
12 | 153.8
13 | 267.7
14 | 464.8
15 | 635.1
16 | 738.3
17 | 623.9
18 | 296.9
19 | 68.8
20 | 1.6
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | TEMP (C)
= | = | = | =
1 | -8.88
2 | -10.48
3 | -11.76
4 | -12.75
5 | -13.69
6 | -14.49
7 | -15.15
8 | -15.63
9 | -14.63
10 | -10.03
11 | -2.2
12 | 8.84
13 | 18.96
14 | 27.19
15 | 33.22
16 | 35.51
17 | 31.46
18 | 23.99
19 | 18.08
20 | 13.02
21 | 8.87
22 | 5.12
23 | 2.03
24 | -1.03
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | TEMP (C)
= | = | = | =
1 | 1.61
2 | 0.93
3 | 0.49
4 | 0.07
5 | -0.41
6 | -0.87
7 | -1.27
8 | -1.64
9 | -1.54
10 | -0.4
11 | 1.59
12 | 4.4
13 | 6.72
14 | 8.66
15 | 10.02
16 | 10.4
17 | 9.41
18 | 7.66
19 | 6.74
20 | 6
21 | 5.41
22 | 4.74
23 | 4.2
24 | 3.66
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | TEMP (C)
= | = | = | =
1 | 22.58
2 | 21.15
3 | 20.23
4 | 19.45
5 | 18.95
6 | 19.24
7 | 21.16
8 | 23.56
9 | 25.67
10 | 28.91
11 | 32.8
12 | 37.49
13 | 41.94
14 | 45.43
15 | 47.41
16 | 47.84
17 | 47.01
18 | 45.53
19 | 37.37
20 | 31.57
21 | 29.05
22 | 26.92
23 | 25.52
24 | 23.84
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | TEMP (C)
= | = | = | =
1 | 24.36
2 | 23.46
3 | 22.86
4 | 22.27
5 | 21.86
6 | 22.01
7 | 23.32
8 | 25.62
9 | 27.59
10 | 28.82
11 | 29.84
12 | 30.98
13 | 32.08
14 | 32.85
15 | 33.33
16 | 33.55
17 | 33.44
18 | 33.23
19 | 30.92
20 | 29.17
21 | 28.31
22 | 27.27
23 | 26.62
24 | 25.54
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | kWh
= | = | = | =
1 | 3.25
2 | 3.409
3 | 3.392
4 | 3.381
5 | 3.417
6 | 3.432
7 | 3.421
8 | 3.337
9 | 2.767
10 | 1.497
11 | 0.151
12 | -0.771
13 | -2.66
14 | -3.575
15 | -3.527
16 | -2.435
17 | -0.356
18 | 0.243
19 | 1.53
20 | 2.321
21 | 2.641
22 | 2.899
23 | 3.017
24 | 3.008
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | ESP
VERSION: | UK-DMU
HOUR | kWh
= | = | = | =
1 | 2.441
2 | 2.606
3 | 2.623
4 | 2.667
5 | 2.744
6 | 2.8
7 | 2.834
8 | 2.837
9 | 2.641
10 | 2.12
11 | 1.502
12 | 0.676
13 | 0.074
14 | 0
15 | 0
16 | 0
17 | 0.027
18 | 0.413
19 | 0.804
20 | 1.068
21 | 1.269
22 | 1.502
23 | 1.658
24 | 1.749
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | ESP
VERSION: | UK-DMU
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 0
-4 | 0
-3 | 0
-2 | 3
-1 | 3
0 | 8
1 | 6
2 | 18
3 | 18
4 | 17
5 | 18
6 | 22
7 | 31
8 | 30
9 | 42
10 | 51
11 | 67
12 | 90
13 | 115
14 | 156
15 | 172
16 | 215
17 | 244
18 | 293
19 | 338
20 | 387
21 | 398
22 | 385
23 | 396
24 | 380
25 | 417
26 | 455
27 | 459
28 | 445
29 | 459
30 | 415
31 | 406
32 | 369
33 | 339
34 | 277
35 | 230
36 | 191
37 | 164
38 | 108
39 | 71
40 | 37
41 | 15
42 | 0
43 | 0
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## BLAST-USIT
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
BLAST-3.0 level 193 v.1
Program Version Release Date:
Program Name for Tables and Charts: |  |  |  | BLAST
Results Submission Date:
Modeler Organization for Titles (long):
National Renewable Energy Lab, U.S.; Politecnico Torino, Italy
Modeler Organization for Tables and Charts (short): |  |  |  | US-IT
Model / Organization Indentifier Charts (short): |  |  |  | BLAST/US-IT
US/IT
BLAST-US/IT
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | BLAST
VERSION: | US/IT
CASE# | MWh
600 | 4.773
610 | 4.806
620 | 5.049
630 | 5.359
640 | 2.888
650 | 0
900 | 1.61
910 | 1.862
920 | 3.752
930 | 4.347
940 | 1.021
950 | 0
960 | 2.664
195
200
210 | 6.559
215
220 | 7.215
230 | 10.74
240 | 6.009
250 | 5.739
270 | 4.93
280 | 5.125
290 | 4.959
300 | 5.077
310 | 5.327
320 | 4.209
395 | 4.799
400 | 7.075
410 | 8.873
420 | 7.61
430 | 6.488
440 | 4.987
800 | 5.953
810 | 2.446
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | BLAST
VERSION: | US/IT
CASE# | MWh
600 | 6.433
610 | 4.851
620 | 4.092
630 | 3.108
640 | 6.183
650 | 5.14
900 | 2.6
910 | 1.533
920 | 2.616
930 | 1.934
940 | 2.536
950 | 0.526
960 | 0.666
195
200
210 | 0.613
215
220 | 0.701
230 | 0.976
240 | 1.072
250 | 2.545
270 | 8.67
280 | 5.895
290 | 7.011
300 | 5.836
310 | 4.57
320 | 5.906
395 | 0.011
400 | 0.04
410 | 0.059
420 | 0.147
430 | 0.617
440 | 4.172
800 | 0.224
810 | 1.405
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | BLAST
VERSION: | US/IT
CASE# | KW | DATE | TIME
600 | 3.94 | JAN 04 | 5
610 | 3.941 | JAN 04 | 5
620 | 3.941 | JAN 04 | 5
630 | 3.941 | JAN 04 | 5
640 | 5.486 | JAN 04 | 8
650 | 0 | JAN 04
900 | 3.453 | JAN 04 | 7
910 | 3.456 | JAN 04 | 7
920 | 3.703 | JAN 04 | 7
930 | 3.732 | JAN 04 | 7
940 | 5.028 | JAN 04 | 8
950 | 0
960 | 2.751 | JAN 04 | 8
195
200
210 | 2.973 | JAN 04 | 5
215
220 | 3.28 | JAN 04 | 5
230 | 4.984 | JAN 04 | 2
240 | 3.1 | JAN 04 | 5
250 | 3.279 | JAN 04 | 5
270 | 3.277 | JAN 04 | 5
280 | 3.278 | JAN 04 | 5
290 | 3.277 | JAN 04 | 5
300 | 3.276 | JAN 04 | 5
310 | 3.277 | JAN 04 | 5
320 | 3.275 | JAN 04 | 5
395 | 2.209 | JAN 04 | 8
400 | 3.28 | JAN 04 | 5
410 | 4.124 | JAN 04 | 5
420 | 3.944 | JAN 04 | 5
430 | 3.944 | JAN 04 | 5
440 | 3.942 | JAN 04 | 5
800 | 3.793 | JAN 04 | 7
810 | 3.566 | JAN 04 | 7
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | BLAST
VERSION: | US/IT
CASE# | kW | DATE | TIME
600 | 5.965 | OCT 16 | 14
610 | 5.824 | NOV 25 | 14
620 | 4.075 | JUL 26 | 17
630 | 3.704 | JUL 26 | 17
640 | 5.892 | OCT 16 | 14
650 | 5.831 | OCT 16 | 14
900 | 3.155 | OCT 06 | 15
910 | 2.5 | OCT 21 | 15
920 | 2.933 | JUL 26 | 17
930 | 2.546 | JUL 26 | 17
940 | 3.155 | OCT 06 | 15
950 | 2.621 | SEP 02 | 15
960 | 1.144 | JUL 26 | 16
195
200
210 | 1.017 | JUL 26 | 15
215
220 | 1.166 | JUL 26 | 15
230 | 1.646 | JUL 26 | 15
240 | 1.347 | JUL 26 | 15
250 | 3.036 | SEP 05 | 12
270 | 6.641 | NOV 25 | 14
280 | 4.631 | NOV 25 | 13
290 | 6.555 | NOV 25 | 14
300 | 4.093 | JUL 26 | 17
310 | 3.749 | JUN 30 | 17
320 | 5.946 | NOV 25 | 14
395 | 0.362 | JUL 26 | 18
400 | 0.581 | JUL 26 | 17
410 | 0.699 | JUL 26 | 17
420 | 0.923 | JUL 26 | 15
430 | 1.772 | AUG 26 | 14
440 | 4.424 | OCT 16 | 14
800 | 0.967 | AUG 16 | 14
810 | 2.357 | AUG 26 | 14
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | BLAST
VERSION: | US/IT
CASE# | TEMP (C) | DATE | TIME
600FF | 65.11 | OCT 16 | 15
900FF | 43.44 | SEP 02 | 16
650FF | 63.45 | OCT 16 | 15
950FF | 36.23 | SEP 02 | 16
960 | 48.88 | OCT 06 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | BLAST
VERSION: |  | USA/ITALY
CASE# | TMP (C) | DATE | HR
600FF | -17.05 | JAN 04 | 8
900FF | -3.15 | JAN 04 | 8
650FF | -22.96 | JAN 04 | 7
950FF | -20.04 | JAN 04 | 7
960 | 1.63 | FEB 06 | 7
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | BLAST
VERSION: |  | USA/ITALY
CASE# | TMP (C)
600FF | 25.43
900FF | 25.93
650FF | 18.69
950FF | 14.26
960 | 27.72
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
SURFACE | kWh/m2
= | = | = | =
NORTH
EAST
WEST
SOUTH
HORZ.
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
CASE# | kWh/m2
= | = | = | =
920WEST
900SOUTH
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
CASE# | kWh/m2
= | = | = | =
930WEST
910SOUTH
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | Wh/m2
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | Wh/m2
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | Wh/m2
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | Wh/m2
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | TEMP (C)
= | = | = | =
1 | -12.0409
2 | -13.523
3 | -14.4018
4 | -15.2598
5 | -15.9988
6 | -16.3983
7 | -17.0108
8 | -17.0531
9 | -13.7364
10 | -7.9937
11 | 2.6043
12 | 12.2151
13 | 20.8602
14 | 27.532
15 | 31.3289
16 | 31.0594
17 | 24.2801
18 | 17.4634
19 | 12.0529
20 | 7.5727
21 | 3.5981
22 | 0.51861
23 | -1.9381
24 | -4.0741
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | TEMP (C)
= | = | = | =
1 | -0.17002
2 | -0.79333
3 | -1.0908
4 | -1.6745
5 | -2.0414
6 | -2.4328
7 | -2.9702
8 | -3.1541
9 | -2.3938
10 | -1.0924
11 | 1.5953
12 | 3.6249
13 | 5.6203
14 | 7.3237
15 | 8.2691
16 | 8.1513
17 | 6.5309
18 | 5.2506
19 | 4.5191
20 | 3.8832
21 | 3.2206
22 | 2.8485
23 | 2.4745
24 | 1.8994
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | TEMP (C)
= | = | = | =
1 | 22.223
2 | 21.1546
3 | 20.3068
4 | 19.5218
5 | 19.295
6 | 19.9144
7 | 22.5284
8 | 25.0275
9 | 28.3327
10 | 31.8311
11 | 35.825
12 | 40.1973
13 | 43.9026
14 | 46.3464
15 | 47.6362
16 | 47.6029
17 | 47.3406
18 | 45.3964
19 | 33.7034
20 | 30.8664
21 | 28.695
22 | 26.4968
23 | 25.6844
24 | 24.0543
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | TEMP (C)
= | = | = | =
1 | 24.5601
2 | 23.8963
3 | 23.3126
4 | 22.6823
5 | 22.4527
6 | 22.8128
7 | 24.6678
8 | 27.3586
9 | 28.3229
10 | 29.2074
11 | 30.1901
12 | 31.3352
13 | 32.1879
14 | 32.845
15 | 33.1198
16 | 33.2478
17 | 33.3523
18 | 32.996
19 | 30.203
20 | 29.3534
21 | 28.5416
22 | 27.3759
23 | 27.174
24 | 25.9805
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | kWh
= | = | = | =
1 | 3.8018
2 | 3.9109
3 | 3.8658
4 | 3.9196
5 | 3.9401
6 | 3.9258
7 | 3.937
8 | 3.7023
9 | 2.6752
10 | 1.3833
11 | 0
12 | -1.2255
13 | -2.4871
14 | -2.9579
15 | -2.631
16 | -1.3491
17 | 0
18 | 0.95017
19 | 2.3779
20 | 2.8665
21 | 3.2126
22 | 3.2845
23 | 3.3307
24 | 3.388
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | BLAST
VERSION: | USA/IT
HOUR | kWh
= | = | = | =
1 | 3.1039
2 | 3.1986
3 | 3.2044
4 | 3.3056
5 | 3.3669
6 | 3.3993
7 | 3.4532
8 | 3.376
9 | 2.8981
10 | 2.3463
11 | 1.3981
12 | 0.37698
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0.12409
18 | 0.76691
19 | 1.3064
20 | 1.613
21 | 1.9255
22 | 2.1361
23 | 2.2208
24 | 2.3111
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | BLAST
VERSION: | USA/IT
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 0
-4 | 1
-3 | 3
-2 | 5
-1 | 6
0 | 10
1 | 17
2 | 14
3 | 19
4 | 14
5 | 25
6 | 19
7 | 33
8 | 34
9 | 42
10 | 54
11 | 72
12 | 115
13 | 137
14 | 159
15 | 165
16 | 198
17 | 245
18 | 277
19 | 317
20 | 365
21 | 358
22 | 372
23 | 341
24 | 368
25 | 357
26 | 389
27 | 420
28 | 463
29 | 419
30 | 396
31 | 393
32 | 348
33 | 315
34 | 321
35 | 303
36 | 254
37 | 195
38 | 175
39 | 99
40 | 66
41 | 32
42 | 25
43 | 5
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## DOE21D
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
DOE-2.1D 14
Program Version Release Date:
Program Name for Tables and Charts: |  |  |  | DOE21D
Results Submission Date:
Modeler Organization for Titles (long):
National Renewable Energy Lab
Modeler Organization for Tables and Charts (short): |  |  |  | NREL
Model / Organization Indentifier Charts (short): |  |  |  | DOE21D/NREL
USA
DOE21D
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | DOE2
VERSION: | USA
CASE# | MWh
600 | 5.709
610 | 5.786
620 | 5.944
630 | 6.469
640 | 3.543
650 | 0
900 | 1.872
910 | 2.254
920 | 4.255
930 | 5.335
940 | 1.239
950 | 0
960 | 2.928
195
200
210
215
220 | 8.787
230 | 12.243
240 | 7.448
250 | 7.024
270
280
290
300
310
320
395 | 5.835
400 | 8.77
410 | 10.506
420 | 9.151
430 | 7.827
440
800 | 7.228
810
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | DOE2
VERSION: | USA
CASE# | MWh
600 | 7.079
610 | 4.852
620 | 4.334
630 | 2.489
640 | 6.759
650 | 5.795
900 | 2.455
910 | 0.976
920 | 2.44
930 | 1.266
940 | 2.34
950 | 0.538
960 | 0.428
195
200
210
215
220 | 0.399
230 | 0.692
240 | 0.66
250 | 2.177
270
280
290
300
310
320
395 | 0
400 | 0.002
410 | 0.01
420 | 0.051
430 | 0.422
440
800 | 0.055
810
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | DOE2
VERSION: | USA
CASE# | KW | DATE | TIME
600 | 4.045 | JAN 04 | 5
610 | 4.034 | JAN 04 | 5
620 | 4.046 | JAN 04 | 5
630 | 4.025 | JAN 04 | 5
640 | 5.943 | JAN 04 | 8
650 | 0
900 | 3.557 | JAN 04 | 7
910 | 3.564 | JAN 04 | 7
920 | 3.805 | JAN 04 | 7
930 | 3.832 | JAN 04 | 7
940 | 5.665 | JAN 04 | 8
950 | 0
960 | 2.727 | JAN 04 | 8
195
200
210
215
220 | 3.465 | JAN 04 | 5
230 | 4.994 | JAN 04 | 2
240 | 3.282 | JAN 04 | 5
250 | 3.465 | JAN 04 | 5
270
280
290
300
310
320
395 | 2.328 | JAN 04 | 3
400 | 3.476 | JAN 04 | 5
410 | 4.233 | JAN 04 | 5
420 | 4.05 | JAN 04 | 5
430 | 4.05 | JAN 04 | 5
440
800 | 3.909 | JAN 04 | 7
810
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | DOE2
VERSION: | USA
CASE# | kW | DATE | TIME
600 | 6.656 | OCT 16 | 13
610 | 6.064 | JAN 13 | 14
620 | 4.43 | JUL 26 | 17
630 | 3.588 | JUL 26 | 17
640 | 6.576 | OCT 16 | 14
650 | 6.516 | OCT 16 | 14
900 | 3.458 | OCT 17 | 14
910 | 2.336 | OCT 17 | 15
920 | 3.109 | JUL 26 | 17
930 | 2.388 | JUL 26 | 18
940 | 3.458 | OCT 17 | 14
950 | 2.664 | SEP 2 | 15
960 | 1.057 | JUL 26 | 16
195
200
210
215
220 | 0.937 | JUL 27 | 14
230 | 1.455 | JUL 27 | 14
240 | 1.119 | JUL 27 | 14
250 | 2.605 | SEP 5 | 11
270
280
290
300
310
320
395 | 0
400 | 0.265 | JUL 27 | 17
410 | 0.413 | JUL 27 | 17
420 | 0.631 | JUL 27 | 15
430 | 1.427 | AUG 16 | 14
440
800 | 0.743 | JUL 28 | 14
810
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | DOE2
VERSION: | USA
CASE# | TEMP (C) | DATE | TIME
600FF | 69.5 | OCT 17 | 15
900FF | 42.7 | SEP 02 | 15
650FF | 68.2 | OCT 17 | 15
950FF | 35.9 | SEP 02 | 16
960 | 49 | OCT 17 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | DOE2
VERSION: |  | USA
CASE# | TMP (C) | DATE | HR
600FF | -18.8 | JAN 04 | 8
900FF | -4.3 | JAN 04 | 8
650FF | -21.6 | JAN 04 | 2
950FF | -18.6 | JAN 04 | 7
960 | 3.9 | FEB 06 | 7
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | DOE2
VERSION: |  | USA
CASE# | TMP (C)
600FF | 24.6
900FF | 24.7
650FF | 19.1
950FF | 14.3
960 | 28
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
SURFACE | kWh/m2
= | = | = | =
NORTH | 434
EAST | 1155
WEST | 1079
SOUTH | 1566
HORZ. | 1831
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
CASE# | kWh/m2
= | = | = | =
920WEST | 735
900SOUTH | 1051
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
CASE# | kWh/m2
= | = | = | =
930WEST | 481
910SOUTH | 831
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 1.5
8 | 12.59
9 | 30.01
10 | 46.23
11 | 59.31
12 | 65.05
13 | 66.98
14 | 63.11
15 | 51.79
16 | 37.13
17 | 19.14
18 | 4.62
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 1.8
8 | 13.92
9 | 31.75
10 | 45.24
11 | 56.63
12 | 61.58
13 | 63.7
14 | 61.46
15 | 51.67
16 | 37.2
17 | 16.72
18 | 2.52
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 20.11
7 | 70.22
8 | 108.13
9 | 219.58
10 | 343.67
11 | 435.54
12 | 475.37
13 | 488.49
14 | 443.66
15 | 367.07
16 | 246.71
17 | 119.19
18 | 68.86
19 | 19.75
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 19.96
7 | 65.86
8 | 97.11
9 | 116.89
10 | 128.97
11 | 138.05
12 | 141.34
13 | 243.51
14 | 462.83
15 | 664.62
16 | 786.35
17 | 649.05
18 | 243.11
19 | 43.19
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | -12.3
2 | -14.1
3 | -15.4
4 | -16.3
5 | -17.1
6 | -17.9
7 | -18.5
8 | -18.8
9 | -14.7
10 | -7.8
11 | 3.2
12 | 13.4
13 | 22.3
14 | 29.5
15 | 33.8
16 | 33.5
17 | 27
18 | 19.7
19 | 13.7
20 | 8.7
21 | 4.4
22 | 1
23 | -1.9
24 | -4.4
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | -0.9
2 | -1.6
3 | -2
4 | -2.5
5 | -2.9
6 | -3.4
7 | -3.9
8 | -4.3
9 | -3.3
10 | -1.6
11 | 1.2
12 | 3.5
13 | 5.5
14 | 7.2
15 | 8
16 | 7.9
17 | 6.2
18 | 4.7
19 | 3.8
20 | 3.2
21 | 2.7
22 | 2.2
23 | 1.7
24 | 1.2
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | 21.8
2 | 20.8
3 | 19.9
4 | 19.1
5 | 18.8
6 | 19.5
7 | 22.2
8 | 24
9 | 27.3
10 | 31.5
11 | 36.2
12 | 41.1
13 | 45.4
14 | 48.4
15 | 50.1
16 | 50.1
17 | 49.1
18 | 46.8
19 | 34
20 | 30.9
21 | 28.5
22 | 26.3
23 | 25.4
24 | 23.7
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | 24.2
2 | 23.5
3 | 22.9
4 | 22.3
5 | 22
6 | 22.5
7 | 24.3
8 | 26.5
9 | 27.5
10 | 28.6
11 | 29.8
12 | 31.1
13 | 32.2
14 | 33
15 | 33.4
16 | 33.5
17 | 33.5
18 | 33.1
19 | 30
20 | 29.1
21 | 28.2
22 | 27.1
23 | 26.8
24 | 25.7
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | kWh
= | = | = | =
1 | 3.926
2 | 4.035
3 | 4.013
4 | 4.041
5 | 4.045
6 | 4.036
7 | 4.045
8 | 3.857
9 | 2.559
10 | 0.843
11 | 0
12 | -1.552
13 | -2.854
14 | -3.398
15 | -3.116
16 | -1.82
17 | 0
18 | 0.775
19 | 2.232
20 | 2.933
21 | 3.323
22 | 3.487
23 | 3.514
24 | 3.561
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | DOE2.1D
VERSION: | USA
HOUR | kWh
= | = | = | =
1 | 3.101
2 | 3.237
3 | 3.279
4 | 3.377
5 | 3.446
6 | 3.498
7 | 3.557
8 | 3.516
9 | 2.974
10 | 2.202
11 | 1.034
12 | 0.232
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0
18 | 0.739
19 | 1.14
20 | 1.429
21 | 1.7
22 | 1.894
23 | 2.028
24 | 2.193
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | DOE2.1D
VERSION: | USA
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 1
-4 | 3
-3 | 7
-2 | 5
-1 | 10
0 | 18
1 | 17
2 | 18
3 | 19
4 | 20
5 | 30
6 | 25
7 | 37
8 | 51
9 | 59
10 | 84
11 | 107
12 | 139
13 | 153
14 | 158
15 | 206
16 | 239
17 | 274
18 | 350
19 | 322
20 | 375
21 | 392
22 | 364
23 | 370
24 | 381
25 | 432
26 | 431
27 | 415
28 | 452
29 | 410
30 | 404
31 | 342
32 | 349
33 | 309
34 | 242
35 | 197
36 | 185
37 | 136
38 | 92
39 | 74
40 | 35
41 | 16
42 | 5
43 | 0
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## SRES-SUN
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
SERIRES/SUNCODE 5.7
Program Version Release Date:
Program Name for Tables and Charts (short): |  |  |  | SRES-SUN
Results Submission Date:
Modeler Organization for Titles (long):
National Renewable Energy Lab
Modeler Organization for Tables and Charts (short): |  |  |  | NREL
Model / Organization Indentifier for Charts (short): |  |  |  | SRES-SUN/NREL
USA
SRES/SUN
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | MWh
600 | 5.226
610 | 5.28
620 | 5.554
630 | 5.883
640 | 3.255
650 | 0
900 | 1.897
910 | 2.174
920 | 4.093
930 | 4.755
940 | 1.231
950 | 0
960 | 2.884
195
200
210
215
220 | 8.102
230 | 11.633
240 | 6.769
250 | 6.608
270 | 5.341
280 | 5.937
290 | 5.406
300 | 5.587
310 | 5.85
320 | 4.627
395 | 5.199
400 | 7.966
410 | 9.726
420 | 8.365
430 | 7.178
440 | 5.652
800 | 6.611
810 | 3.004
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | MWh
600 | 7.278
610 | 5.448
620 | 4.633
630 | 3.493
640 | 7.026
650 | 5.894
900 | 3.165
910 | 1.872
920 | 2.943
930 | 2.173
940 | 3.036
950 | 0.921
960 | 0.803
195
200
210
215
220 | 0.827
230 | 1.131
240 | 1.239
250 | 2.924
270 | 9.828
280 | 6.511
290 | 7.871
300 | 6.665
310 | 5.245
320 | 6.725
395 | 0.016
400 | 0.061
410 | 0.084
420 | 0.189
430 | 0.704
440 | 4.674
800 | 0.272
810 | 1.711
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | KW | DATE | TIME
600 | 4.258 | JAN 04 | 2
610 | 4.258 | JAN 04 | 2
620 | 4.277 | JAN 04 | 2
630 | 4.28 | JAN 04 | 2
640 | 6.53 | JAN 04 | 8
650 | 0
900 | 3.76 | JAN 04 | 7
910 | 3.764 | JAN 04 | 7
920 | 4.013 | JAN 04 | 7
930 | 4.042 | JAN 04 | 7
940 | 6.116 | JAN 04 | 8
950 | 0
960 | 2.863 | JAN 04 | 8
195
200
210
215
220 | 3.695 | JAN 04 | 2
230 | 5.279 | JAN 04 | 2
240 | 3.495 | JAN 04 | 2
250 | 3.695 | JAN 04 | 2
270 | 3.661 | JAN 04 | 2
280 | 3.685 | JAN 04 | 2
290 | 3.661 | JAN 04 | 2
300 | 3.681 | JAN 04 | 2
310 | 3.669 | JAN 04 | 2
320 | 3.651 | JAN 04 | 2
395 | 2.385 | JAN 04 | 3
400 | 3.695 | JAN 04 | 2
410 | 4.487 | JAN 04 | 2
420 | 4.287 | JAN 04 | 2
430 | 4.287 | JAN 04 | 2
440 | 4.277 | JAN 04 | 2
800 | 4.138 | JAN 04 | 2
810 | 3.915 | JAN 04 | 7
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | kW | DATE | TIME
600 | 6.827 | OCT 16 | 14
610 | 6.371 | NOV 25 | 14
620 | 4.593 | JUL 26 | 17
630 | 4.116 | JUL 26 | 17
640 | 6.776 | OCT 16 | 14
650 | 6.671 | OCT 16 | 14
900 | 3.871 | OCT 17 | 14
910 | 3.277 | OCT 17 | 15
920 | 3.487 | JUL 26 | 17
930 | 3.08 | JUL 26 | 17
940 | 3.871 | OCT 17 | 14
950 | 3.17 | SEP 02 | 14
960 | 1.37 | JUL 26 | 16
195
200
210
215
220 | 1.34 | JUL 26 | 15
230 | 1.875 | JUL 26 | 15
240 | 1.54 | JUL 26 | 15
250 | 2.59 | AUG 26 | 14
270 | 7.234 | OCT 16 | 14
280 | 5.22 | OCT 16 | 14
290 | 6.976 | NOV 25 | 14
300 | 4.657 | JUL 26 | 17
310 | 4.164 | JUL 26 | 17
320 | 6.553 | OCT 16 | 14
395 | 0.394 | JUL 26 | 17
400 | 0.666 | JUL 26 | 16
410 | 0.814 | JUL 26 | 15
420 | 1.047 | JUL 26 | 15
430 | 1.762 | JUL 26 | 15
440 | 5.053 | OCT 16 | 14
800 | 1.352 | JUL 27 | 14
810 | 2.991 | SEP 02 | 14
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | TEMP (C) | DATE | TIME
600FF | 68.6 | OCT 16 | 15
900FF | 44.8 | SEP 02 | 15
650FF | 67 | OCT 16 | 15
950FF | 38.5 | SEP 02 | 15
960 | 51 | OCT 17 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | SRES/SUN
VERSION: |  | USA
CASE# | TMP (C) | DATE | HR
600FF | -18 | JAN 04 | 7
900FF | -4.5 | JAN 04 | 8
650FF | -23 | JAN 04 | 2
950FF | -19.7 | JAN 04 | 7
960 | 3.1 | FEB 06 | 7
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | SRES/SUN
VERSION: |  | USA
CASE# | TMP (C)
600FF | 25.48
900FF | 25.49
650FF | 18.96
950FF | 14.97
960 | 28.69
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
SURFACE | kWh/m2
= | = | = | =
NORTH | 456
EAST | 1083
WEST | 1003
SOUTH | 1476
HORZ. | 1832
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | kWh/m2
= | = | = | =
920WEST | 689
900SOUTH | 962
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
CASE# | kWh/m2
= | = | = | =
930WEST | 554
910SOUTH | 803
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3.0447
8 | 20.6464
9 | 38.8836
10 | 54.5664
11 | 65.9733
12 | 71.7839
13 | 72.2839
14 | 66.4075
15 | 54.8997
16 | 38.8836
17 | 20.4797
18 | 3.0447
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 2.9967
8 | 20.1831
9 | 37.955
10 | 53.2444
11 | 64.4672
12 | 69.9819
13 | 70.8061
14 | 65.6633
15 | 54.9214
16 | 39.4869
17 | 21.2906
18 | 3.27
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.16667
6 | 27.8275
7 | 77.3025
8 | 99.9892
9 | 211.0064
10 | 331.0058
11 | 418.1717
12 | 454.9942
13 | 464.5689
14 | 413.6364
15 | 334.2839
16 | 211.9439
17 | 111.7408
18 | 73.0792
19 | 17.7025
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.16667
6 | 27.8275
7 | 77.3025
8 | 99.9892
9 | 120.0506
10 | 134.9631
11 | 149.5847
12 | 153.1336
13 | 266.4489
14 | 461.2772
15 | 635.5103
16 | 719.3256
17 | 502.7889
18 | 141.2425
19 | 25.2472
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | -12.21
2 | -13.8
3 | -14.9
4 | -15.79
5 | -16.55
6 | -17.2
7 | -17.74
8 | -17.85
9 | -14.88
10 | -9.07
11 | 1.01
12 | 11.21
13 | 20.03
14 | 27.27
15 | 31.34
16 | 31.47
17 | 25.96
18 | 18.96
19 | 13.04
20 | 8.31
21 | 4.27
22 | 0.99
23 | -1.66
24 | -3.92
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | -1.31
2 | -1.97
3 | -2.37
4 | -2.81
5 | -3.25
6 | -3.68
7 | -4.1
8 | -4.4
9 | -3.45
10 | -1.6
11 | 1.66
12 | 4.4
13 | 6.56
14 | 8.39
15 | 9.04
16 | 8.58
17 | 6.44
18 | 4.43
19 | 3.37
20 | 2.73
21 | 2.11
22 | 1.66
23 | 1.26
24 | 0.83
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | 22.37
2 | 21.19
3 | 20.33
4 | 19.54
5 | 19.21
6 | 19.86
7 | 22.51
8 | 24.89
9 | 28.29
10 | 32.42
11 | 37.12
12 | 42.08
13 | 46.46
14 | 49.69
15 | 51.3
16 | 51.28
17 | 50.46
18 | 48.37
19 | 35.39
20 | 31.63
21 | 29.12
22 | 26.83
23 | 25.87
24 | 24.19
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | TEMP (C)
= | = | = | =
1 | 24.52
2 | 23.81
3 | 23.22
4 | 22.6
5 | 22.32
6 | 22.77
7 | 24.73
8 | 27.59
9 | 29.09
10 | 30.5
11 | 31.98
12 | 33.56
13 | 34.79
14 | 35.65
15 | 35.96
16 | 35.82
17 | 35.61
18 | 34.93
19 | 30.96
20 | 29.79
21 | 28.83
22 | 27.59
23 | 27.28
24 | 26.1
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | kWh
= | = | = | =
1 | 4.127
2 | 4.258
3 | 4.229
4 | 4.22
5 | 4.22
6 | 4.221
7 | 4.222
8 | 4.09
9 | 2.902
10 | 1.275
11 | 0
12 | -1.066
13 | -2.586
14 | -3.225
15 | -2.826
16 | -1.552
17 | -0.001
18 | 0.8
19 | 2.34
20 | 2.988
21 | 3.365
22 | 3.532
23 | 3.605
24 | 3.663
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | SRES/SUN
VERSION: | USA
HOUR | kWh
= | = | = | =
1 | 3.394
2 | 3.54
3 | 3.557
4 | 3.613
5 | 3.666
6 | 3.715
7 | 3.76
8 | 3.749
9 | 3.17
10 | 2.32
11 | 0.949
12 | 0.101
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0.277
18 | 1.216
19 | 1.608
20 | 1.816
21 | 2.038
22 | 2.174
23 | 2.293
24 | 2.423
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | SRES/SUN
VERSION: | USA
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 2
-4 | 3
-3 | 5
-2 | 7
-1 | 7
0 | 19
1 | 19
2 | 13
3 | 15
4 | 23
5 | 28
6 | 29
7 | 28
8 | 46
9 | 62
10 | 69
11 | 111
12 | 137
13 | 141
14 | 154
15 | 188
16 | 232
17 | 253
18 | 301
19 | 336
20 | 342
21 | 362
22 | 329
23 | 348
24 | 352
25 | 361
26 | 373
27 | 415
28 | 390
29 | 405
30 | 418
31 | 401
32 | 341
33 | 330
34 | 285
35 | 246
36 | 213
37 | 156
38 | 146
39 | 112
40 | 90
41 | 58
42 | 36
43 | 18
44 | 5
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## SRES-BRE
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
SERIRES 1.2
Program Version Release Date:
Program Name for Tables and Charts: |  |  |  | SRES
Results Submission Date:
Modeler Organization for Titles (long):
Building Research Establishment, UK
Modeler Organization for Tables and Charts (short): |  |  |  | BRE
Model / Organization Indentifier Charts (short): |  |  |  | SRES/BRE
UK-BRE
SRES-BRE
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | MWh
600 | 5.596
610 | 5.62
620 | 5.734
630 | 6.001
640 | 3.803
650 | 0
900 | 1.988
910 | 2.282
920 | 4.058
930 | 4.728
940 | 1.411
950 | 0
960 | 2.851
195
200
210
215
220 | 8.127
230 | 11.649
240 | 6.786
250 | 6.653
270 | 5.92
280 | 6.148
290 | 5.942
300 | 5.964
310 | 6.165
320 | 5.141
395 | 5.201
400 | 7.973
410 | 9.734
420 | 8.373
430 | 7.186
440 | 5.811
800 | 6.6
810 | 2.828
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | MWh
600 | 7.964
610 | 5.778
620 | 5.004
630 | 3.701
640 | 7.811
650 | 6.545
900 | 3.415
910 | 1.854
920 | 3.092
930 | 2.238
940 | 3.241
950 | 0.589
960 | 0.718
195
200
210
215
220 | 0.835
230 | 1.139
240 | 1.246
250 | 2.931
270 | 10.35
280 | 7.114
290 | 8.089
300 | 7.1
310 | 5.471
320 | 7.304
395 | 0.014
400 | 0.058
410 | 0.084
420 | 0.188
430 | 0.684
440 | 5.204
800 | 0.222
810 | 1.708
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | KW | DATE | TIME
600
610
620
630
640
650
900
910
920
930
940
950
960
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
800
810
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | kW | DATE | TIME
600
610
620
630
640
650
900
910
920
930
940
950
960
195
200
210
215
220
230
240
250
270
280
290
300
310
320
395
400
410
420
430
440
800
810
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | TEMP (C) | DATE | TIME
600FF
900FF
650FF
950FF
960
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | SERIRES
VERSION: |  | UK-BRE
CASE# | TMP (C) | DATE | HR
600FF
900FF
650FF
950FF
960
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | SERIRES
VERSION: |  | UK-BRE
CASE# | TMP (C)
600FF | 25.93
900FF | 25.72
650FF | 19.62
950FF | 14.29
960 | 28.54
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
SURFACE | kWh/m2
= | = | = | =
NORTH | 407.3
EAST | 1217.3
WEST | 856.5
SOUTH | 1467.7
HORZ. | 1831.8
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | kWh/m2
= | = | = | =
920WEST | 562.96
900SOUTH | 954.3
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
CASE# | kWh/m2
= | = | = | =
930WEST | 441.3
910SOUTH | 774.86
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3.02
8 | 20.59
9 | 38.83
10 | 54.53
11 | 54.77
12 | 59.65
13 | 60.1
14 | 55.24
15 | 45.68
16 | 32.37
17 | 17.06
18 | 2.54
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3
8 | 20.24
9 | 38.01
10 | 53.27
11 | 53.37
12 | 57.91
13 | 58.3
14 | 54.15
15 | 45.38
16 | 32.7
17 | 17.7
18 | 2.73
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.14
6 | 29.94
7 | 89.2
8 | 112.85
9 | 164.86
10 | 291.84
11 | 389.26
12 | 437.2
13 | 455.75
14 | 413.67
15 | 341.53
16 | 223.71
17 | 105.72
18 | 68.47
19 | 14.35
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.14
6 | 29.94
7 | 89.2
8 | 112.85
9 | 121.41
10 | 123.51
11 | 125.06
12 | 121.07
13 | 117.94
14 | 333.68
15 | 525.35
16 | 634.59
17 | 478.44
18 | 140.3
19 | 21.96
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | TEMP (C)
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | TEMP (C)
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | TEMP (C)
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | TEMP (C)
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | kWh
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | SERIRES
VERSION: | UK-BRE
HOUR | kWh
= | = | = | =
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | SERIRES
VERSION: | UK-BRE
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 0
-4 | 4
-3 | 2
-2 | 7
-1 | 5
0 | 18
1 | 10
2 | 20
3 | 15
4 | 20
5 | 24
6 | 27
7 | 28
8 | 33
9 | 57
10 | 53
11 | 89
12 | 112
13 | 142
14 | 151
15 | 178
16 | 195
17 | 248
18 | 266
19 | 332
20 | 344
21 | 361
22 | 376
23 | 366
24 | 341
25 | 397
26 | 426
27 | 418
28 | 446
29 | 432
30 | 422
31 | 389
32 | 334
33 | 338
34 | 311
35 | 262
36 | 203
37 | 189
38 | 137
39 | 103
40 | 71
41 | 35
42 | 18
43 | 5
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | ======== | = | =
= | ======== | = | =
= | = | = | =
= | = | = | =

## S3PAS
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
S3PAS
Program Version Release Date:
Program Name for Tables and Charts: |  |  |  | S3PAS
Results Submission Date:
Modeler Organization for Titles (long):
University of Sevilla, Spain
Modeler Organization for Tables and Charts (short): |  |  |  | SPAIN
Model / Organization Indentifier Charts (short): |  |  |  | S3PAS/SPAIN
SPAIN
S3PAS
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | MWh
600 | 4.882
610 | 4.971
620 | 5.564
630 | 6.095
640 | 3.065
650 | 0
900 | 1.73
910 | 2.063
920 | 4.235
930 | 5.168
940 | 1.179
950 | 0
960 | 2.943
195
200
210
215
220 | 7.422
230 | 11.037
240 | 6.194
250 | 5.974
270
280
290
300
310
320
395 | 4.967
400 | 7.287
410 | 9.019
420 | 7.774
430 | 6.662
440
800 | 6.161
810
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | MWh
600 | 6.492
610 | 4.764
620 | 4.011
630 | 2.489
640 | 6.247
650 | 5.088
900 | 2.572
910 | 1.428
920 | 2.457
930 | 1.439
940 | 2.489
950 | 0.551
960 | 0.643
195
200
210
215
220 | 0.734
230 | 1.02
240 | 1.108
250 | 2.486
270
280
290
300
310
320
395 | 0.01
400 | 0.042
410 | 0.063
420 | 0.154
430 | 0.563
440
800 | 0.195
810
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | KW | DATE | TIME
600 | 4.037 | JAN 04 | 2
610 | 4.037 | JAN 04 | 2
620 | 4.277 | JAN 04 | 2
630 | 4.278 | JAN 04 | 2
640 | 6.347 | JAN 04 | 8
650 | 0
900 | 3.608 | JAN 04 | 8
910 | 3.618 | JAN 04 | 8
920 | 4.029 | JAN 04 | 7
930 | 4.064 | JAN 04 | 7
940 | 6.117 | JAN 04 | 8
950 | 0
960 | 2.852 | JAN 04 | 8
195
200
210
215
220 | 3.348 | JAN 04 | 8
230 | 5.159 | JAN 04 | 2
240 | 3.159 | JAN 04 | 8
250 | 3.341 | JAN 04 | 6
270
280
290
300
310
320
395 | 2.263 | JAN 04 | 4
400 | 3.342 | JAN 04 | 8
410 | 4.227 | JAN 04 | 2
420 | 4.044 | JAN 04 | 2
430 | 4.044 | JAN 04 | 2
440
800 | 3.902 | JAN 04 | 8
810
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | kW | DATE | TIME
600 | 6.286 | NOV 25 | 14
610 | 6.17 | NOV 25 | 14
620 | 4.297 | JUL 26 | 17
630 | 3.665 | JUL 26 | 17
640 | 6.25 | NOV 25 | 14
650 | 6.143 | NOV 25 | 14
900 | 3.334 | OCT 17 | 15
910 | 2.786 | OCT 17 | 15
920 | 3.071 | JUL 26 | 17
930 | 2.486 | JUL 26 | 17
940 | 3.334 | OCT 17 | 15
950 | 2.677 | SEP 02 | 15
960 | 1.179 | JUL 26 | 16
195
200
210
215
220 | 1.215 | JUL 26 | 16
230 | 1.7 | JUL 26 | 15
240 | 1.398 | JUL 26 | 16
250 | 2.258 | AUG 26 | 14
270
280
290
300
310
320
395 | 0.356 | JUL 26 | 18
400 | 0.612 | JUL 26 | 17
410 | 0.724 | JUL 26 | 16
420 | 0.938 | JUL 26 | 15
430 | 1.575 | JUL 26 | 15
440
800 | 1.028 | JUL 27 | 15
810
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | TEMP (C) | DATE | TIME
600FF | 64.9 | OCT 16 | 16
900FF | 43 | SEP 02 | 15
650FF | 63.3 | OCT 16 | 16
950FF | 36.1 | SEP 02 | 16
960 | 50.2 | OCT 17 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | S3PAS
VERSION: |  | SPAIN
CASE# | TMP (C) | DATE | HR
600FF | -17.8 | JAN 04 | 8
900FF | -4 | JAN 04 | 8
650FF | -22.9 | JAN 04 | 2
950FF | -20.2 | JAN 04 | 7
960 | 1.4 | FEB 06 | 6
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | S3PAS
VERSION: |  | SPAIN
CASE# | TMP (C)
600FF | 25.2
900FF | 25.2
650FF | 18.4
950FF | 14
960 | 28
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
SURFACE | kWh/m2
= | = | = | =
NORTH | 457
EAST | 1082
WEST | 1002
SOUTH | 1474
HORZ. | 1832
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | kWh/m2
= | = | = | =
920WEST | 642
900SOUTH | 926
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
CASE# | kWh/m2
= | = | = | =
930WEST | 431
910SOUTH | 757
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3
8 | 21
9 | 39
10 | 55
11 | 66
12 | 72
13 | 72
14 | 66
15 | 55
16 | 39
17 | 20
18 | 3
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3
8 | 20
9 | 38
10 | 53
11 | 64
12 | 70
13 | 71
14 | 66
15 | 55
16 | 40
17 | 21
18 | 3
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 28
7 | 80
8 | 104
9 | 217
10 | 336
11 | 423
12 | 459
13 | 469
14 | 418
15 | 340
16 | 218
17 | 115
18 | 74
19 | 18
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 28
7 | 80
8 | 104
9 | 125
10 | 140
11 | 154
12 | 157
13 | 270
14 | 463
15 | 635
16 | 715
17 | 497
18 | 139
19 | 24
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | TEMP (C)
= | = | = | =
1 | -12.1
2 | -13.7
3 | -14.7
4 | -15.6
5 | -16.4
6 | -17
7 | -17.6
8 | -17.8
9 | -14.6
10 | -8.9
11 | 1
12 | 10.7
13 | 19.2
14 | 26.1
15 | 29.8
16 | 29.7
17 | 23.9
18 | 17.6
19 | 12.2
20 | 7.8
21 | 4
22 | 0.9
23 | -1.7
24 | -3.9
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | TEMP (C)
= | = | = | =
1 | -0.7
2 | -1.4
3 | -1.8
4 | -2.3
5 | -2.7
6 | -3.2
7 | -3.6
8 | -4
9 | -3.2
10 | -1.7
11 | 0.9
12 | 3.1
13 | 5.1
14 | 6.8
15 | 7.6
16 | 7.4
17 | 5.8
18 | 4.4
19 | 3.6
20 | 3
21 | 2.4
22 | 1.9
23 | 1.5
24 | 1
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | TEMP (C)
= | = | = | =
1 | 22.4
2 | 21.2
3 | 20.4
4 | 19.5
5 | 19.2
6 | 19.9
7 | 22.5
8 | 24.7
9 | 27.9
10 | 31.7
11 | 36.2
12 | 40.8
13 | 45
14 | 48.1
15 | 49.6
16 | 49.7
17 | 49.1
18 | 47.2
19 | 35.1
20 | 31.6
21 | 29.2
22 | 26.9
23 | 25.9
24 | 24.2
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | TEMP (C)
= | = | = | =
1 | 24.6
2 | 23.9
3 | 23.3
4 | 22.7
5 | 22.4
6 | 22.8
7 | 24.6
8 | 27.1
9 | 28.2
10 | 29.3
11 | 30.5
12 | 31.7
13 | 32.8
14 | 33.6
15 | 34
16 | 34.1
17 | 34.1
18 | 33.7
19 | 30.6
20 | 29.6
21 | 28.7
22 | 27.5
23 | 27.3
24 | 26.1
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | kWh
= | = | = | =
1 | 3.925
2 | 4.037
3 | 4.003
4 | 4.001
5 | 4.001
6 | 4.001
7 | 4.001
8 | 3.898
9 | 2.706
10 | 1.151
11 | 0
12 | -1.036
13 | -2.498
14 | -3.085
15 | -2.637
16 | -1.345
17 | 0
18 | 0.88
19 | 2.331
20 | 2.949
21 | 3.309
22 | 3.347
23 | 3.494
24 | 3.527
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | S3PAS
VERSION: | SPAIN
HOUR | kWh
= | = | = | =
1 | 3.208
2 | 3.349
3 | 3.382
4 | 3.447
5 | 3.506
6 | 3.558
7 | 3.605
8 | 3.608
9 | 3.08
10 | 2.348
11 | 1.117
12 | 0.3
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0.143
18 | 0.91
19 | 1.281
20 | 1.543
21 | 1.81
22 | 1.995
23 | 2.154
24 | 2.311
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | S3PAS
VERSION: | SPAIN
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 0
-4 | 4
-3 | 3
-2 | 8
-1 | 5
0 | 18
1 | 20
2 | 14
3 | 19
4 | 21
5 | 27
6 | 30
7 | 33
8 | 46
9 | 61
10 | 71
11 | 116
12 | 127
13 | 157
14 | 160
15 | 207
16 | 224
17 | 255
18 | 315
19 | 347
20 | 352
21 | 366
22 | 349
23 | 357
24 | 341
25 | 392
26 | 399
27 | 403
28 | 440
29 | 396
30 | 395
31 | 360
32 | 337
33 | 306
34 | 306
35 | 256
36 | 217
37 | 166
38 | 138
39 | 97
40 | 57
41 | 31
42 | 10
43 | 1
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## TRNSYS
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
TRNSYS 13.1
Program Version Release Date:
Program Name for Tables and Charts: |  |  |  | TSYS
Results Submission Date:
Modeler Organization for Titles (long):
Building Research Establishment, U.K. Vrije Universiteit (VUB) Brussels, Belgium
Modeler Organization for Tables and Charts (short): |  |  |  | BEL-BRE
Model / Organization Indentifier Charts (short): |  |  |  | TSYS/BEL-BRE
BEL/UK
TSYS-BEL/BRE
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | MWh
600 | 4.872
610 | 4.97
620 | 5.073
630 | 5.624
640 | 3.043
650 | 4.171e-06
900 | 1.655
910 | 2.097
920 | 3.776
930 | 4.74
940 | 1.08
950 | 7.801e-06
960 | 3.373
195
200
210 | 6.554
215
220 | 7.297
230 | 10.84
240 | 6.076
250 | 5.764
270 | 5.047
280 | 5.279
290 | 5.132
300 | 5.124
310 | 5.61
320 | 4.348
395 | 4.855
400 | 7.166
410 | 8.936
420 | 7.697
430 | 6.5
440 | 5.098
800 | 5.94
810 | 2.567
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | MWh
600 | 6.492
610 | 4.601
620 | 3.901
630 | 2.416
640 | 6.246
650 | 5.119
900 | 2.485
910 | 1.326
920 | 2.418
930 | 1.416
940 | 2.383
950 | 0.5606
960 | 0.4113
195
200
210 | 0.6679
215
220 | 0.7368
230 | 1.04
240 | 1.114
250 | 2.684
270 | 8.764
280 | 5.761
290 | 6.699
300 | 5.721
310 | 3.727
320 | 5.956
395 | 0.01029
400 | 0.04468
410 | 0.06707
420 | 0.1575
430 | 0.6174
440 | 3.975
800 | 0.2073
810 | 1.191
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | KW | DATE | TIME
600 | 3.9306 | Jan-04 | 6
610 | 3.9222 | Jan-04 | 6
620 | 3.9222 | Jan-04 | 6
630 | 3.9222 | Jan-04 | 6
640 | 5.7222 | Jan-04 | 8
650 | 0
900 | 3.5167 | Jan-04 | 7
910 | 3.5361 | Jan-04 | 7
920 | 3.7083 | Jan-04 | 7
930 | 3.7444 | Jan-04 | 7
940 | 5.1222 | Jan-03 | 9
950 | 0
960 | 2.522 | Jan-04 | 8
195
200
210 | 2.9806 | Jan-04 | 5
215
220 | 3.3361 | Jan-04 | 6
230 | 4.8917 | Jan-04 | 6
240 | 3.1528 | Jan-04 | 6
250 | 3.3361 | Jan-04 | 6
270 | 3.3361 | Jan-04 | 6
280 | 3.3361 | Jan-04 | 6
290 | 3.3278 | Jan-04 | 6
300 | 3.3278 | Jan-04 | 6
310 | 3.3278 | Jan-04 | 6
320 | 3.3361 | Jan-04 | 6
395 | 2.2211 | Jan-04 | 8
400 | 3.3361 | Jan-04 | 6
410 | 4.1139 | Jan-04 | 6
420 | 3.9306 | Jan-04 | 6
430 | 3.9306 | Jan-04 | 6
440 | 3.9306 | Jan-04 | 6
800 | 3.7861 | Jan-04 | 7
810 | 3.6056 | Jan-04 | 7
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | kW | DATE | TIME
600 | 6.4861 | 2009-10-16 | 14
610 | 5.675 | 2009-11-25 | 14
620 | 4.275 | 2009-07-26 | 17
630 | 3.6083 | 2009-07-26 | 17
640 | 6.4417 | 2009-10-16 | 14
650 | 6.3778 | 2009-10-17 | 14
900 | 3.5667 | 2009-10-17 | 15
910 | 2.7917 | 2009-10-17 | 15
920 | 3.05 | 2009-07-26 | 17
930 | 2.4983 | 2009-07-26 | 17
940 | 3.5667 | 2009-10-17 | 15
950 | 2.6861 | 2009-09-02 | 15
960 | 1.378 | 2009-07-26 | 16
195
200
210 | 1.0678 | 2009-07-26 | 16
215
220 | 1.1789 | 2009-07-26 | 16
230 | 1.7078 | 2009-07-26 | 16
240 | 1.3614 | 2009-07-26 | 16
250 | 3.2278 | 2009-09-05 | 13
270 | 6.7639 | 2009-10-17 | 14
280 | 4.7861 | 2009-10-16 | 14
290 | 6.2028 | 2009-11-25 | 14
300 | 4.2778 | 2009-07-26 | 17
310 | 3.5889 | 2009-07-26 | 17
320 | 6.1778 | 2009-10-17 | 14
395 | 0.3625 | 2009-07-26 | 18
400 | 0.61333 | 2009-07-26 | 17
410 | 0.74306 | 2009-07-26 | 17
420 | 0.93778 | 2009-07-26 | 16
430 | 1.7983 | 2009-09-05 | 13
440 | 4.6861 | 2009-10-16 | 14
800 | 0.98278 | 2009-08-16 | 14
810 | 2.3436 | 2009-09-02 | 14
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | TEMP (C) | DATE | TIME
600FF | 65.25 | Oct-17 | 16
900FF | 42.46 | Oct-17 | 15
650FF | 63.74 | Oct-17 | 16
950FF | 35.67 | Sep-02 | 15
960 | 55.34 | Oct-17 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | TRNSYS
VERSION: |  | BEL/UK
CASE# | TMP (C) | DATE
600FF | -17.81 | Jan-04 | 7
900FF | -6.38 | Jan-04 | 8
650FF | -22.83 | Jan-04 | 7
950FF | -19.34 | Jan-04 | 7
960 | -2.82 | Jan-04 | 8
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | TRNSYS
VERSION: |  | BEL/UK
CASE# | TMP (C)
600FF | 24.49
900FF | 24.47
650FF | 17.99
950FF | 14.53
960 | 28.96
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
SURFACE | kWh/m2
= | = | = | =
NORTH | 367.4
EAST | 1101
WEST | 1012
SOUTH | 1522
HORZ. | 1832
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | kWh/m2
= | = | = | =
920WEST | 661.67
900SOUTH | 984.17
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
CASE# | kWh/m2
= | = | = | =
930WEST | 437.5
910SOUTH | 782
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3.05
8 | 20.69
9 | 38.94
10 | 54.67
11 | 66.08
12 | 71.92
13 | 72.42
14 | 66.53
15 | 55
16 | 38.94
17 | 20.52
18 | 3.05
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 2.99
8 | 20.17
9 | 37.92
10 | 53.17
11 | 64.39
12 | 69.89
13 | 70.75
14 | 65.69
15 | 55.03
16 | 39.61
17 | 21.42
18 | 3.28
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.17
6 | 27.01
7 | 63
8 | 71.22
9 | 187.72
10 | 314.17
11 | 404.44
12 | 443.61
13 | 452.5
14 | 400.56
15 | 316.94
16 | 188.89
17 | 86.03
18 | 69.78
19 | 17.61
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.17
6 | 27.01
7 | 63
8 | 71.22
9 | 85.58
10 | 98.03
11 | 109.14
12 | 113.06
13 | 235.17
14 | 453.89
15 | 652.5
16 | 762.78
17 | 568.33
18 | 158
19 | 26.6
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | TEMP (C)
= | = | = | =
1 | -12.02
2 | -13.5
3 | -14.7
4 | -15.65
5 | -16.47
6 | -17.14
7 | -17.7
8 | -17.59
9 | -13.46
10 | -7.099
11 | 3.657
12 | 13.49
13 | 21.77
14 | 28.26
15 | 32.09
16 | 32.16
17 | 25.71
18 | 18.84
19 | 13.1
20 | 8.408
21 | 4.387
22 | 0.9659
23 | -1.781
24 | -4.032
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | TEMP (C)
= | = | = | =
1 | -3.455
2 | -3.986
3 | -4.395
4 | -4.8
5 | -5.216
6 | -5.604
7 | -5.984
8 | -6.078
9 | -4.717
10 | -2.977
11 | 0.2494
12 | 2.539
13 | 4.382
14 | 5.853
15 | 6.614
16 | 6.333
17 | 4.204
18 | 2.869
19 | 2.107
20 | 1.581
21 | 1.047
22 | 0.5504
23 | 0.1517
24 | -0.238
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | TEMP (C)
= | = | = | =
1 | 22.69
2 | 21.33
3 | 20.41
4 | 19.61
5 | 19.16
6 | 19.6
7 | 21.68
8 | 23.47
9 | 26.38
10 | 30.35
11 | 34.82
12 | 39.38
13 | 43.48
14 | 46.14
15 | 47.4
16 | 47.33
17 | 46.71
18 | 45.28
19 | 33.1
20 | 30.49
21 | 28.55
22 | 26.66
23 | 25.55
24 | 24.26
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | TEMP (C)
= | = | = | =
1 | 25.28
2 | 24.47
3 | 23.87
4 | 23.26
5 | 22.87
6 | 23.06
7 | 24.38
8 | 27.21
9 | 27.98
10 | 29.11
11 | 30.31
12 | 31.53
13 | 32.55
14 | 33.15
15 | 33.37
16 | 33.38
17 | 33.37
18 | 33.16
19 | 30.43
20 | 29.61
21 | 28.89
22 | 27.93
23 | 27.42
24 | 26.59
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | kWh
= | = | = | =
1 | 3.7667
2 | 3.8667
3 | 3.9028
4 | 3.8944
5 | 3.9167
6 | 3.9306
7 | 3.9306
8 | 3.7528
9 | 2.4228
10 | 0.79667
11 | -0.034833
12 | -1.435
13 | -2.7203
14 | -3.1556
15 | -2.8444
16 | -1.7158
17 | 0
18 | 0.77306
19 | 2.3014
20 | 2.9667
21 | 3.2778
22 | 3.4611
23 | 3.5
24 | 3.4722
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | TRNSYS
VERSION: | BEL/UK
HOUR | kWh
= | = | = | =
1 | 3.0806
2 | 3.2028
3 | 3.2778
4 | 3.3306
5 | 3.4167
6 | 3.4694
7 | 3.5167
8 | 3.4639
9 | 2.8333
10 | 2.0561
11 | 0.79333
12 | 0.037278
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0.13494
18 | 0.76444
19 | 1.1986
20 | 1.4589
21 | 1.7008
22 | 1.9342
23 | 2.0922
24 | 2.2267
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | TRNSYS
VERSION: | BEL/UK
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 1
-6 | 3
-5 | 3
-4 | 6
-3 | 6
-2 | 12
-1 | 13
0 | 12
1 | 12
2 | 20
3 | 18
4 | 20
5 | 26
6 | 34
7 | 29
8 | 44
9 | 55
10 | 57
11 | 95
12 | 127
13 | 143
14 | 162
15 | 183
16 | 234
17 | 273
18 | 296
19 | 356
20 | 346
21 | 388
22 | 380
23 | 366
24 | 401
25 | 404
26 | 436
27 | 465
28 | 412
29 | 408
30 | 398
31 | 335
32 | 348
33 | 310
34 | 297
35 | 202
36 | 197
37 | 161
38 | 97
39 | 86
40 | 48
41 | 22
42 | 11
43 | 2
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =

## TASE
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2out.XLS
INSTRUCTIONS:
1) Use specified units.
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
Program Name and Version (with full build detail):
TASE
Program Version Release Date:
Program Name for Tables and Charts: |  |  |  | TASE
Results Submission Date:
Modeler Organization for Titles (long):
Tampere University, Finland
Modeler Organization for Tables and Charts (short): |  |  |  | FINLAND
Model / Organization Indentifier Charts (short): |  |  |  | TASE/FINLAND
FINLAND
TASE
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | MWh
600 | 5.362
610 | 5.383
620 | 5.728
630
640 | 3.309
650 | 0
900 | 2.041
910 | 2.22
920 | 4.3
930
940 | 1.323
950 | 0
960 | 2.816
195
200
210 | 6.967
215
220 | 7.437
230 | 10.964
240 | 6.234
250 | 5.738
270 | 5.489
280 | 5.841
290 | 5.509
300 | 5.786
310
320 | 4.84
395 | 4.839
400 | 7.326
410 | 9.085
420 | 7.863
430 | 6.51
440 | 5.642
800 | 5.861
810 | 2.962
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | MWh
600 | 6.778
610 | 5.506
620 | 4.351
630
640 | 6.508
650 | 5.456
900 | 2.599
910 | 1.767
920 | 2.613
930
940 | 2.516
950 | 0.771
960 | 0.786
195
200
210 | 0.641
215
220 | 0.683
230 | 0.985
240 | 1.045
250 | 3.38
270 | 8.714
280 | 6.257
290 | 7.431
300 | 5.781
310
320 | 5.663
395 | 0.011
400 | 0.044
410 | 0.065
420 | 0.143
430 | 0.875
440 | 4.684
800 | 0.325
810 | 1.624
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | KW | DATE | TIME
600 | 4.354 | JAN 04 | 2
610 | 4.354 | JAN 04 | 2
620 | 4.379 | JAN 04 | 2
630
640 | 6.954 | JAN 04 | 8
650 | 0
900 | 3.797 | JAN 04 | 7
910 | 3.801 | JAN 04 | 7
920 | 4.061 | JAN 04 | 7
930
940 | 6.428 | JAN 04 | 8
950 | 0
960 | 2.779 | JAN 04 | 8
195
200
210 | 3.325 | JAN 04 | 2
215
220 | 3.52 | JAN 04 | 2
230 | 5.107 | JAN 04 | 2
240 | 3.333 | JAN 04 | 8
250 | 3.525 | JAN 04 | 2
270 | 3.738 | JAN 04 | 2
280 | 3.759 | JAN 04 | 2
290 | 3.738 | JAN 04 | 2
300 | 3.77 | JAN 04 | 2
310
320 | 3.735 | JAN 04 | 3
395 | 2.27 | JAN 04 | 3
400 | 3.52 | JAN 04 | 2
410 | 4.314 | JAN 04 | 2
420 | 4.126 | JAN 04 | 2
430 | 4.137 | JAN 04 | 2
440 | 4.376 | JAN 04 | 2
800 | 3.939 | JAN 04 | 7
810 | 3.963 | JAN 04 | 7
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | kW | DATE | TIME
600 | 6.812 | OCT 17 | 14
610 | 6.146 | OCT 17 | 14
620 | 5.096 | JUL 26 | 16
630
640 | 6.771 | OCT 17 | 14
650 | 6.679 | OCT 17 | 14
900 | 3.457 | OCT 17 | 15
910 | 3.147 | OCT 17 | 15
920 | 3.505 | JUL 26 | 17
930
940 | 3.457 | OCT 17 | 15
950 | 2.867 | SEP 02 | 14
960 | 1.403 | JUL 26 | 16
195
200
210 | 1.142 | JUL 26 | 15
215
220 | 1.213 | JUL 26 | 15
230 | 1.749 | JUL 26 | 15
240 | 1.397 | JUL 26 | 15
250 | 4.912 | SEP 05 | 12
270 | 6.867 | OCT 16 | 14
280 | 5.236 | OCT 16 | 14
290 | 6.621 | NOV 25 | 14
300 | 4.929 | JUL 26 | 17
310
320 | 6.141 | OCT 16 | 14
395 | 0.345 | JUL 26 | 18
400 | 0.572 | JUL 26 | 17
410 | 0.71 | JUL 26 | 17
420 | 0.921 | JUL 26 | 15
430 | 2.578 | SEP 05 | 12
440 | 5.278 | OCT 17 | 14
800 | 1.358 | SEP 05 | 12
810 | 2.862 | SEP 02 | 14
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | TEMP (C) | DATE | TIME
600FF | 65.25 | OCT 15 | 16
900FF | 43.17 | SEP 15 | 15
650FF | 63.82 | OCT 16 | 16
950FF | 37.58 | SEP 15 | 16
960 | 48.92 | OCT 15 | 15
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM: |  | TASE
VERSION: |  | FINLAND
CASE# | TMP (C) | DATE | HR
600FF | -18.47 | JAN 08 | 9
900FF | -5.64 | JAN 08 | 9
650FF | -22.91 | JAN 02 | 23
950FF | -19.96 | JAN 07 | 22
960 | -0.39 | FEB 05 | 7
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM: |  | TASE
VERSION: |  | FINLAND
CASE# | TMP (C)
600FF | 24.22
900FF | 24.45
650FF | 18.36
950FF | 14.64
960 | 26.43
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
SURFACE | kWh/m2
= | = | = | =
NORTH | 453
EAST | 962
WEST | 1090
SOUTH | 1468
HORZ. | 1832
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | kWh/m2
= | = | = | =
920WEST | 706
900SOUTH | 914
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
CASE# | kWh/m2
= | = | = | =
930WEST
910SOUTH | 809
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3
8 | 20.68
9 | 38.94
10 | 54.56
11 | 65.99
12 | 71.74
13 | 72.3
14 | 66.38
15 | 54.8
16 | 38.84
17 | 20.46
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 3
8 | 20.15
9 | 37.9
10 | 53.15
11 | 64.4
12 | 69.95
13 | 71.16
14 | 66.02
15 | 55.16
16 | 39.73
17 | 21.6
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.2
6 | 25.7
7 | 62.1
8 | 107.47
9 | 232.33
10 | 349.16
11 | 430.22
12 | 459.85
13 | 462.28
14 | 404.57
15 | 319.26
16 | 193.61
17 | 132.3
18 | 76.6
19 | 18.05
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0.2
6 | 25.7
7 | 62.1
8 | 72
9 | 92.6
10 | 112.8
11 | 136.75
12 | 150.9
13 | 382.5
14 | 576.81
15 | 744.52
16 | 807.29
17 | 541.68
18 | 145.25
19 | 24.9
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | TEMP (C)
= | = | = | =
1 | -13.04
2 | -14.59
3 | -15.65
4 | -16.46
5 | -17.16
6 | -17.79
7 | -18.32
8 | -18.47
9 | -15.47
10 | -9.56
11 | 0.49
12 | 10.39
13 | 18.75
14 | 25.48
15 | 29.21
16 | 28.97
17 | 22.58
18 | 15.59
19 | 10.2
20 | 6.02
21 | 2.39
22 | -0.59
23 | -3.04
24 | -5.14
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | TEMP (C)
= | = | = | =
1 | -2.68
2 | -3.33
3 | -3.72
4 | -4.1
5 | -4.51
6 | -4.93
7 | -5.34
8 | -5.64
9 | -4.59
10 | -2.64
11 | 0.75
12 | 3.26
13 | 4.99
14 | 6.51
15 | 7.11
16 | 6.68
17 | 4.24
18 | 2.45
19 | 1.71
20 | 1.32
21 | 0.82
22 | 0.42
23 | 0.05
24 | -0.34
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | TEMP (C)
= | = | = | =
1 | 22.26
2 | 21.11
3 | 20.28
4 | 19.49
5 | 19.14
6 | 19.81
7 | 22.49
8 | 24.81
9 | 28.04
10 | 32.11
11 | 36.54
12 | 41.15
13 | 45.03
14 | 47.65
15 | 49.04
16 | 49.28
17 | 48.73
18 | 46.58
19 | 34.91
20 | 30.69
21 | 28.81
22 | 26.66
23 | 25.69
24 | 24.1
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | TEMP (C)
= | = | = | =
1 | 24.53
2 | 23.8
3 | 23.23
4 | 22.6
5 | 22.27
6 | 22.67
7 | 24.55
8 | 27.57
9 | 29.42
10 | 30.68
11 | 31.91
12 | 33.27
13 | 34.27
14 | 34.9
15 | 35.19
16 | 35.28
17 | 35.3
18 | 34.71
19 | 30.74
20 | 29.38
21 | 27.64
22 | 27.46
23 | 27.1
24 | 26.02
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | kWh
= | = | = | =
1 | 4.225
2 | 4.354
3 | 4.321
4 | 4.308
5 | 4.303
6 | 4.307
7 | 4.307
8 | 4.167
9 | 2.912
10 | 1.466
11 | 0
12 | -0.424
13 | -2.364
14 | -2.759
15 | -2.431
16 | -1.14
17 | 0
18 | 1.292
19 | 2.445
20 | 2.941
21 | 3.405
22 | 3.594
23 | 3.696
24 | 3.769
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM: | TASE
VERSION: | FINLAND
HOUR | kWh
= | = | = | =
1 | 3.4
2 | 3.547
3 | 3.573
4 | 3.629
5 | 3.687
6 | 3.747
7 | 3.797
8 | 3.794
9 | 3.168
10 | 2.449
11 | 1.293
12 | 0.619
13 | 0.136
14 | 0
15 | 0
16 | 0.088
17 | 1.198
18 | 1.602
19 | 1.805
20 | 1.943
21 | 2.121
22 | 2.227
23 | 2.338
24 | 2.458
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM: | TASE
VERSION: | FINLAND
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 2
-5 | 4
-4 | 5
-3 | 7
-2 | 10
-1 | 18
0 | 20
1 | 12
2 | 16
3 | 25
4 | 24
5 | 27
6 | 35
7 | 45
8 | 59
9 | 73
10 | 118
11 | 134
12 | 138
13 | 173
14 | 183
15 | 234
16 | 274
17 | 298
18 | 342
19 | 352
20 | 331
21 | 334
22 | 343
23 | 349
24 | 338
25 | 404
26 | 393
27 | 396
28 | 411
29 | 391
30 | 362
31 | 342
32 | 322
33 | 291
34 | 266
35 | 210
36 | 169
37 | 151
38 | 132
39 | 85
40 | 59
41 | 32
42 | 20
43 | 1
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =