## Read Me
ASHRAE Standard 140-2017
Informative Annex B16, Section B16.7.2 Example Results
for
Section 5.5, Constant Volume and Variable Air Volume Systems
AE301 through AE445
This spreadsheet contains the Informative Annex B16, Section B16.7.2 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results; see instructions on page.
"Program List" : Documentation of simulation programs used to produce informative Annex B16, Section B16.7.2 example results
"Table List": List of Informative Annex B16, Section B16.7.2 Tables in workbook with locations.
"Figure List": List of Informative Annex B16, Section B16.7.2 Figures in workbook with locations.
"Tables 1" through "Delta Tables 2" : Formatted result tables
"Fig B16.7.2-1 TotalCoil H+C" through "Fig B16.7.2-35 VAV dEcono" : Figures
"Detailed Location Results": Tool to compare detailed results
"Aggregate Results Final" : Unformatted results for use in tables and charts.
"Delta Results Final": Unformatted delta results for use in tables and charts.
Individual Example Results Worksheets as follows:
QAS: QAS model results set, 12Nov2014. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
DEEAP: DEEAP model results set, 10Dec2012. Submitted by AAON, Inc., Tulsa, Oklahoma, United States.
DeST: DeST 2 model results set, 21Nov2013. Submitted by Tsinghua University, Beijing, China.
DOE22: DOE-2.2 model results set, 10Mar2015. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
EPlus: EnergyPlus 8.2 model results set, 15Jan2015. Submitted by GARD Analytics, Arlington Heights, Illinois, United States.
IES-VE: IES-VE model results set, 20Feb2015. Submitted by Integrated Environmental Solutions, Glasgow, United Kingdom.
TRNSYS: TRNSYS-17 with TESS libraries model results set, 18Nov2014. Submitted by TESS, Madison, Wisconsin, United States.

## Adding Results
Output spreadsheet for Airside HVAC Equipment Diagnostic Tests: AE101 through AE445
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell C50 of Sec5-5out.xlsx is in C50 of Sheet "YourData"
Check that the summary results for Case AE101 start at YourData!C61.
Data should flow to "YourData" cells as tabulated below. Your data will then appear in the rightmost column
of each table on sheets "Tables 1" to "Delta Tables 2". Charts are also updated with "your data" automatically.
Complete the program information block on "YourData", which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT SHEETS AND NEW RESULTS
Gives locations for data in "YourData" sheet and in participant sheets.
Program Information Block - complete blue boxes to identify program and organization for report
| Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
| I5 | [5 empty] | O5
| Program Version Release Date: |  |  |  | I6 |  | Modeler Organization for Tables and Charts (short): |  |  |  | O6
| Program Name for Tables and Charts (short): |  |  |  | I7
| Results Submission Date: |  |  |  | I8 |  | Model / Organization Indentifier for Charts (short): |  |  |  | O8 | defaults to short program name / short organization name
Results
| Software: | C50
| Version: | C51
| Date: | C52
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | C61 | D61 | E61 | F61 | G61 | H61 | I61 | J61 | [5 empty] | AE101 | Dry bulb temperature (°C) | S61 | T61 | U61 | V61 | W61 | X61 | Y61
| AE103 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | [6 empty] | Humidity ratio (g/gda) | S62 | T62 | U62 | V62 | W62 | X62 | Y62
| AE104 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | [6 empty] | Specific volume (L/kgda) | S63 | T63 | U63 | V63 | W63 | X63 | Y63
[16 empty] | Enthalpy (J/gda) | S64 | T64 | U64 | V64 | W64 | X64 | Y64
[16 empty] | Mass flow rate (kgda/s) | S65 | T65 | U65 | V65 | W65 | #N/A | Y65
[15 empty] | AE103 | Dry bulb temperature (°C) | S66 | T66 | U66 | V66 | W66 | X66 | Y66
[16 empty] | Humidity ratio (g/gda) | S67 | T67 | U67 | V67 | W67 | X67 | Y67
[16 empty] | Specific volume (L/kgda) | S68 | T68 | U68 | V68 | W68 | X68 | Y68
[16 empty] | Enthalpy (J/gda) | S69 | T69 | U69 | V69 | W69 | X69 | Y69
[16 empty] | Mass flow rate (kgda/s) | S70 | T70 | U70 | V70 | W70 | #N/A | Y70
[15 empty] | AE104 | Dry bulb temperature (°C) | S71 | T71 | U71 | V71 | W71 | X71 | Y71
[16 empty] | Humidity ratio (g/gda) | S72 | T72 | U72 | V72 | W72 | X72 | Y72
[16 empty] | Specific volume (L/kgda) | S73 | T73 | U73 | V73 | W73 | X73 | Y73
[16 empty] | Enthalpy (J/gda) | S74 | T74 | U74 | V74 | W74 | X74 | Y74
[16 empty] | Mass flow rate (kgda/s) | S75 | T75 | U75 | V75 | W75 | #N/A | Y75
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | [5 empty] | AE201 | Dry bulb temperature (°C) | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89
| AE203 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | [6 empty] | Humidity ratio (g/gda) | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90
| AE204 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | [6 empty] | Specific volume (L/kgda) | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91
| AE205 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | [6 empty] | Enthalpy (J/gda) | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92
| AE206 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | [6 empty] | Mass flow rate (kgda/s) | S93 | T93 | U93 | V93 | W93 | #N/A | Y93 | Z93
| AE226 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | [5 empty] | AE203 | Dry bulb temperature (°C) | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94
| AE245 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | [6 empty] | Humidity ratio (g/gda) | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95
[16 empty] | Specific volume (L/kgda) | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96
[16 empty] | Enthalpy (J/gda) | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97
[16 empty] | Mass flow rate (kgda/s) | S98 | T98 | U98 | V98 | W98 | #N/A | Y98 | Z98
[15 empty] | AE204 | Dry bulb temperature (°C) | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99
[16 empty] | Humidity ratio (g/gda) | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100
[16 empty] | Specific volume (L/kgda) | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101
[16 empty] | Enthalpy (J/gda) | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102
[16 empty] | Mass flow rate (kgda/s) | S103 | T103 | U103 | V103 | W103 | #N/A | Y103 | Z103
[15 empty] | AE205 | Dry bulb temperature (°C) | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104
[16 empty] | Humidity ratio (g/gda) | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105
[16 empty] | Specific volume (L/kgda) | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106
[16 empty] | Enthalpy (J/gda) | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107
[16 empty] | Mass flow rate (kgda/s) | S108 | T108 | U108 | V108 | W108 | #N/A | Y108 | Z108
[15 empty] | AE206 | Dry bulb temperature (°C) | S109 | T109 | U109 | V109 | W109 | X109 | Y109 | Z109
[16 empty] | Humidity ratio (g/gda) | S110 | T110 | U110 | V110 | W110 | X110 | Y110 | Z110
[16 empty] | Specific volume (L/kgda) | S111 | T111 | U111 | V111 | W111 | X111 | Y111 | Z111
[16 empty] | Enthalpy (J/gda) | S112 | T112 | U112 | V112 | W112 | X112 | Y112 | Z112
[16 empty] | Mass flow rate (kgda/s) | S113 | T113 | U113 | V113 | W113 | #N/A | Y113 | Z113
[15 empty] | AE226 | Dry bulb temperature (°C) | S114 | T114 | U114 | V114 | W114 | X114 | Y114 | Z114
[16 empty] | Humidity ratio (g/gda) | S115 | T115 | U115 | V115 | W115 | X115 | Y115 | Z115
[16 empty] | Specific volume (L/kgda) | S116 | T116 | U116 | V116 | W116 | X116 | Y116 | Z116
[16 empty] | Enthalpy (J/gda) | S117 | T117 | U117 | V117 | W117 | X117 | Y117 | Z117
[16 empty] | Mass flow rate (kgda/s) | S118 | T118 | U118 | V118 | W118 | #N/A | Y118 | Z118
[15 empty] | AE245 | Dry bulb temperature (°C) | S119 | T119 | U119 | V119 | W119 | X119 | Y119 | Z119
[16 empty] | Humidity ratio (g/gda) | S120 | T120 | U120 | V120 | W120 | X120 | Y120 | Z120
[16 empty] | Specific volume (L/kgda) | S121 | T121 | U121 | V121 | W121 | X121 | Y121 | Z121
[16 empty] | Enthalpy (J/gda) | S122 | T122 | U122 | V122 | W122 | X122 | Y122 | Z122
[16 empty] | Mass flow rate (kgda/s) | S123 | T123 | U123 | V123 | W123 | #N/A | Y123 | Z123
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | C137 | D137 | E137 | F137 | G137 | H137 | I137 | J137 | K137 | L137 | M137 | N137 | O137 | AE301 | Dry bulb temperature (°C) | S137 | T137 | U137 | V137 | W137 | X137 | Y137 | Z137 | AA137 | AB137 | AC137
| AE303 | C138 | D138 | E138 | F138 | G138 | H138 | I138 | J138 | K138 | L138 | M138 | N138 | O138 |  | Humidity ratio (g/gda) | S138 | T138 | U138 | V138 | W138 | X138 | Y138 | Z138 | AA138 | AB138 | AC138
| AE304 | C139 | D139 | E139 | F139 | G139 | H139 | I139 | J139 | K139 | L139 | M139 | N139 | O139 |  | Specific volume (L/kgda) | S139 | T139 | U139 | V139 | W139 | X139 | Y139 | Z139 | AA139 | AB139 | AC139
| AE305 | C140 | D140 | E140 | F140 | G140 | H140 | I140 | J140 | K140 | L140 | M140 | N140 | O140 |  | Enthalpy (J/gda) | S140 | T140 | U140 | V140 | W140 | X140 | Y140 | Z140 | AA140 | AB140 | AC140
| AE306 | C141 | D141 | E141 | F141 | G141 | H141 | I141 | J141 | K141 | L141 | M141 | N141 | O141 |  | Mass flow rate (kgda/s) | S141 | T141 | U141 | V141 | W141 | X141 | Y141 | #N/A | #N/A | AB141 | AC141
| AE326 | C142 | D142 | E142 | F142 | G142 | H142 | I142 | J142 | K142 | L142 | M142 | N142 | O142 | AE303 | Dry bulb temperature (°C) | S142 | T142 | U142 | V142 | W142 | X142 | Y142 | Z142 | AA142 | AB142 | AC142
| AE345 | C143 | D143 | E143 | F143 | G143 | H143 | I143 | J143 | K143 | L143 | M143 | N143 | O143 |  | Humidity ratio (g/gda) | S143 | T143 | U143 | V143 | W143 | X143 | Y143 | Z143 | AA143 | AB143 | AC143
[16 empty] | Specific volume (L/kgda) | S144 | T144 | U144 | V144 | W144 | X144 | Y144 | Z144 | AA144 | AB144 | AC144
[16 empty] | Enthalpy (J/gda) | S145 | T145 | U145 | V145 | W145 | X145 | Y145 | Z145 | AA145 | AB145 | AC145
[16 empty] | Mass flow rate (kgda/s) | S146 | T146 | U146 | V146 | W146 | X146 | Y146 | #N/A | #N/A | AB146 | AC146
[15 empty] | AE304 | Dry bulb temperature (°C) | S147 | T147 | U147 | V147 | W147 | X147 | Y147 | Z147 | AA147 | AB147 | AC147
[16 empty] | Humidity ratio (g/gda) | S148 | T148 | U148 | V148 | W148 | X148 | Y148 | Z148 | AA148 | AB148 | AC148
[16 empty] | Specific volume (L/kgda) | S149 | T149 | U149 | V149 | W149 | X149 | Y149 | Z149 | AA149 | AB149 | AC149
[16 empty] | Enthalpy (J/gda) | S150 | T150 | U150 | V150 | W150 | X150 | Y150 | Z150 | AA150 | AB150 | AC150
[16 empty] | Mass flow rate (kgda/s) | S151 | T151 | U151 | V151 | W151 | X151 | Y151 | #N/A | #N/A | AB151 | AC151
[15 empty] | AE305 | Dry bulb temperature (°C) | S152 | T152 | U152 | V152 | W152 | X152 | Y152 | Z152 | AA152 | AB152 | AC152
[16 empty] | Humidity ratio (g/gda) | S153 | T153 | U153 | V153 | W153 | X153 | Y153 | Z153 | AA153 | AB153 | AC153
[16 empty] | Specific volume (L/kgda) | S154 | T154 | U154 | V154 | W154 | X154 | Y154 | Z154 | AA154 | AB154 | AC154
[16 empty] | Enthalpy (J/gda) | S155 | T155 | U155 | V155 | W155 | X155 | Y155 | Z155 | AA155 | AB155 | AC155
[16 empty] | Mass flow rate (kgda/s) | S156 | T156 | U156 | V156 | W156 | X156 | Y156 | #N/A | #N/A | AB156 | AC156
[15 empty] | AE306 | Dry bulb temperature (°C) | S157 | T157 | U157 | V157 | W157 | X157 | Y157 | Z157 | AA157 | AB157 | AC157
[16 empty] | Humidity ratio (g/gda) | S158 | T158 | U158 | V158 | W158 | X158 | Y158 | Z158 | AA158 | AB158 | AC158
[16 empty] | Specific volume (L/kgda) | S159 | T159 | U159 | V159 | W159 | X159 | Y159 | Z159 | AA159 | AB159 | AC159
[16 empty] | Enthalpy (J/gda) | S160 | T160 | U160 | V160 | W160 | X160 | Y160 | Z160 | AA160 | AB160 | AC160
[16 empty] | Mass flow rate (kgda/s) | S161 | T161 | U161 | V161 | W161 | X161 | Y161 | #N/A | #N/A | AB161 | AC161
[15 empty] | AE326 | Dry bulb temperature (°C) | S162 | T162 | U162 | V162 | W162 | X162 | Y162 | Z162 | AA162 | AB162 | AC162
[16 empty] | Humidity ratio (g/gda) | S163 | T163 | U163 | V163 | W163 | X163 | Y163 | Z163 | AA163 | AB163 | AC163
[16 empty] | Specific volume (L/kgda) | S164 | T164 | U164 | V164 | W164 | X164 | Y164 | Z164 | AA164 | AB164 | AC164
[16 empty] | Enthalpy (J/gda) | S165 | T165 | U165 | V165 | W165 | X165 | Y165 | Z165 | AA165 | AB165 | AC165
[16 empty] | Mass flow rate (kgda/s) | S166 | T166 | U166 | V166 | W166 | X166 | Y166 | #N/A | #N/A | AB166 | AC166
[15 empty] | AE345 | Dry bulb temperature (°C) | S167 | T167 | U167 | V167 | W167 | X167 | Y167 | Z167 | AA167 | AB167 | AC167
[16 empty] | Humidity ratio (g/gda) | S168 | T168 | U168 | V168 | W168 | X168 | Y168 | Z168 | AA168 | AB168 | AC168
[16 empty] | Specific volume (L/kgda) | S169 | T169 | U169 | V169 | W169 | X169 | Y169 | Z169 | AA169 | AB169 | AC169
[16 empty] | Enthalpy (J/gda) | S170 | T170 | U170 | V170 | W170 | X170 | Y170 | Z170 | AA170 | AB170 | AC170
[16 empty] | Mass flow rate (kgda/s) | S171 | T171 | U171 | V171 | W171 | X171 | Y171 | #N/A | #N/A | AB171 | AC171
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | C164 | D164 | E164 | F164 | G164 | H164 | I164 | J164 | K164 | L164 | M164 | N164 | O164 | AE401 | Dry bulb temperature (°C) | S185 | T185 | U185 | V185 | W185 | X185 | Y185 | Z185 | AA185 | AB185 | AC185
| AE403 | C165 | D165 | E165 | F165 | G165 | H165 | I165 | J165 | K165 | L165 | M165 | N165 | O165 |  | Humidity ratio (g/gda) | S186 | T186 | U186 | V186 | W186 | X186 | Y186 | Z186 | AA186 | AB186 | AC186
| AE404 | C166 | D166 | E166 | F166 | G166 | H166 | I166 | J166 | K166 | L166 | M166 | N166 | O166 |  | Specific volume (L/kgda) | S187 | T187 | U187 | V187 | W187 | X187 | Y187 | Z187 | AA187 | AB187 | AC187
| AE405 | C167 | D167 | E167 | F167 | G167 | H167 | I167 | J167 | K167 | L167 | M167 | N167 | O167 |  | Enthalpy (J/gda) | S188 | T188 | U188 | V188 | W188 | X188 | Y188 | Z188 | AA188 | AB188 | AC188
| AE406 | C168 | D168 | E168 | F168 | G168 | H168 | I168 | J168 | K168 | L168 | M168 | N168 | O168 |  | Mass flow rate (kgda/s) | S189 | T189 | U189 | V189 | W189 | X189 | Y189 | #N/A | #N/A | AB189 | AC189
| AE426 | C169 | D169 | E169 | F169 | G169 | H169 | I169 | J169 | K169 | L169 | M169 | N169 | O169 | AE403 | Dry bulb temperature (°C) | S190 | T190 | U190 | V190 | W190 | X190 | Y190 | Z190 | AA190 | AB190 | AC190
| AE445 | C170 | D170 | E170 | F170 | G170 | H170 | I170 | J170 | K170 | L170 | M170 | N170 | O170 |  | Humidity ratio (g/gda) | S191 | T191 | U191 | V191 | W191 | X191 | Y191 | Z191 | AA191 | AB191 | AC191
[16 empty] | Specific volume (L/kgda) | S192 | T192 | U192 | V192 | W192 | X192 | Y192 | Z192 | AA192 | AB192 | AC192
[16 empty] | Enthalpy (J/gda) | S193 | T193 | U193 | V193 | W193 | X193 | Y193 | Z193 | AA193 | AB193 | AC193
[16 empty] | Mass flow rate (kgda/s) | S194 | T194 | U194 | V194 | W194 | X194 | Y194 | #N/A | #N/A | AB194 | AC194
[15 empty] | AE404 | Dry bulb temperature (°C) | S195 | T195 | U195 | V195 | W195 | X195 | Y195 | Z195 | AA195 | AB195 | AC195
[16 empty] | Humidity ratio (g/gda) | S196 | T196 | U196 | V196 | W196 | X196 | Y196 | Z196 | AA196 | AB196 | AC196
[16 empty] | Specific volume (L/kgda) | S197 | T197 | U197 | V197 | W197 | X197 | Y197 | Z197 | AA197 | AB197 | AC197
[16 empty] | Enthalpy (J/gda) | S198 | T198 | U198 | V198 | W198 | X198 | Y198 | Z198 | AA198 | AB198 | AC198
[16 empty] | Mass flow rate (kgda/s) | S199 | T199 | U199 | V199 | W199 | X199 | Y199 | #N/A | #N/A | AB199 | AC199
[15 empty] | AE405 | Dry bulb temperature (°C) | S200 | T200 | U200 | V200 | W200 | X200 | Y200 | Z200 | AA200 | AB200 | AC200
[16 empty] | Humidity ratio (g/gda) | S201 | T201 | U201 | V201 | W201 | X201 | Y201 | Z201 | AA201 | AB201 | AC201
[16 empty] | Specific volume (L/kgda) | S202 | T202 | U202 | V202 | W202 | X202 | Y202 | Z202 | AA202 | AB202 | AC202
[16 empty] | Enthalpy (J/gda) | S203 | T203 | U203 | V203 | W203 | X203 | Y203 | Z203 | AA203 | AB203 | AC203
[16 empty] | Mass flow rate (kgda/s) | S204 | T204 | U204 | V204 | W204 | X204 | Y204 | #N/A | #N/A | AB204 | AC204
[15 empty] | AE406 | Dry bulb temperature (°C) | S205 | T205 | U205 | V205 | W205 | X205 | Y205 | Z205 | AA205 | AB205 | AC205
[16 empty] | Humidity ratio (g/gda) | S206 | T206 | U206 | V206 | W206 | X206 | Y206 | Z206 | AA206 | AB206 | AC206
[16 empty] | Specific volume (L/kgda) | S207 | T207 | U207 | V207 | W207 | X207 | Y207 | Z207 | AA207 | AB207 | AC207
[16 empty] | Enthalpy (J/gda) | S208 | T208 | U208 | V208 | W208 | X208 | Y208 | Z208 | AA208 | AB208 | AC208
[16 empty] | Mass flow rate (kgda/s) | S209 | T209 | U209 | V209 | W209 | X209 | Y209 | #N/A | #N/A | AB209 | AC209
[15 empty] | AE426 | Dry bulb temperature (°C) | S210 | T210 | U210 | V210 | W210 | X210 | Y210 | Z210 | AA210 | AB210 | AC210
[16 empty] | Humidity ratio (g/gda) | S211 | T211 | U211 | V211 | W211 | X211 | Y211 | Z211 | AA211 | AB211 | AC211
[16 empty] | Specific volume (L/kgda) | S212 | T212 | U212 | V212 | W212 | X212 | Y212 | Z212 | AA212 | AB212 | AC212
[16 empty] | Enthalpy (J/gda) | S213 | T213 | U213 | V213 | W213 | X213 | Y213 | Z213 | AA213 | AB213 | AC213
[16 empty] | Mass flow rate (kgda/s) | S214 | T214 | U214 | V214 | W214 | X214 | Y214 | #N/A | #N/A | AB214 | AC214
[15 empty] | AE445 | Dry bulb temperature (°C) | S215 | T215 | U215 | V215 | W215 | X215 | Y215 | Z215 | AA215 | AB215 | AC215
[16 empty] | Humidity ratio (g/gda) | S216 | T216 | U216 | V216 | W216 | X216 | Y216 | Z216 | AA216 | AB216 | AC216
[16 empty] | Specific volume (L/kgda) | S217 | T217 | U217 | V217 | W217 | X217 | Y217 | Z217 | AA217 | AB217 | AC217
[16 empty] | Enthalpy (J/gda) | S218 | T218 | U218 | V218 | W218 | X218 | Y218 | Z218 | AA218 | AB218 | AC218
[16 empty] | Mass flow rate (kgda/s) | S219 | T219 | U219 | V219 | W219 | X219 | Y219 | #N/A | #N/A | AB219 | AC219

## YourData
Output spreadsheet for Airside Mechanical Equipment Diagnostic Tests: AE101 through AE445
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | Carrier Hourly Analysis Program 6.0.0.888 | [5 empty] | Carrier Global Corporation
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2023-02-14 |  | Modeler Organization for Tables and Charts (short): |  |  |  | Carrier
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | HAP
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2023-10-21 |  | Model / Organization Indentifier for Charts (short): |  |  |  | HAP/Carrier | defaults to short program name / short organization name
© Carrier 2023. All rights reserved.
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | Carrier HAP
| Version: | 6.0.0.888
| Date: | 2023-02-14
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 | 0 | 0.5861 | 8.452 | 0 | 0 | 0 | 29.95 | [6 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4489 | 29.6284 | 5.0343 | 29.6284 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.5861 | 0 | 0.76511 | 0 | 0.76511 | 31.346 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0022891 | 0.0022891
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.48 | 2.2377 | 5.7177 | 94.51 | [7 empty] | Specific volume (L/kgda) | 692.0128 | 788.5312 | 860.0545 | 790.194 | 860.0545 | 836.7683 | 836.7683
[17 empty] | Enthalpy (J/gda) | -28.5066 | 8.5163 | 33.8932 | 9.1063 | 33.8932 | 27.028 | 27.028
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
[16 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7287 | 19.0955 | 19.0955 | 19.0955 | 23.3333 | 23.3333
[17 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0049602 | 0.0049602
[17 empty] | Specific volume (L/kgda) | 821.6589 | 838.3516 | 833.6932 | 833.6932 | 833.6932 | 846.6945 | 846.6945
[17 empty] | Enthalpy (J/gda) | 22.9959 | 31.7097 | 30.0557 | 30.0557 | 30.0557 | 36.0667 | 36.0667
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
[16 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.9003 | 15.5085 | 15.5085 | 15.5085 | 23.8902 | 23.8902
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012972 | 0.010397 | 0.010397 | 0.010397 | 0.011072 | 0.011072
[17 empty] | Specific volume (L/kgda) | 873.0237 | 862.0467 | 831.4964 | 831.4964 | 831.4964 | 856.5545 | 856.5545
[17 empty] | Enthalpy (J/gda) | 69.814 | 58.063 | 41.8848 | 41.8848 | 41.8848 | 52.188 | 52.188
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3818 | 0 | 0 | 0 | 30.7878 | [6 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.639 | 29.0288 | 4.639 | 29.614 | 21.0967 | 21.0967 | 21.3955
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.82766 | 9.0949e-16 | 0.82766 | 32.4016 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0022891 | 0.0022891 | 0.0022891
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5482 | 2.273 | 5.8212 | 96.8838 | [7 empty] | Specific volume (L/kgda) | 692.013 | 789.0711 | 858.3515 | 789.0711 | 860.0137 | 836.727 | 836.727 | 837.5768
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9122 | 2.2737e-16 | 1.9122 | 44.0703 | [7 empty] | Enthalpy (J/gda) | -28.5066 | 8.7079 | 33.2889 | 8.7079 | 33.8787 | 27.0136 | 27.0136 | 27.3151
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.6935 | 1.5535 | 3.247 | 86.2264 | [7 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5406 | 2.3442 | 3.8848 | 95.7023 | [6 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9621 | 18.5655 | 18.5655 | 19.1478 | 23.3856 | 23.3856 | 23.683
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2048 | 4.5475e-16 | 2.2048 | 33.9774 | [7 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0049602 | 0.0049602 | 0.0049602
[17 empty] | Specific volume (L/kgda) | 821.6592 | 839.0176 | 832.1808 | 832.1808 | 833.8419 | 846.8437 | 846.8437 | 847.693
[17 empty] | Enthalpy (J/gda) | 22.9959 | 31.946 | 29.5187 | 29.5187 | 30.1085 | 36.1195 | 36.1195 | 36.421
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.1021 | 14.9397 | 14.9397 | 15.5154 | 23.899 | 23.899 | 24.1937
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012889 | 0.010273 | 0.010273 | 0.010273 | 0.010948 | 0.010948 | 0.010948
[17 empty] | Specific volume (L/kgda) | 873.0237 | 862.518 | 829.6955 | 829.6955 | 831.3537 | 856.412 | 856.412 | 857.2616
[17 empty] | Enthalpy (J/gda) | 69.814 | 58.0604 | 40.9888 | 40.9888 | 41.5784 | 51.8815 | 51.8815 | 52.1836
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0602 | 18.5389 | 18.5389 | 19.1196 | 23.3454 | 23.3454 | 23.6419
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0058322 | 0.0058322 | 0.0058322 | 0.0058322 | 0.0065078 | 0.0065078 | 0.0065078
[17 empty] | Specific volume (L/kgda) | 850.518 | 849.9509 | 834.1613 | 834.1613 | 835.8218 | 848.819 | 848.819 | 849.668
[17 empty] | Enthalpy (J/gda) | 36.4347 | 39.0236 | 33.4157 | 33.4157 | 34.0055 | 40.0165 | 40.0165 | 40.3181
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4198 | 18.5807 | 18.5807 | 19.1553 | 23.3374 | 23.3374 | 23.6309
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.013336 | 0.011545 | 0.011545 | 0.011545 | 0.012221 | 0.012221 | 0.012221
[17 empty] | Specific volume (L/kgda) | 860.0491 | 858.2558 | 841.8723 | 841.8723 | 843.5306 | 856.5118 | 856.5118 | 857.3596
[17 empty] | Enthalpy (J/gda) | 62.7052 | 57.4654 | 47.9431 | 47.9431 | 48.5328 | 54.5439 | 54.5439 | 54.8455
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 18.6083 | 18.6083 | 19.1816 | 23.3538 | 23.3538 | 23.6465
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.012863 | 0.012863 | 0.012863 | 0.013538 | 0.013538 | 0.013538
[17 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 843.7033 | 843.7033 | 845.3611 | 858.3386 | 858.3386 | 859.1862
[17 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 51.3124 | 51.3124 | 51.9022 | 57.9133 | 57.9133 | 58.2148
[17 empty] | Mass flow rate (kgda/s) | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 18.5181 | 18.5181 | 19.1002 | 23.3365 | 23.3365 | 23.6338
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051566 | 0.0051566 | 0.0051566
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 832.3066 | 832.3066 | 833.9676 | 846.9687 | 846.9687 | 847.818
[17 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 29.9688 | 29.9688 | 30.5586 | 36.5696 | 36.5696 | 36.8711
[17 empty] | Mass flow rate (kgda/s) | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 3.5822 | 0 | 0 | 0 | 23.8892 | 7.501 | 8.1235 |  | AE301 | Dry bulb temperature (°C) | -29 | 2.4103 | 7.2222 | 7.2222 | 7.8075 | 29.6391 | 28.0732 | 21.1199 | 22.2336 | 21.6769 | 21.9691
| AE303 | 0 | 1.4654 | 0 | 0 | 2.3446 | 0 | 0 | 6.4549 | 0 | 6.4549 | 33.4715 | 2.171 | 2.3444 |  |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0021725 | 0.0023652 | 0.0022689 | 0.0022689
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.0831 | 6.9711 | 17.0541 | 94.7543 | 0.93938 | 1.451 |  |  | Specific volume (L/kgda) | 692.013 | 782.5942 | 796.2601 | 796.2601 | 797.9222 | 859.9241 | 855.477 | 836.6368 | 840.0622 | 838.3495 | 839.1805
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.1982 | 0 | 9.1982 | 64.9185 | 2.1923 | 2.3735 |  |  | Enthalpy (J/gda) | -28.5066 | 6.1697 | 11.0183 | 11.0183 | 11.608 | 33.6059 | 32.0281 | 26.7408 | 28.3541 | 27.5475 | 27.8423
| AE306 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 0 | 8.6909 | 6.0483 | 14.7392 | 95.3924 | 6.603 | 7.0813 |  |  | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
| AE326 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 0 | 8.1485 | 12.6386 | 20.7871 | 99.8848 | 6.6056 | 7.0847 |  | AE303 | Dry bulb temperature (°C) | 15.5 | 20.842 | 20.842 | 12.1941 | 12.7778 | 19.0797 | 18.6109 | 23.3333 | 24.4444 | 23.8889 | 24.1808
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.5096 | -3.638e-15 | 9.5096 | 50.9986 | 2.1841 | 2.3628 |  |  | Humidity ratio (g/gda) | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334
[17 empty] | Specific volume (L/kgda) | 821.6592 | 836.8655 | 836.8655 | 812.2486 | 813.9103 | 831.8491 | 830.5147 | 843.9573 | 847.1201 | 845.5387 | 846.3695
[17 empty] | Enthalpy (J/gda) | 22.9959 | 28.3928 | 28.3928 | 19.6559 | 20.2456 | 26.6124 | 26.1388 | 30.9098 | 32.0324 | 31.4711 | 31.766
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5745 | 25.5745 | 12.1999 | 12.7778 | 15.4775 | 16.3522 | 23.89 | 25.002 | 24.4461 | 24.7346
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012082 | 0.012082 | 0.0083798 | 0.0083798 | 0.0083798 | 0.0083798 | 0.0090551 | 0.0092474 | 0.0091512 | 0.0091512
[17 empty] | Specific volume (L/kgda) | 873.0237 | 862.786 | 862.786 | 819.3443 | 821.0038 | 828.7558 | 831.2673 | 853.8247 | 857.2823 | 855.5535 | 856.3831
[17 empty] | Enthalpy (J/gda) | 69.814 | 56.4896 | 56.4896 | 33.4063 | 33.996 | 36.7509 | 37.6434 | 47.054 | 48.6799 | 47.8669 | 48.1618
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4574 | 24.4574 | 12.197 | 12.7778 | 19.1092 | 18.6531 | 23.3359 | 24.4477 | 23.8919 | 24.1819
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0063915 | 0.0065838 | 0.0064876 | 0.0064876
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.9291 | 850.9291 | 815.8737 | 817.5342 | 835.6372 | 834.3332 | 848.6347 | 852.0779 | 850.3563 | 851.1864
[17 empty] | Enthalpy (J/gda) | 36.4347 | 39.1307 | 39.1307 | 26.6807 | 27.2704 | 33.6997 | 33.2366 | 39.7108 | 41.3309 | 40.5209 | 40.8157
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7267 | 23.7267 | 12.1999 | 12.7778 | 31.7525 | 30.2201 | 23.341 | 24.4542 | 23.8977 | 24.1862
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.011654 | 0.011654 | 0.008437 | 0.008437 | 0.008437 | 0.008437 | 0.0091126 | 0.0093049 | 0.0092088 | 0.0092088
[17 empty] | Specific volume (L/kgda) | 860.0491 | 856.8696 | 856.8696 | 819.4189 | 821.0783 | 875.5668 | 871.1661 | 852.3243 | 855.7852 | 854.0548 | 854.8844
[17 empty] | Enthalpy (J/gda) | 62.7052 | 53.5007 | 53.5007 | 33.5507 | 34.1405 | 53.5047 | 51.9408 | 46.6394 | 48.2666 | 47.453 | 47.7479
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2005 | 12.778 | 31.7464 | 30.2159 | 23.341 | 24.4542 | 23.8977 | 24.186
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.015566 | 0.0088403 | 0.0088403 | 0.0088403 | 0.0088403 | 0.0095159 | 0.0097083 | 0.0096121 | 0.0096121
[17 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 860.0491 | 819.9449 | 821.6042 | 876.1092 | 871.7114 | 852.869 | 856.3319 | 854.6005 | 855.43
[17 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 62.7052 | 34.5692 | 35.159 | 54.5309 | 52.9678 | 47.6656 | 49.2936 | 48.4796 | 48.7745
[17 empty] | Mass flow rate (kgda/s) | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.1957 | 12.7778 | 19.0996 | 18.64 | 23.3359 | 24.4477 | 23.8919 | 24.1825
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051566 | 0.005349 | 0.0052528 | 0.0052528
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 850.518 | 814.2649 | 815.9259 | 833.966 | 832.6545 | 846.967 | 850.4039 | 848.6855 | 849.5159
[17 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 36.4347 | 23.5631 | 24.1529 | 30.558 | 30.0923 | 36.569 | 38.1866 | 37.3778 | 37.6726
[17 empty] | Mass flow rate (kgda/s) | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.3476 | 0 | 0 | 0 | 4.1447 | 4.5018 | 4.8988 |  | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.2849 | 46.6818 | 35.8658 | 21.1299 | 22.2381 | 22.2381 | 22.4393
| AE403 | 0 | 1.4654 | 0 | 0 | 2.3446 | 0 | 0 | 1.4098 | 7.5791e-17 | 1.4098 | 32.3951 | 0 | 0 |  |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022891 | 0.0022874 | 0.0022874 | 0.0022874
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.2943 | 6.48 | 13.7744 | 96.7661 | 0 | 0 |  |  | Specific volume (L/kgda) | 692.013 | 692.013 | 794.6804 | 794.6804 | 794.858 | 906.5239 | 875.8672 | 836.8215 | 839.9704 | 839.9704 | 840.5426
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.0987 | -3.0316e-16 | 4.0987 | 52.6788 | 0 | 0 |  |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.9084 | 7.9084 | 7.9714 | 47.578 | 36.7044 | 27.047 | 28.1611 | 28.1611 | 28.3641
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.5461 | 4.8931 | 8.4392 | 99.3471 | 0 | 0 |  |  | Mass flow rate (kgda/s) | 0.28416 | 0.28416 | 0.28416 | 0.28416 | 0.28416 | 0.11366 | 0.17049 | n/a* | n/a* | 1.9429e-16 | 1.9429e-16
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.4927 | 5.4244 | 8.9171 | 99.8844 | 0 | 0 |  | AE403 | Dry bulb temperature (°C) | 15.5 | 16.8403 | 16.8403 | 12.6915 | 12.7778 | 12.7781 | 12.7781 | 23.3333 | 24.4444 | 23.9387 | 24.1396
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1393 | -6.0633e-16 | 4.1393 | 49.3605 | 0 | 0 |  |  | Humidity ratio (g/gda) | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334
[17 empty] | Specific volume (L/kgda) | 821.6592 | 825.4746 | 825.4746 | 813.6646 | 813.9103 | 813.9113 | 813.9113 | 843.9573 | 847.1201 | 845.6804 | 846.2525
[17 empty] | Enthalpy (J/gda) | 22.9959 | 24.35 | 24.35 | 20.1584 | 20.2456 | 20.246 | 20.246 | 30.9098 | 32.0324 | 31.5214 | 31.7244
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.33634 | 0.33634 | 0.33634 | 0.33634 | 0.13741 | 0.19892 | n/a* | n/a* | 0.052179 | 0.052179
[16 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.8033 | 25.8033 | 12.5624 | 12.7778 | 12.7846 | 12.7846 | 23.8864 | 24.9961 | 24.3686 | 24.567
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013482 | 0.013482 | 0.0087695 | 0.0087695 | 0.0087824 | 0.0087824 | 0.0096746 | 0.010009 | 0.0098198 | 0.0098198
[17 empty] | Specific volume (L/kgda) | 873.0237 | 865.3527 | 865.3527 | 820.8926 | 821.5114 | 821.5477 | 821.5477 | 854.6527 | 858.2997 | 856.2368 | 856.8079
[17 empty] | Enthalpy (J/gda) | 69.814 | 60.2922 | 60.2922 | 34.7601 | 34.98 | 35.0193 | 35.0193 | 48.6272 | 50.6138 | 49.4901 | 49.6931
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.53949 | 0.53949 | 0.53949 | 0.53949 | 0.25809 | 0.2814 | n/a* | n/a* | 0.25533 | 0.25533
[16 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7845 | 24.7845 | 12.6927 | 12.7778 | 12.7778 | 12.7778 | 23.3304 | 24.4403 | 23.9329 | 24.1326
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0064717 | 0.0065313 | 0.0065041 | 0.0065041
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.6004 | 850.6004 | 816.0786 | 816.3214 | 816.3214 | 816.3214 | 848.7275 | 851.9855 | 850.496 | 851.0677
[17 empty] | Enthalpy (J/gda) | 36.4347 | 37.091 | 37.091 | 24.8332 | 24.9194 | 24.9194 | 24.9194 | 39.9093 | 41.1898 | 40.6044 | 40.8075
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.13656 | 0.19768 | n/a* | n/a* | 0.050079 | 0.050216
[16 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1602 | 23.1602 | 12.6947 | 12.7778 | 12.7783 | 12.7783 | 23.3304 | 24.4403 | 23.9299 | 24.128
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.014886 | 0.014886 | 0.0090865 | 0.0090865 | 0.0090851 | 0.0090851 | 0.010785 | 0.010845 | 0.010818 | 0.010818
[17 empty] | Specific volume (L/kgda) | 860.0491 | 859.5975 | 859.5975 | 821.6856 | 821.9243 | 821.9239 | 821.9239 | 854.553 | 857.8335 | 856.325 | 856.896
[17 empty] | Enthalpy (J/gda) | 62.7052 | 61.1428 | 61.1428 | 35.6955 | 35.7803 | 35.7772 | 35.7772 | 50.8845 | 52.1751 | 51.5817 | 51.7847
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.1355 | 0.19614 | n/a* | n/a* | 0.047479 | 0.047479
[16 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6949 | 12.778 | 12.778 | 12.778 | 23.3304 | 24.4403 | 23.9299 | 24.1313
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.015566 | 0.0091365 | 0.0091365 | 0.0091365 | 0.0091365 | 0.010837 | 0.010897 | 0.010869 | 0.010869
[17 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 860.0491 | 821.7513 | 821.99 | 821.99 | 821.99 | 854.6228 | 857.9035 | 856.3948 | 856.9754
[17 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 62.7052 | 35.8219 | 35.9068 | 35.9068 | 35.9068 | 51.0159 | 52.3067 | 51.7131 | 51.9196
[17 empty] | Mass flow rate (kgda/s) | 0.3317 | 0.3317 | 0.3317 | 0.3317 | 0.3317 | 0.13548 | 0.19612 | n/a* | n/a* | 0.04744 | 0.047539
[16 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6925 | 12.7778 | 12.7862 | 12.7862 | 23.3304 | 24.4403 | 23.9333 | 24.133
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0061658 | 0.0062255 | 0.0061982 | 0.0061982
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 850.518 | 815.6827 | 815.9259 | 815.95 | 815.95 | 848.3143 | 851.5708 | 850.083 | 850.6546
[17 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 36.4347 | 24.0665 | 24.1529 | 24.1614 | 24.1614 | 39.131 | 40.411 | 39.8262 | 40.0292
[17 empty] | Mass flow rate (kgda/s) | 0.33468 | 0.33468 | 0.33468 | 0.33468 | 0.33468 | 0.13674 | 0.19793 | n/a* | n/a* | 0.050519 | 0.050519
* n/a = not applicable

## Title Page
ASHRAE Standard 140-2017 | To print example results:
Informative Annex B16, Section B16.7.2 | 1. Select results type in cell B21:
"Example" for Airside HVAC BESTEST Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.5, Airside HVAC Equipment Performance Tests AE301 through AE445 | "Title Page" thru "Figure List"
"Tables 1" thru "Delta Tables 2"
"Fig B16.7.2-1 TotalCoil" through "Fig B16.7.2-35 VAV dEcono"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Scratch area for Table subtitle 1
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445
Scratch area for Table subtitle 2
Scratch area for chart subtitles 1
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Scratch area for chart subtitles 2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445

## Program List
ASHRAE Standard 140-2017
Computer Programs, Program Authors, and Producers of Example Results for
Section 5.5, Airside HVAC Equipment Performance Tests AE301 through AE445
The quasi-analytical solution and programs used to generate the example results are described in Table B17-13. The first
column of the table ("Model") indicates the program name and version number, or indicates a quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry organization
with expertise in building science that wrote the simulation software.
The third column ("Implemented By") indicates the national research facility, university, or industry organization with
expertise in building science that performed the simulations or did the quasi-analytical solutions. The organizations that
performed simulations either ran software written by their organization or otherwise maintained contact with the program
authors during the project.
The fourth column ("Abbreviation") indicates the identifying abbreviation used in the results tables and figures.
See Standard 140, Informative Annex B17 for further details.
Table B17-13 Airside HVAC Cases
Participating Organizations and Models
Model | Authoring Organization | Implemented by | Abbreviation
Quasi-Analytical Solution (QAS) | PSUa/UNOb/TAMUc/NRELd/JNAe/ MDKf, United States | NRELd/JNAe/MDKf, United States | QAS/PSU-TAMU-NREL
DEEAPg 1.1.2 | AAON, Inc., United States | AAON, Inc., United States | DEEAP/AAON
DeSTh 2 | Tsinghua University, China | Tsinghua University, China / LBNLi, United States | DeST/TsinghuaU-LBNL
DOE-2.2 V48L | JJHj/LBNLi/UCk, United States | NRELd/JNAe/MDKf, United States | DOE-2.2/NREL
EnergyPlus 8.2.0 | DOE-BTl, United States | GARD Analytics, Inc., United States | EnergyPlus/GARD
IES-VEm 2014.2 | IESn, United Kingdom | IESn, United Kingdom | IES-VE/IES
LCEMo 3.10 | MLITp, Japan | TTEq, Japan | LCEM/MLIT-TTE
TRNSYS 17.01.0028 | TESSr/UWMs, United States | TESSr, United States | TRNSYS/TESS
a PSU: The Pennsylvania State University, United States
b UNO: University of Nebraska - Omaha, United States
c TAMU: Texas A&M University, United States
d NREL: National Renewable Energy Laboratory, United States
e JNA: J. Neymark & Associates, United States
f MDK: Mike D. Kennedy, Inc., United States
g DEEAP: Detailed Energy and Economic Analysis Program
h DeST: Designer's Simulation Toolkit
i LBNL: Lawrence Berkeley National Laboratory, United States
J JJH: James J. Hirsch & Associates, United States
k UC: University of California, United States
l DOE-BT: U.S. Department of Energy, Office of Building Technologies, Energy Efficiency and Renewable Energy, United States
m IES-VE: Integrated Environmental Solutions - Virtual Environment
n IES: Integrated Environmental Solutions, United Kingdom
o LCEM: Life Cycle Energy Management tool; LCEM was not run for the CV and VAV system cases (AE301 through AE445)
p MLIT: Ministry of Land, Infrastructure, Transportation and Tourism, Japan
q TTE: Takasago Thermal Engineering, Japan
r TESS: Thermal Energy System Specialists, United States
s UWM: University of Wisconsin - Madison, United States

## Table List
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.7.2-1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | Tables 1 | A5–J21
| B16.7.2-2 | CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) |  | A24–J40
| B16.7.2-3 | CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) |  | A43–J59
| B16.7.2-4 | CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) |  | A62–J78
| B16.7.2-5 | CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) |  | A81–J97
| B16.7.2-6 | CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) |  | A100–J116
| B16.7.2-7 | CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) |  | A119–J135
| B16.7.2-8 | CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) |  | A138–J154
| B16.7.2-9 | CV/VAV Outdoor Air Temperature (°F) |  | A157–J173
| B16.7.2-10 | CV/VAV Outdoor Air Humidity Ratio (g/gda) |  | A176–J192
| B16.7.2-11 | CV/VAV Outdoor Air Mass Flow Rate (kgda/s) |  | A195–J211
| B16.7.2-12 | CV/VAV Cooling Coil Outlet Air Temperature (°C) |  | A214–J230
| B16.7.2-13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) |  | A233–J249
| B16.7.2-14 | CV/VAV Supply Fan Air Temperature Rise (°C) |  | A252–J268
| B16.7.2-15 | CV/VAV Supply Air Temperature (°C) |  | A271–J287
| B16.7.2-16 | CV/VAV Supply Air Humidity Ratio (g/gda) |  | A290–J306
| B16.7.2-17 | CV/VAV Supply Air Specific Volume (L/kgda) |  | A309–J325
| B16.7.2-18 | CV/VAV Supply Air Enthalpy (J/gda) |  | A328–J344
| B16.7.2-19 | CV/VAV Supply Air Mass Flow Rate (kgda/s) |  | A347–J363
| B16.7.2-20 | CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) |  | A366–J382
| B16.7.2-21 | CV/VAV Zone 1 Supply Air Temperature (°C) |  | A385–J401
| B16.7.2-22 | CV/VAV Zone 1 Air Temperature (°C) |  | A404–J420
| B16.7.2-23 | CV/VAV Zone 1 Humidity Ratio (g/gda) |  | A423–J439
| B16.7.2-24 | CV/VAV Zone 2 Supply Air Temperature (°C) |  | A442–J458
| B16.7.2-25 | CV/VAV Zone 2 Air Temperature (°C) |  | A461–J477
| B16.7.2-26 | CV/VAV Zone 2 Humidity Ratio (g/gda) |  | A480–J496
| B16.7.2-27 | CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) |  | A499–J516
| B16.7.2-28 | CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) |  | A518–J535
| B16.7.2-29 | CV/VAV Return Fan Air Temperature Rise (°C) |  | A537–J553
| B16.7.2-30 | CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | Delta Tables 1 | A5–J14
| B16.7.2-31 | CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) |  | A17–J26
| B16.7.2-32 | CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) |  | A29–J38
| B16.7.2-33 | CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) |  | A41–J50
| B16.7.2-34 | CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Delta Tables 2 | A5–K13
| B16.7.2-35 | VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) |  | A16–K24

## Figure List
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445
List of Figures
| Figure | Description | Sheet Tab
| B16.7.2-1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent | Fig B16.7.2-1 TotalCoil H+C
| B16.7.2-2 | CV/VAV Total Sensible Coil Load, Heating + Cooling | Fig B16.7.2-2 TotalSensCoil H+C
| B16.7.2-3 | CV/VAV Pre-Heating Coil Load [QHpreheat] | Fig B16.7.2-3 PreHeatCoil
| B16.7.2-4 | CV/VAV Cooling Coil Load, Total [QCtotal] | Fig B16.7.2-4 CoolCoilTot
| B16.7.2-5 | CV/VAV Cooling Coil Load, Sensible [QCsensible] | Fig B16.7.2-5 CoolCoilSens
| B16.7.2-6 | CV/VAV Cooling Coil Load, Latent [QClatent] | Fig B16.7.2-6 CoolCoilLat
| B16.7.2-7 | CV/VAV Zone 1 Reheat Load [QH1reheat] | Fig B16.7.2-7 Zone1 Reheat
| B16.7.2-8 | CV/VAV Zone 2 Reheat Load [QH2reheat] | Fig B16.7.2-8 Zone2 Reheat
| B16.7.2-9 | CV/VAV Outdoor Air Temperature | Fig B16.7.2-9 OAT
| B16.7.2-10 | CV/VAV Outdoor Air Humidity Ratio | Fig B16.7.2-10 OAW
| B16.7.2-11 | CV/VAV Outdoor Air Mass Flow Rate | Fig B16.7.2-11 OAmassflow
| B16.7.2-12 | CV/VAV Cooling Coil Outlet Air Temperature | Fig B16.7.2-12 CCOT
| B16.7.2-13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] | Fig B16.7.2-13 RHcco
| B16.7.2-14 | CV/VAV Supply Fan Air Temperature Rise | Fig B16.7.2-14 Supply Fan dT
| B16.7.2-15 | CV/VAV Supply Air Temperature | Fig B16.7.2-15 SAT
| B16.7.2-16 | CV/VAV Supply Air Humidity Ratio | Fig B16.7.2-16 SAW
| B16.7.2-17 | CV/VAV Supply Air Specific Volume | Fig B16.7.2-17 SAVs
| B16.7.2-18 | CV/VAV Supply Air Enthalpy | Fig B16.7.2-18 SAenth
| B16.7.2-19 | CV/VAV Supply Air Mass Flow Rate | Fig B16.7.2-19 SAmassflow
| B16.7.2-20 | CV/VAV Outdoor Air to Supply Air Mass Flow Ratio | Fig B16.7.2-20 OAfrac
| B16.7.2-21 | CV/VAV Zone 1 Supply Air Temperature | Fig B16.7.2-21 Zone1 SAT
| B16.7.2-22 | CV/VAV Zone 1 Air Temperature | Fig B16.7.2-22 Zone1 AirT
| B16.7.2-23 | CV/VAV Zone 1 Humidity Ratio | Fig B16.7.2-23 Zone1 AirW
| B16.7.2-24 | CV/VAV Zone 2 Supply Air Temperature | Fig B16.7.2-24 Zone2 SAT
| B16.7.2-25 | CV/VAV Zone 2 Air Temperature | Fig B16.7.2-25 Zone2 AirT
| B16.7.2-26 | CV/VAV Zone 2 Humidity Ratio | Fig B16.7.2-26 Zone2 AirW
| B16.7.2-27 | CV/VAV Moisture Added to Zone 1 by Latent Gains | Fig B16.7.2-27 Zone1 Lat Gain
| B16.7.2-28 | CV/VAV Moisture Added to Zone 2 by Latent Gains | Fig B16.7.2-28 Zone2 Lat Gain
| B16.7.2-29 | CV/VAV Return Fan Air Temperature Rise | Fig B16.7.2-29 Return Fan dT
| B16.7.2-30 | CV/VAV Delta Pre-Heating Coil Load, CV-VAV | Fig B16.7.2-30 CV-VV dPreheat
| B16.7.2-31 | CV/VAV Delta Total Cooling Coil Load, CV-VAV | Fig B16.7.2-31 CV-VV dTot Cool
| B16.7.2-32 | CV/VAV Delta Sensible Cooling Coil Load, CV-VAV | Fig B16.7.2-32 CV-VV dSens Cool
| B16.7.2-33 | CV/VAV Delta Latent Cooling Coil Load, CV-VAV | Fig B16.7.2-33 CV-VV dLat Cool
| B16.7.2-34 | CV Delta Cooling Coil Load, Economizer Operation | Fig B16.7.2-34 CV dEcono
| B16.7.2-35 | VAV Delta Cooling Coil Load, Economizer Operation | Fig B16.7.2-35 VAV dEcono

## scrape titles new new (hidden)
Org Tab Name | Org Chart Title | Org Yaxis Title | Proposed Num | New Tab Name | New Chart Title | New Axis Title
Fig 4.2-1 TotalCoil H+C | Figure 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent | Coil Load (kWh/h) | 1 | Fig 4.2-1 TotalCoil H+C | Figure 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent
Fig 4.2-2 TotalSensCoil H+C | Figure 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling | Coil Load (kWh/h) | 2 | Fig 4.2-2 TotalSensCoil H+C | Figure 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-2 | CV/VAV Total Sensible Coil Load, Heating + Cooling
Fig 4.2-3 PreHeatCoil | Figure 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] | Coil Load (kWh/h) | 3 | Fig 4.2-3 PreHeatCoil | Figure 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-3 | CV/VAV Pre-Heating Coil Load [QHpreheat]
Fig 4.2-4 CoolCoilTot | Figure 4.2-4. CV/VAV Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | 4 | Fig 4.2-4 CoolCoilTot | Figure 4.2-4. CV/VAV Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-4 | CV/VAV Cooling Coil Load, Total [QCtotal]
Fig 4.2-5 CoolCoilSens | Figure 4.2-5. CV/VAV Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | 5 | Fig 4.2-5 CoolCoilSens | Figure 4.2-5. CV/VAV Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-5 | CV/VAV Cooling Coil Load, Sensible [QCsensible]
Fig 4.2-6 CoolCoilLat | Figure 4.2-6. CV/VAV Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | 6 | Fig 4.2-6 CoolCoilLat | Figure 4.2-6. CV/VAV Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-6 | CV/VAV Cooling Coil Load, Latent [QClatent]
Fig 4.2-7 Zone1 Reheat | Figure 4.2-7. CV/VAV Zone 1 Reheat Load [QH1reheat] | Coil Load (kWh/h) | 7 | Fig 4.2-7 Zone1 Reheat | Figure 4.2-7. CV/VAV Zone 1 Reheat Load [QH1reheat] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-7 | CV/VAV Zone 1 Reheat Load [QH1reheat]
Fig 4.2-8 Zone2 Reheat | Figure 4.2-8. CV/VAV Zone 2 Reheat Load [QH2reheat] | Coil Load (kWh/h) | 8 | Fig 4.2-8 Zone2 Reheat | Figure 4.2-8. CV/VAV Zone 2 Reheat Load [QH2reheat] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-8 | CV/VAV Zone 2 Reheat Load [QH2reheat]
Fig 4.2-9 OAT | Figure 4.2-9. CV/VAV Outdoor Air Temperature | Humidity Ratio (g/gda) | 9 | Fig 4.2-9 OAT | Figure 4.2-9. CV/VAV Outdoor Air Temperature | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-9 | CV/VAV Outdoor Air Temperature
Fig 4.2-10 OAW | Figure 4.2-10. CV/VAV Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | 10 | Fig 4.2-10 OAW | Figure 4.2-10. CV/VAV Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-10 | CV/VAV Outdoor Air Humidity Ratio
Fig 4.2-11 OAmassflow | Figure 4.2-11. CV/VAV Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 11 | Fig 4.2-11 OAmassflow | Figure 4.2-11. CV/VAV Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.2-11 | CV/VAV Outdoor Air Mass Flow Rate
Fig 4.2-12 CCOT | Figure 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature | Temperature (°C) | 12 | Fig 4.2-12 CCOT | Figure 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-12 | CV/VAV Cooling Coil Outlet Air Temperature
Fig 4.2-13 RHcco | Figure 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | 13 | Fig 4.2-13 RHcco | Figure 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | TRUE | TRUE | TRUE | 4.2-13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco]
Fig 4.2-14 Supply Fan dT | Figure 4.2-14. CV/VAV Supply Fan Air Temperature Rise | Temperature (°C) | 14 | Fig 4.2-14 Supply Fan dT | Figure 4.2-14. CV/VAV Supply Fan Air Temperature Rise | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-14 | CV/VAV Supply Fan Air Temperature Rise
Fig 4.2-15 SAT | Figure 4.2-15. CV/VAV Supply Air Temperature | Temperature (°C) | 15 | Fig 4.2-15 SAT | Figure 4.2-15. CV/VAV Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-15 | CV/VAV Supply Air Temperature
Fig 4.2-16 SAW | Figure 4.2-16. CV/VAV Supply Air Humidity Ratio | Humidity Ratio (g/gda) | 16 | Fig 4.2-16 SAW | Figure 4.2-16. CV/VAV Supply Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-16 | CV/VAV Supply Air Humidity Ratio
Fig 4.2-17 SAVs | Figure 4.2-17. CV/VAV Supply Air Specific Volume | Specific Volume (L/kgda) | 17 | Fig 4.2-17 SAVs | Figure 4.2-17. CV/VAV Supply Air Specific Volume | Specific Volume (L/kgda) | TRUE | TRUE | TRUE | 4.2-17 | CV/VAV Supply Air Specific Volume
Fig 4.2-18 SAenth | Figure 4.2-18. CV/VAV Supply Air Enthalpy | Enthalpy (J/gda) | 18 | Fig 4.2-18 SAenth | Figure 4.2-18. CV/VAV Supply Air Enthalpy | Enthalpy (J/gda) | TRUE | TRUE | TRUE | 4.2-18 | CV/VAV Supply Air Enthalpy
Fig 4.2-19 SAmassflow | Figure 4.2-19. CV/VAV Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 19 | Fig 4.2-19 SAmassflow | Figure 4.2-19. CV/VAV Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.2-19 | CV/VAV Supply Air Mass Flow Rate
Fig 4.2-20 Oafrac | Figure 4.2-20. CV/VAV Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0 - 1) | 20 | Fig 4.2-20 Oafrac | Figure 4.2-20. CV/VAV Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0 - 1) | TRUE | TRUE | TRUE | 4.2-20 | CV/VAV Outdoor Air to Supply Air Mass Flow Ratio
Fig 4.2-21 Zone1 SAT | Figure 4.2-21. CV/VAV Zone 1 Supply Air Temperature | Temperature (°C) | 21 | Fig 4.2-21 Zone1 SAT | Figure 4.2-21. CV/VAV Zone 1 Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-21 | CV/VAV Zone 1 Supply Air Temperature
Fig 4.2-22 Zone1 AirT | Figure 4.2-22. CV/VAV Zone 1 Air Temperature | Temperature (°C) | 22 | Fig 4.2-22 Zone1 AirT | Figure 4.2-22. CV/VAV Zone 1 Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-22 | CV/VAV Zone 1 Air Temperature
Fig 4.2-23 Zone1 AirW | Figure 4.2-23. CV/VAV Zone 1 Humidity Ratio | Humidity Ratio (g/gda) | 23 | Fig 4.2-23 Zone1 AirW | Figure 4.2-23. CV/VAV Zone 1 Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-23 | CV/VAV Zone 1 Humidity Ratio
Fig 4.2-24 Zone2 SAT | Figure 4.2-24. CV/VAV Zone 2 Supply Air Temperature | Temperature (°C) | 24 | Fig 4.2-24 Zone2 SAT | Figure 4.2-24. CV/VAV Zone 2 Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-24 | CV/VAV Zone 2 Supply Air Temperature
Fig 4.2-25 Zone2 AirT | Figure 4.2-25. CV/VAV Zone 2 Air Temperature | Temperature (°C) | 25 | Fig 4.2-25 Zone2 AirT | Figure 4.2-25. CV/VAV Zone 2 Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-25 | CV/VAV Zone 2 Air Temperature
Fig 4.2-26 Zone2 AirW | Figure 4.2-26. CV/VAV Zone 2 Humidity Ratio | Humidity Ratio (g/gda) | 26 | Fig 4.2-26 Zone2 AirW | Figure 4.2-26. CV/VAV Zone 2 Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-26 | CV/VAV Zone 2 Humidity Ratio
Fig 4.2-27 Zone1 Lat Gain | Figure 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains | Water Vapor (g/s) | 27 | Fig 4.2-27 Zone1 Lat Gain | Figure 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains | Water Vapor (g/s) | TRUE | TRUE | TRUE | 4.2-27 | CV/VAV Moisture Added to Zone 1 by Latent Gains
Fig 4.2-28 Zone2 Lat Gain | Figure 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains | Water Vapor (g/s) | 28 | Fig 4.2-28 Zone2 Lat Gain | Figure 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains | Water Vapor (g/s) | TRUE | TRUE | TRUE | 4.2-28 | CV/VAV Moisture Added to Zone 2 by Latent Gains
Fig 4.2-29 Return Fan dT | Figure 4.2-29. CV/VAV Return Fan Air Temperature Rise | Temperature (°C) | 29 | Fig 4.2-29 Return Fan dT | Figure 4.2-29. CV/VAV Return Fan Air Temperature Rise | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-29 | CV/VAV Return Fan Air Temperature Rise
Fig 4.2-30 CV-VV dPreheat | Figure 4.2-30. CV/VAV Delta Pre-Heating Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 30 | Fig 4.2-30 CV-VV dPreheat | Figure 4.2-30. CV/VAV Delta Pre-Heating Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-30 | CV/VAV Delta Pre-Heating Coil Load, CV-VAV
Fig 4.2-31 CV-VV dTot Cool | Figure 4.2-31. CV/VAV Delta Total Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 31 | Fig 4.2-31 CV-VV dTot Cool | Figure 4.2-31. CV/VAV Delta Total Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-31 | CV/VAV Delta Total Cooling Coil Load, CV-VAV
Fig 4.2-32 CV-VV dSens Cool | Figure 4.2-32. CV/VAV Delta Sensible Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 32 | Fig 4.2-32 CV-VV dSens Cool | Figure 4.2-32. CV/VAV Delta Sensible Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-32 | CV/VAV Delta Sensible Cooling Coil Load, CV-VAV
Fig 4.2-33 CV-VV dLat Cool | Figure 4.2-33. CV/VAV Delta Latent Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 33 | Fig 4.2-33 CV-VV dLat Cool | Figure 4.2-33. CV/VAV Delta Latent Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-33 | CV/VAV Delta Latent Cooling Coil Load, CV-VAV
Fig 4.2-34 CV dEcono | Figure 4.2-34. CV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | 34 | Fig 4.2-34 CV dEcono | Figure 4.2-34. CV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-34 | CV Delta Cooling Coil Load, Economizer Operation
Fig 4.2-35 VAV dEcono | Figure 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | 35 | Fig 4.2-35 VAV dEcono | Figure 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-35 | VAV Delta Cooling Coil Load, Economizer Operation
=CONCATENATE("Figure 4.2-",D36,". Airside HVAC, ",MID(B36,FIND("VAV",B36,8),100))

## scrape titles new (hidden)
Org Name | New Title | Yaxis Title | Proposed Num | New Name | New Title | New Axis title
Fig 4-1 TotalCoil | Figure 4-1. Airside HVAC: Total Coil Load | Total Coil Load (kWh/h) | 18 | Fig 4-18 TotalCoil | Figure 4-18. Airside HVAC - CV/VAV: Total Coil Load | Total Coil Load (kWh/h)
Fig 4-2 TotalSensCoil | Figure 4-2. Airside HVAC: Total Sensible Coil Load | Total Sensible Coil Load (kWh/h) | 19 | Fig 4-19 TotalSensCoil | Figure 4-19. Airside HVAC - CV/VAV: Total Sensible Coil Load | Total Sensible Coil Load (kWh/h)
Fig 4-3 PreHeatCoilkWh | Figure 4-3. Airside HVAC: Pre-Heating Coil Load | Pre-Heating Coil Load (QHpreheat) (kWh/h) | 20 | Fig 4-20 PreHeatCoilkWh | Figure 4-20. Airside HVAC - CV/VAV: Pre-Heating Coil Load | Pre-Heating Coil Load (QHpreheat) (kWh/h)
Fig 4-4 CoolCoilTot | Figure 4-4. Airside HVAC: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h) | 21 | Fig 4-21 CoolCoilTot | Figure 4-21. Airside HVAC - CV/VAV: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h)
Fig 4-5 CoolCoilSens | Figure 4-5. Airside HVAC: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h) | 22 | Fig 4-22 CoolCoilSens | Figure 4-22. Airside HVAC - CV/VAV: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
Fig 4-6 CoolCoilLat | Figure 4-6. Airside HVAC: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h) | 23 | Fig 4-23 CoolCoilLat | Figure 4-23. Airside HVAC - CV/VAV: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h)
Fig 4-7 RHcco | Figure 4-7. Airside HVAC: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%) | 24 | Fig 4-24 RHcco | Figure 4-24. Airside HVAC - CV/VAV: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%)
Fig 4-8 Z1 Reheat | Figure 4-8. Airside HVAC: Zone 1 Reheat Load | Zone 1 Reheat Load (QH1reheat) (kWh/h) | 25 | Fig 4-25 Z1 Reheat | Figure 4-25. Airside HVAC - CV/VAV: Zone 1 Reheat Load | Zone 1 Reheat Load (QH1reheat) (kWh/h)
Fig 4-9 Z2 Reheat | Figure 4-9. Airside HVAC: Zone 2 Reheat Load | Zone 2 Reheat Load (QH2reheat) (kWh/h) | 26 | Fig 4-26 Z2 Reheat | Figure 4-26. Airside HVAC - CV/VAV: Zone 2 Reheat Load | Zone 2 Reheat Load (QH2reheat) (kWh/h)
Fig 4-10 OAW | Figure 4-10. Airside HVAC: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda) | 27 | Fig 4-27 OAW | Figure 4-27. Airside HVAC - CV/VAV: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda)
Fig 4-11 OAmassflow | Figure 4-11. Airside HVAC: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s) | 28 | Fig 4-28 OAmassflow | Figure 4-28. Airside HVAC - CV/VAV: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s)
Fig 4-12 CCOT | Figure 4-12. Airside HVAC: Cooling Coil Outlet Air Temperature | Cooling Coil Outlet Air Temperature (°C) | 29 | Fig 4-29 CCOT | Figure 4-29. Airside HVAC - CV/VAV: Cooling Coil Outlet Air Temperature | Cooling Coil Outlet Air Temperature (°C)
Fig 4-13 SAT | Figure 4-13. Airside HVAC: Supply Air Temperature | Supply Air Temperature (°C) | 30 | Fig 4-30 SAT | Figure 4-30. Airside HVAC - CV/VAV: Supply Air Temperature | Supply Air Temperature (°C)
Fig 4-14 SAW | Figure 4-14. Airside HVAC: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda) | 31 | Fig 4-31 SAW | Figure 4-31. Airside HVAC - CV/VAV: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda)
Fig 4-15 SAVs | Figure 4-15. Airside HVAC: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda) | 32 | Fig 4-32 SAVs | Figure 4-32. Airside HVAC - CV/VAV: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda)
Fig 4-16 SAenth | Figure 4-16. Airside HVAC: Supply Air Enthalpy | Supply Air Enthalpy (j/gda) | 33 | Fig 4-33 SAenth | Figure 4-33. Airside HVAC - CV/VAV: Supply Air Enthalpy | Supply Air Enthalpy (j/gda)
Fig 4-17 SAmassflow | Figure 4-17. Airside HVAC: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s) | 34 | Fig 4-34 SAmassflow | Figure 4-34. Airside HVAC - CV/VAV: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s)
Fig 4-18 Supply Fan dT | Figure 4-18. Airside HVAC: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C) | 35 | Fig 4-35 Supply Fan dT | Figure 4-35. Airside HVAC - CV/VAV: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C)
Fig 4-19 Z1 AirTemp | Figure 4-19. Airside HVAC: Zone 1 Air Temperature | Zone 1 Air Temperature (°C) | 36 | Fig 4-36 Z1 AirTemp | Figure 4-36. Airside HVAC - CV/VAV: Zone 1 Air Temperature | Zone 1 Air Temperature (°C)
Fig 4-20 Z1 SAT | Figure 4-20. Airside HVAC: Zone 1 Supply Air Temperature | Zone 1 Supply Air Temperature (°C) | 37 | Fig 4-37 Z1 SAT | Figure 4-37. Airside HVAC - CV/VAV: Zone 1 Supply Air Temperature | Zone 1 Supply Air Temperature (°C)
Fig 4-21 Z1 delta W | Figure 4-21. Airside HVAC: Zone 1 Humidity Ratio Rise | Delta W (Zone 1 W minus SAW) | 38 | Fig 4-38 Z1 delta W | Figure 4-38. Airside HVAC - CV/VAV: Zone 1 Humidity Ratio Rise | Delta W (Zone 1 W minus SAW)
Fig 4-22 Z2 AirTemp | Figure 4-22. Airside HVAC: Zone 2 Air Temperature | Zone 2 Air Temperature (°C) | 39 | Fig 4-39 Z2 AirTemp | Figure 4-39. Airside HVAC - CV/VAV: Zone 2 Air Temperature | Zone 2 Air Temperature (°C)
Fig 4-23 Z2 SAT | Figure 4-23. Airside HVAC: Zone 2 Supply Air Temperature | Zone 2 Supply Air Temperature (°C) | 40 | Fig 4-40 Z2 SAT | Figure 4-40. Airside HVAC - CV/VAV: Zone 2 Supply Air Temperature | Zone 2 Supply Air Temperature (°C)
Fig 4-24 Z2 delta W | Figure 4-24. Airside HVAC: Zone 1 Humidity Ratio Rise | Delta W (Zone 2 W minus SAW) | 41 | Fig 4-41 Z2 delta W | Figure 4-41. Airside HVAC - CV/VAV: Zone 1 Humidity Ratio Rise | Delta W (Zone 2 W minus SAW)
Fig 4-25 Return Fan dT | Figure 4-25. Airside HVAC: Return Fan Temperature Rise | Return Fan Temperature Rise (°C) | 42 | Fig 4-42 Return Fan dT | Figure 4-42. Airside HVAC - CV/VAV: Return Fan Temperature Rise | Return Fan Temperature Rise (°C)
Fig 4-26 CV-VV dPreheat | Figure 4-26. Airside HVAC: Delta Pre-Heating Coil Load, CV-VAV | Delta Pre-Heating Coil Load (QHpreheat) (kWh/h) | 43 | Fig 4-43 CV-VV dPreheat | Figure 4-43. Airside HVAC - CV/VAV: Delta Pre-Heating Coil Load, CV-VAV | Delta Pre-Heating Coil Load (QHpreheat) (kWh/h)
Fig 4-27 CV-VV dTot Cool | Figure 4-27. Airside HVAC: Delta Total Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Total (QCtotal) (kWh/h) | 44 | Fig 4-44 CV-VV dTot Cool | Figure 4-44. Airside HVAC - CV/VAV: Delta Total Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Total (QCtotal) (kWh/h)
Fig 4-28 CV-VV dSens Cool | Figure 4-28. Airside HVAC: Delta Sensible Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Sensible (QCsensible) (kWh/h) | 45 | Fig 4-45 CV-VV dSens Cool | Figure 4-45. Airside HVAC - CV/VAV: Delta Sensible Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Sensible (QCsensible) (kWh/h)
Fig 4-29 CV-VV dLat Cool | Figure 4-29. Airside HVAC: Delta Latent Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Latent (QClatent) (kWh/h) | 46 | Fig 4-46 CV-VV dLat Cool | Figure 4-46. Airside HVAC - CV/VAV: Delta Latent Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Latent (QClatent) (kWh/h)
Fig 4-30 CV dEcono | Figure 4-30. Airside HVAC: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h) | 47 | Fig 4-47 CV dEcono | Figure 4-47. Airside HVAC - CV/VAV: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h)
Fig 4-31 VAV dEcono | Figure 4-31. Airside HVAC: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h) | 48 | Fig 4-48 VAV dEcono | Figure 4-48. Airside HVAC - CV/VAV: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h)

## scrape titles (hidden)
Org Name | Yaxis Title | Proposed Num | New root | New Name | New Title | New Axis title
TotalCoil (2) | Aggregate Coil Loads, Heating+Cooling (kWh/h) | 1 | TotalCoil | Fig 4-1 TotalCoil | Figure 4-1. Airside HVAC - CV/VAV: Aggregate Coil Loads, Heating+Cooling | Total Coil Load (kWh/h)
TotalSensCoil (2) | Aggregate Coil Loads, Heating+Cooling (kWh/h) | 2 | TotalSensCoil | Fig 4-2 TotalSensCoil | Figure 4-2. Airside HVAC: Aggregate Coil Loads, Heating+Cooling | Total Sensible Coil Load (kWh/h)
PreHeatCoilkWh (2) | Pre-Heating Coil Load (QHpreheat) (kWh/h) | 3 | PreHeatCoilkWh | Fig 4-3 PreHeatCoilkWh | Figure 4-3. Airside HVAC: Pre-Heating Coil Load | Pre-Heating Coil Load (QHpreheat) (kWh/h)
CoolCoilTot (2) | Cooling Coil Loads, Total (QCtotal) (kWh/h) | 4 | CoolCoilTot | Fig 4-4 CoolCoilTot | Figure 4-4. Airside HVAC: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h)
CoolCoilSens (2) | Cooling Coil Loads, Sensible (QCsensible) (kWh/h) | 5 | CoolCoilSens | Fig 4-5 CoolCoilSens | Figure 4-5. Airside HVAC: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
CoolCoilLat (2) | Cooling Coil Loads, Latent (QClatent) (kWh/h) | 6 | CoolCoilLat | Fig 4-6 CoolCoilLat | Figure 4-6. Airside HVAC: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h)
RHcco (2) | Cooling Coil Outlet Relative Humidity (RHcco) (%) | 7 | RHcco | Fig 4-7 RHcco | Figure 4-7. Airside HVAC: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%)
Z1 Reheat (2) | Zone 1 Reheat Load (QH1reheat) (kWh/h) | 8 | Z1 Reheat | Fig 4-8 Z1 Reheat | Figure 4-8. Airside HVAC: Zone 1 Reheat Load | Zone 1 Reheat Load (QH1reheat) (kWh/h)
Z2 Reheat (2) | Zone 2 Reheat Load (QH2reheat) (kWh/h) | 9 | Z2 Reheat | Fig 4-9 Z2 Reheat | Figure 4-9. Airside HVAC: Zone 2 Reheat Load | Zone 2 Reheat Load (QH2reheat) (kWh/h)
OAW (2) | Outdoor Air Humidity Ratio (g/gda) | 10 | OAW | Fig 4-10 OAW | Figure 4-10. Airside HVAC: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda)
OAmassflow (2) | Outdoor Air Mass Flow Rate (kgda/s) | 11 | OAmassflow | Fig 4-11 OAmassflow | Figure 4-11. Airside HVAC: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s)
CCOT (2) | Cooling Coil Outlet Air Temperature (°C) | 12 | CCOT | Fig 4-12 CCOT | Figure 4-12. Airside HVAC: Cooling Coil Outlet Air Temperature | Cooling Coil Outlet Air Temperature (°C)
SAT (2) | Supply Air Temperature (°C) | 13 | SAT | Fig 4-13 SAT | Figure 4-13. Airside HVAC: Supply Air Temperature | Supply Air Temperature (°C)
SAW (2) | Supply Air Humidity Ratio (g/gda) | 14 | SAW | Fig 4-14 SAW | Figure 4-14. Airside HVAC: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda)
SAVs (2) | Supply Air Specific Volume (L/kgda) | 15 | SAVs | Fig 4-15 SAVs | Figure 4-15. Airside HVAC: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda)
SAenth (2) | Supply Air Enthalpy (j/gda) | 16 | SAenth | Fig 4-16 SAenth | Figure 4-16. Airside HVAC: Supply Air Enthalpy | Supply Air Enthalpy (j/gda)
SAmassflow (2) | Supply Air Mass Flow Rate (kgda/s) | 17 | SAmassflow | Fig 4-17 SAmassflow | Figure 4-17. Airside HVAC: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s)
Supply Fan dT (2) | Supply Fan Temperature Rise (°C) | 18 | Supply Fan dT | Fig 4-18 Supply Fan dT | Figure 4-18. Airside HVAC: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C)
Z1 AirTemp (2) | Zone 1 Air Temperature (°C) | 19 | Z1 AirTemp | Fig 4-19 Z1 AirTemp | Figure 4-19. Airside HVAC: Zone 1 Air Temperature | Zone 1 Air Temperature (°C)
Z1 SAT (2) | Zone 1 Supply Air Temperature (°C) | 20 | Z1 SAT | Fig 4-20 Z1 SAT | Figure 4-20. Airside HVAC: Zone 1 Supply Air Temperature | Zone 1 Supply Air Temperature (°C)
Z1 delta W (2) | Delta W (Zone 1 W minus SAW) | 21 | Z1 delta W | Fig 4-21 Z1 delta W | Figure 4-21. Airside HVAC: Delta W | Delta W (Zone 1 W minus SAW)
Z2 AirTemp (2) | Zone 2 Air Temperature (°C) | 22 | Z2 AirTemp | Fig 4-22 Z2 AirTemp | Figure 4-22. Airside HVAC: Zone 2 Air Temperature | Zone 2 Air Temperature (°C)
Z2 SAT (2) | Zone 2 Supply Air Temperature (°C) | 23 | Z2 SAT | Fig 4-23 Z2 SAT | Figure 4-23. Airside HVAC: Zone 2 Supply Air Temperature | Zone 2 Supply Air Temperature (°C)
Z2 delta W (2) | Delta W (Zone 2 W minus SAW) | 24 | Z2 delta W | Fig 4-24 Z2 delta W | Figure 4-24. Airside HVAC: Delta W | Delta W (Zone 2 W minus SAW)
Return Fan dT (2) | Return Fan Temperature Rise (°C) | 25 | Return Fan dT | Fig 4-25 Return Fan dT | Figure 4-25. Airside HVAC: Return Fan Temperature Rise | Return Fan Temperature Rise (°C)
CV-VV Delta Preheat (2) | CV - VAV Delta Pre-Heating Coil Load (QHpreheat) (kWh/h) | 26 | CV-VV dPreheat | Fig 4-26 CV-VV dPreheat | Figure 4-26. Airside HVAC: CV - VAV Delta Pre-Heating Coil Load | Delta Pre-Heating Coil Load (QHpreheat) (kWh/h)
CV-VV Delta Total Cooling (2) | CV - VAV Delta Cooling Coil Load, Total (QCtotal) (kWh/h) | 27 | CV-VV dTot Cool | Fig 4-27 CV-VV dTot Cool | Figure 4-27. Airside HVAC: CV - VAV Delta Cooling Coil Load, Total | Delta Cooling Coil Loads, Total (QCtotal) (kWh/h)
CV-VV Delta Sensible Coolin (2 | CV - VAV Delta Cooling Coil Load, Sensible (QCsensible) (kWh/h) | 28 | CV-VV dSens Cool | Fig 4-28 CV-VV dSens Cool | Figure 4-28. Airside HVAC: CV - VAV Delta Cooling Coil Load, Sensible | Delta Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
CV-VV Delta Latent Cooling (2) | CV - VAV Delta Cooling Coil Load, Latent (QClatent) (kWh/h) | 29 | CV-VV dLat Cool | Fig 4-29 CV-VV dLat Cool | Figure 4-29. Airside HVAC: CV - VAV Delta Cooling Coil Load, Latent | Delta Cooling Coil Loads, Latent (QClatent) (kWh/h)
CV Delta Econo (2) | Economizer Delta Cooling Coil Load (kWh/h) | 30 | CV dEcono | Fig 4-30 CV dEcono | Figure 4-30. Airside HVAC: Economizer Delta Cooling Coil Load | Delta Cooling Coil Loads, Econo - No Econo (kWh/h)
VAV Delta Econo (2) | Economiser Delta Cooling Coil Load (kWh/h) | 31 | VAV dEcono | Fig 4-31 VAV dEcono | Figure 4-31. Airside HVAC: Economiser Delta Cooling Coil Load | Delta Cooling Coil Loads, Econo - No Econo (kWh/h)

## scrape Table names (hidden)
worksheet | Table Name | sequence | Table Name Root | New Table Name | number
Tables 1 | Table 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | 1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | Table 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | 4.2-1 | TRUE
Tables 1 | Table 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | 2 | CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | Table 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | 4.2-2 | TRUE
Tables 1 | Table 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) | 3 | CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) | Table 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) | 4.2-3 | TRUE
Tables 1 | Table 4.2-4. CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) | 4 | CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) | Table 4.2-4. CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) | 4.2-4 | TRUE
Tables 1 | Table 4.2-5. CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) | 5 | CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) | Table 4.2-5. CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) | 4.2-5 | TRUE
Tables 1 | Table 4.2-6. CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) | 6 | CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) | Table 4.2-6. CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) | 4.2-6 | TRUE
Tables 1 | Table 4.2-7. CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) | 7 | CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) | Table 4.2-7. CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) | 4.2-7 | TRUE
Tables 1 | Table 4.2-8. CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) | 8 | CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) | Table 4.2-8. CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) | 4.2-8 | TRUE
Tables 1 | Table 4.2-9. CV/VAV Outdoor Air Temperature (°F) | 9 | CV/VAV Outdoor Air Temperature (°F) | Table 4.2-9. CV/VAV Outdoor Air Temperature (°F) | 4.2-9 | TRUE
Tables 1 | Table 4.2-10. CV/VAV Outdoor Air Humidity Ratio (g/gda) | 10 | CV/VAV Outdoor Air Humidity Ratio (g/gda) | Table 4.2-10. CV/VAV Outdoor Air Humidity Ratio (g/gda) | 4.2-10 | TRUE
Tables 1 | Table 4.2-11. CV/VAV Outdoor Air Mass Flow Rate (kgda/s) | 11 | CV/VAV Outdoor Air Mass Flow Rate (kgda/s) | Table 4.2-11. CV/VAV Outdoor Air Mass Flow Rate (kgda/s) | 4.2-11 | TRUE
Tables 1 | Table 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature (°C) | 12 | CV/VAV Cooling Coil Outlet Air Temperature (°C) | Table 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature (°C) | 4.2-12 | TRUE
Tables 1 | Table 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) | 13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) | Table 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) | 4.2-13 | TRUE
Tables 1 | Table 4.2-14. CV/VAV Supply Fan Air Temperature Rise (°C) | 14 | CV/VAV Supply Fan Air Temperature Rise (°C) | Table 4.2-14. CV/VAV Supply Fan Air Temperature Rise (°C) | 4.2-14 | TRUE
Tables 1 | Table 4.2-15. CV/VAV Supply Air Temperature (°C) | 15 | CV/VAV Supply Air Temperature (°C) | Table 4.2-15. CV/VAV Supply Air Temperature (°C) | 4.2-15 | TRUE
Tables 1 | Table 4.2-16. CV/VAV Supply Air Humidity Ratio (g/gda) | 16 | CV/VAV Supply Air Humidity Ratio (g/gda) | Table 4.2-16. CV/VAV Supply Air Humidity Ratio (g/gda) | 4.2-16 | TRUE
Tables 1 | Table 4.2-17. CV/VAV Supply Air Specific Volume (L/kgda) | 17 | CV/VAV Supply Air Specific Volume (L/kgda) | Table 4.2-17. CV/VAV Supply Air Specific Volume (L/kgda) | 4.2-17 | TRUE
Tables 1 | Table 4.2-18. CV/VAV Supply Air Enthalpy (J/gda) | 18 | CV/VAV Supply Air Enthalpy (J/gda) | Table 4.2-18. CV/VAV Supply Air Enthalpy (J/gda) | 4.2-18 | TRUE
Tables 1 | Table 4.2-19. CV/VAV Supply Air Mass Flow Rate (kgda/s) | 19 | CV/VAV Supply Air Mass Flow Rate (kgda/s) | Table 4.2-19. CV/VAV Supply Air Mass Flow Rate (kgda/s) | 4.2-19 | TRUE
Tables 1 | Table 4.2-20. CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) | 20 | CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) | Table 4.2-20. CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) | 4.2-20 | TRUE
Tables 1 | Table 4.2-21. CV/VAV Zone 1 Supply Air Temperature (°C) | 21 | CV/VAV Zone 1 Supply Air Temperature (°C) | Table 4.2-21. CV/VAV Zone 1 Supply Air Temperature (°C) | 4.2-21 | TRUE
Tables 1 | Table 4.2-22. CV/VAV Zone 1 Air Temperature (°C) | 22 | CV/VAV Zone 1 Air Temperature (°C) | Table 4.2-22. CV/VAV Zone 1 Air Temperature (°C) | 4.2-22 | TRUE
Tables 1 | Table 4.2-23. CV/VAV Zone 1 Humidity Ratio (g/gda) | 23 | CV/VAV Zone 1 Humidity Ratio (g/gda) | Table 4.2-23. CV/VAV Zone 1 Humidity Ratio (g/gda) | 4.2-23 | TRUE
Tables 1 | Table 4.2-24. CV/VAV Zone 2 Supply Air Temperature (°C) | 24 | CV/VAV Zone 2 Supply Air Temperature (°C) | Table 4.2-24. CV/VAV Zone 2 Supply Air Temperature (°C) | 4.2-24 | TRUE
Tables 1 | Table 4.2-25. CV/VAV Zone 2 Air Temperature (°C) | 25 | CV/VAV Zone 2 Air Temperature (°C) | Table 4.2-25. CV/VAV Zone 2 Air Temperature (°C) | 4.2-25 | TRUE
Tables 1 | Table 4.2-26. CV/VAV Zone 2 Humidity Ratio (g/gda) | 26 | CV/VAV Zone 2 Humidity Ratio (g/gda) | Table 4.2-26. CV/VAV Zone 2 Humidity Ratio (g/gda) | 4.2-26 | TRUE
Tables 1 | Table 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) | 27 | CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) | Table 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) | 4.2-27 | TRUE
Tables 1 | Table 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) | 28 | CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) | Table 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) | 4.2-28 | TRUE
Tables 1 | Table 4.2-29. CV/VAV Return Fan Air Temperature Rise (°C) | 29 | CV/VAV Return Fan Air Temperature Rise (°C) | Table 4.2-29. CV/VAV Return Fan Air Temperature Rise (°C) | 4.2-29 | TRUE
Delta Tables 1 | Table 4.2-30. CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | 30 | CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | Table 4.2-30. CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | 4.2-30 | TRUE
Delta Tables 1 | Table 4.2-31. CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 31 | CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-31. CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 4.2-31 | TRUE
Delta Tables 1 | Table 4.2-32. CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 32 | CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-32. CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 4.2-32 | TRUE
Delta Tables 1 | Table 4.2-33. CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 33 | CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-33. CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 4.2-33 | TRUE
Delta Tables 2 | Table 4.2-34. CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 34 | CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Table 4.2-34. CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 4.2-34 | TRUE
Delta Tables 2 | Table 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 35 | VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Table 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 4.2-35 | TRUE

## scrape Table names (old) (hidden)
worksheet | Table Name | sequence | Table Name Root | New Table Name | number
Tables 1 | Table 4.2-1. CV/VAV Total Sensible Coil Load (kWh/h) | 1 | CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | Table 4.2-1. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | 4.2-1
Tables 1 | Table 4.2-2. CV/VAV Total Sensible and Latent Coil Load (kWh/h) | 2 | CV/VAV Total Coil Load, Heating + Cooling, Sensible and Latent (kWh/h) | Table 4.2-2. CV/VAV Total Coil Load, Heating + Cooling, Sensible and Latent (kWh/h) | 4.2-2
Tables 1 | Table 4.2-3. CV/VAV Pre-Heating Coil Load (kWh/h) | 3 | CV/VAV Pre-Heating Coil Load (kWh/h) | Table 4.2-3. CV/VAV Pre-Heating Coil Load (kWh/h) | 4.2-3
Tables 1 | Table 4.2-4. CV/VAV Total Cooling Coil Load (kWh/h) | 4 | CV/VAV Total Cooling Coil Load (kWh/h) | Table 4.2-4. CV/VAV Total Cooling Coil Load (kWh/h) | 4.2-4
Tables 1 | Table 4.2-5. CV/VAV Sensible Cooling Coil Load (kWh/h) | 5 | CV/VAV Sensible Cooling Coil Load (kWh/h) | Table 4.2-5. CV/VAV Sensible Cooling Coil Load (kWh/h) | 4.2-5
Tables 1 | Table 4.2-6. CV/VAV Latent Cooling Coil Load (kWh/h) | 6 | CV/VAV Latent Cooling Coil Load (kWh/h) | Table 4.2-6. CV/VAV Latent Cooling Coil Load (kWh/h) | 4.2-6
Tables 1 | Table 4.2-7. CV/VAV Cooling Coil Outlet Relative Humidity (%) | 7 | CV/VAV Cooling Coil Outlet Relative Humidity (%) | Table 4.2-7. CV/VAV Cooling Coil Outlet Relative Humidity (%) | 4.2-7
Tables 1 | Table 4.2-8. CV/VAV Zone 1 Reheat Coil Load (kWh/h) | 8 | CV/VAV Zone 1 Reheat Coil Load (kWh/h) | Table 4.2-8. CV/VAV Zone 1 Reheat Coil Load (kWh/h) | 4.2-8
Tables 1 | Table 4.2-9. CV/VAV Zone 2 Reheat Coil Load (kWh/h) | 9 | CV/VAV Zone 2 Reheat Coil Load (kWh/h) | Table 4.2-9. CV/VAV Zone 2 Reheat Coil Load (kWh/h) | 4.2-9
Tables 1 | Table 4.2-10. Outdoor Air Humidity Ratio (g/gda) | 10 | Outdoor Air Humidity Ratio (g/gda) | Table 4.2-10. Outdoor Air Humidity Ratio (g/gda) | 4.2-10
Tables 1 | Table 4.2-11. Outdoor Air Mass Flow Rate (kgda/s) | 11 | Outdoor Air Mass Flow Rate (kgda/s) | Table 4.2-11. Outdoor Air Mass Flow Rate (kgda/s) | 4.2-11
Tables 1 | Table 4.2-12. Cooling Coil Outlet Air Temperature (°C) | 12 | Cooling Coil Outlet Air Temperature (°C) | Table 4.2-12. Cooling Coil Outlet Air Temperature (°C) | 4.2-12
Tables 1 | Table 4.2-13. Supply Air Temperature (°C) | 13 | Supply Air Temperature (°C) | Table 4.2-13. Supply Air Temperature (°C) | 4.2-13
Tables 1 | Table 4.2-14. Supply Air Humidity Ratio (g/gda) | 14 | Supply Air Humidity Ratio (g/gda) | Table 4.2-14. Supply Air Humidity Ratio (g/gda) | 4.2-14
Tables 1 | Table 4.2-15. Supply Air Specific Volume (L/kgda) | 15 | Supply Air Specific Volume (L/kgda) | Table 4.2-15. Supply Air Specific Volume (L/kgda) | 4.2-15
Tables 1 | Table 4.2-16. Supply Air Enthalpy (j/gda) | 16 | Supply Air Enthalpy (j/gda) | Table 4.2-16. Supply Air Enthalpy (j/gda) | 4.2-16
Tables 1 | Table 4.2-17. Supply Air Mass Flow Rate (kgda/s) | 17 | Supply Air Mass Flow Rate (kgda/s) | Table 4.2-17. Supply Air Mass Flow Rate (kgda/s) | 4.2-17
Tables 1 | Table 4.2-18. Zone 1 Supply Air Temperature (°C) | 18 | Zone 1 Supply Air Temperature (°C) | Table 4.2-18. Zone 1 Supply Air Temperature (°C) | 4.2-18
Tables 1 | Table 4.2-19. Zone 1 Air Temperature (°C) | 19 | Zone 1 Air Temperature (°C) | Table 4.2-19. Zone 1 Air Temperature (°C) | 4.2-19
Tables 1 | Table 4.2-20. Zone 1 Humidity Ratio (g/gda) | 20 | Zone 1 Humidity Ratio (g/gda) | Table 4.2-20. Zone 1 Humidity Ratio (g/gda) | 4.2-20
Tables 1 | Table 4.2-21. Zone 2 Air Temperature (°C) | 21 | Zone 2 Air Temperature (°C) | Table 4.2-21. Zone 2 Air Temperature (°C) | 4.2-21
Tables 1 | Table 4.2-22. Zone 2 Supply Air Temperature (°C) | 22 | Zone 2 Supply Air Temperature (°C) | Table 4.2-22. Zone 2 Supply Air Temperature (°C) | 4.2-22
Tables 1 | Table 4.2-23. Zone 2 Humidity Ratio (g/gda) | 23 | Zone 2 Humidity Ratio (g/gda) | Table 4.2-23. Zone 2 Humidity Ratio (g/gda) | 4.2-23
Tables 1 | Table 4.2-24. Supply Fan Air Temperature Rise (°C) | 24 | Supply Fan Air Temperature Rise (°C) | Table 4.2-24. Supply Fan Air Temperature Rise (°C) | 4.2-24
Tables 1 | Table 4.2-25. Return Fan Air Temperature Rise (°C) | 25 | Return Fan Air Temperature Rise (°C) | Table 4.2-25. Return Fan Air Temperature Rise (°C) | 4.2-25
Tables 1 | Table 4.2-26. Zone 1 Humidity Ratio Increase (g/gda) | 26 | Zone 1 Humidity Ratio Increase (g/gda) | Table 4.2-26. Zone 1 Humidity Ratio Increase (g/gda) | 4.2-26
Tables 1 | Table 4.2-27. Zone 2 Humidity Ratio Increase (g/gda) | 27 | Zone 2 Humidity Ratio Increase (g/gda) | Table 4.2-27. Zone 2 Humidity Ratio Increase (g/gda) | 4.2-27
Delta Tables 1 | Table 4.2-28. Delta Preheat Coil Load, CV - VAV (kWh/h) | 28 | Delta Preheat Coil Load, CV - VAV (kWh/h) | Table 4.2-28. Delta Preheat Coil Load, CV - VAV (kWh/h) | 4.2-28
Delta Tables 1 | Table 4.2-29. Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 29 | Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-29. Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 4.2-29
Delta Tables 1 | Table 4.2-30. Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 30 | Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-30. Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 4.2-30
Delta Tables 1 | Table 4.2-31. Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 31 | Delta Total Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-31. Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 4.2-31
Delta Tables 2 | Table 4.2-32. CV Delta Cooling Coil Load, Economizer - No Economizer Operation (kWh/h) | 32 | CV Delta Cooling Coil Load, Economizer - No Economizer Operation (kWh/h) | Table 4.2-32. CV Delta Cooling Coil Load, Economizer - No Economizer Operation (kWh/h) | 4.2-32
Delta Tables 2 | Table 4.2-33. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 33 | VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Table 4.2-33. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 4.2-33

## Tables 1
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445
Table B16.7.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 19.2067
AE303 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 10.9704
AE304 | 19.0908 | 19.0527 | 19.2794 | 18.1695 | 19.1753 | 18.996 | 19.0917 | 19.4445
AE305 | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.764
AE306 | 19.0892 | 19.0285 | 19.24 | 18.4116 | 19.1067 | 18.957 | 19.0823 | 28.4234
AE326 | 25.4875 | 25.4099 | 25.4312 | 24.358 | 25.395 | 25.208 | 25.5104 | 34.4774
AE345 | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0565
AE401 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163 | 19.7482
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098
AE404 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076 | 13.7744
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987
AE406 | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187 | 8.4392
AE426 | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045 | 8.9171
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393
Table B16.7.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 19.2067
AE303 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 10.9704
AE304 | 12.8325 | 12.7579 | 12.2686 | 11.9555 | 12.5536 | 12.368 | 12.8301 | 12.4735
AE305 | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.764
AE306 | 13.646 | 13.5844 | 13.1365 | 12.9778 | 13.3578 | 13.206 | 13.6388 | 22.3751
AE326 | 13.1857 | 13.0657 | 12.552 | 12.6457 | 12.8634 | 12.65 | 13.2051 | 21.8388
AE345 | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0565
AE401 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163 | 19.7482
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098
AE404 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862 | 7.2943
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987
AE406 | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296 | 3.5461
AE426 | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849 | 3.4927
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393
Table B16.7.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 2.947 | 2.9697 | 3.58 | 3.7882 | 3.5747 | 3.647 | 2.9467 | 3.5822
AE303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE401 | 10.2597 | 10.2479 | 10.31 | 10.8176 | 10.343 | 10.451 | 10.2578 | 10.3476
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-4. CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.4549
AE304 | 16.5785 | 16.5503 | 17.0695 | 16.1037 | 16.778 | 16.662 | 16.5765 | 17.0541
AE305 | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1982
AE306 | 14.3643 | 14.3129 | 14.8022 | 14.0314 | 14.4926 | 14.403 | 14.3584 | 14.7392
AE326 | 20.7626 | 20.6943 | 20.9933 | 19.9438 | 20.7797 | 20.654 | 20.7757 | 20.7871
AE345 | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5096
AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098
AE404 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076 | 13.7744
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987
AE406 | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187 | 8.4392
AE426 | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045 | 8.9171
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393
Table B16.7.2-5. CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.4549
AE304 | 10.3202 | 10.2556 | 10.0587 | 9.8897 | 10.1563 | 10.034 | 10.315 | 10.0831
AE305 | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1982
AE306 | 8.9211 | 8.8688 | 8.6987 | 8.5975 | 8.7437 | 8.652 | 8.9149 | 8.6909
AE326 | 8.4609 | 8.3501 | 8.1141 | 8.2315 | 8.2481 | 8.096 | 8.4705 | 8.1485
AE345 | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5096
AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098
AE404 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862 | 7.2943
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987
AE406 | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296 | 3.5461
AE426 | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849 | 3.4927
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393
Table B16.7.2-6. CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 | 6.2583 | 6.2947 | 7.0108 | 6.214 | 6.6217 | 6.629 | 6.2615 | 6.9711
AE305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 | 5.4432 | 5.4441 | 6.1035 | 5.4338 | 5.7489 | 5.75 | 5.4435 | 6.0483
AE326 | 12.3018 | 12.3442 | 12.8792 | 11.7123 | 12.5316 | 12.558 | 12.3053 | 12.6386
AE345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.638e-15
AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5791e-17
AE404 | 5.9242 | 5.9745 | 6.5805 | 5.9168 | 6.3173 | 6.313 | 5.9214 | 6.48
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0316e-16
AE406 | 4.5879 | 4.6068 | 4.9686 | 4.4948 | 4.84 | 4.868 | 4.5892 | 4.8931
AE426 | 5.2366 | 5.2655 | 5.6327 | 5.1885 | 5.3897 | 5.456 | 5.2196 | 5.4244
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0633e-16
Table B16.7.2-7. CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 7.7129 | 7.7075 | 7.4721 | 7.706 | 7.5057 | 7.539 | 7.7093 | 7.501
AE303 | 2.2584 | 2.2547 | 2.1363 | 2.15 | 2.1827 | 2.188 | 2.2552 | 2.171
AE304 | 0.99332 | 0.98884 | 0.85904 | 0.79774 | 0.94208 | 0.915 | 0.99153 | 0.93938
AE305 | 2.2598 | 2.2561 | 2.1367 | 2.0723 | 2.193 | 2.188 | 2.2567 | 2.1923
AE306 | 2.2625 | 2.2588 | 2.1374 | 2.1107 | 2.2136 | 2.188 | 2.2618 | 6.603
AE326 | 2.2625 | 2.2588 | 2.1374 | 2.1256 | 2.2141 | 2.188 | 2.2668 | 6.6056
AE345 | 2.2587 | 2.255 | 2.1374 | 2.0887 | 2.1849 | 2.188 | 2.2607 | 2.1841
AE401 | 4.4994 | 4.4963 | 4.5019 | 4.5839 | 4.5034 | 4.524 | 4.4895 | 4.5018
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-8. CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 8.3889 | 8.3822 | 8.0774 | 8.3763 | 8.1309 | 8.17 | 8.3843 | 8.1235
AE303 | 2.4572 | 2.4515 | 2.3 | 2.3194 | 2.3607 | 2.366 | 2.4545 | 2.3444
AE304 | 1.519 | 1.5135 | 1.3509 | 1.2681 | 1.4552 | 1.419 | 1.5236 | 1.451
AE305 | 2.4589 | 2.4532 | 2.3017 | 2.2232 | 2.3739 | 2.366 | 2.4562 | 2.3735
AE306 | 2.4624 | 2.4568 | 2.3004 | 2.2695 | 2.4005 | 2.366 | 2.4621 | 7.0813
AE326 | 2.4624 | 2.4568 | 2.3005 | 2.2886 | 2.4012 | 2.366 | 2.4678 | 7.0847
AE345 | 2.4575 | 2.4518 | 2.3005 | 2.2414 | 2.3635 | 2.366 | 2.461 | 2.3628
AE401 | 4.8772 | 4.8725 | 4.891 | 5.0147 | 4.9022 | 4.926 | 4.8689 | 4.8988
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-9. CV/VAV Outdoor Air Temperature (°F)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE303 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE304 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9
AE305 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
AE306 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE326 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE345 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
AE401 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE403 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE404 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9
AE405 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
AE406 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE426 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE445 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
Table B16.7.2-10. CV/VAV Outdoor Air Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901
AE303 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | 0.0029334
AE304 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | 0.016772
AE305 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481
AE306 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566
AE326 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566
AE345 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481
AE401 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901
AE403 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | 0.0029334
AE404 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | 0.016772
AE405 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481
AE406 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566
AE426 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566
AE445 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481
Table B16.7.2-11. CV/VAV Outdoor Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.28139 | 0.28143 | 0.28316 | 0.29649 | 0.28418 | 0.28316 | 0.2814 | 0.28416
AE303 | 0.27809 | 0.27814 | 0.28316 | 0.28151 | 0.28418 | 0.28316 | 0.27808 | 0.28416
AE304 | 0.27554 | 0.27557 | 0.28316 | 0.2735 | 0.28418 | 0.28316 | 0.27553 | 0.28416
AE305 | 0.2774 | 0.27745 | 0.28316 | 0.27741 | 0.28418 | 0.28316 | 0.27739 | 0.28416
AE306 | 0.27605 | 0.27609 | 0.28316 | 0.27538 | 0.28418 | 0.28316 | 0.27604 | 0.28416
AE326 | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73881
AE345 | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.73881
AE401 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814 | 0.28416
AE403 | 0.27809 | 0.27814 | 0.28316 | 0.28597 | 0.28418 | 0.28316 | 0.27808 | 0.28416
AE404 | 0.27533 | 0.27537 | 0.28316 | 0.27289 | 0.28418 | 0.28316 | 0.27532 | 0.28419
AE405 | 0.2774 | 0.27745 | 0.28316 | 0.27761 | 0.28418 | 0.28316 | 0.27739 | 0.28419
AE406 | 0.27552 | 0.27556 | 0.28316 | 0.27474 | 0.28418 | 0.28316 | 0.27552 | 0.28419
AE426 | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133 | 0.3317
AE445 | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411 | 0.33468
Table B16.7.2-12. CV/VAV Cooling Coil Outlet Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.22 | 7.22 | 7.22 | 7.2222
AE303 | 12.2066 | 12.2059 | 12.2049 | 12.1667 | 12.197 | 12.199 | 12.215 | 12.1941
AE304 | 12.2072 | 12.2065 | 12.2047 | 12.2222 | 12.2012 | 12.199 | 12.2114 | 12.1999
AE305 | 12.2068 | 12.2061 | 12.2049 | 12.2778 | 12.1989 | 12.199 | 12.2132 | 12.197
AE306 | 12.2072 | 12.2065 | 12.1759 | 12.2222 | 12.2019 | 12.199 | 12.2138 | 12.1999
AE326 | 12.2072 | 12.2065 | 12.2038 | 12.2222 | 12.2017 | 12.199 | 12.2 | 12.2005
AE345 | 12.2066 | 12.2059 | 12.2049 | 12.2222 | 12.197 | 12.199 | 12.2 | 12.1957
AE401 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.2031 | 7.22 | 7.22 | 7.2222
AE403 | 12.6643 | 12.6466 | 12.6699 | 12.6667 | 12.6598 | 12.66 | 12.6692 | 12.6915
AE404 | 12.4805 | 12.4612 | 12.4633 | 12.4444 | 12.4725 | 12.47 | 12.491 | 12.5624
AE405 | 12.6644 | 12.6468 | 12.6704 | 12.6667 | 12.661 | 12.66 | 12.6697 | 12.6927
AE406 | 12.6647 | 12.6472 | 12.6693 | 12.6667 | 12.6637 | 12.66 | 12.6584 | 12.6947
AE426 | 12.6647 | 12.6472 | 12.6574 | 12.6667 | 12.6638 | 12.66 | 12.67 | 12.6949
AE445 | 12.6644 | 12.6519 | 12.6704 | 12.6667 | 12.6608 | 12.66 | 12.67 | 12.6925
Table B16.7.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 24.7331 | 24.7328 |  | 23.9613 | 23.8906 | 24.65 | 24.6351 | 23.8892
AE303 | 48.1495 | 47.6873 | 48.22 | 47.9247 | 47.4569 | 48.02 | 48.1783 | 33.4715
AE304 | 100 | 99.9992 | 95.49 | 100 | 99.1258 | 100 | 100 | 94.7543
AE305 | 65.719 | 65.3364 | 65.84 | 65.5319 | 64.909 | 65.57 | 65.7465 | 64.9185
AE306 | 100 | 99.9992 | 96.21 | 100 | 99.2475 | 100 | 100 | 95.3924
AE326 | 100 | 99.9992 | 98.89 | 100 | 99.9275 | 100 | 100 | 99.8848
AE345 | 51.0891 | 50.7067 | 51.33 | 51.1359 | 50.9944 | 51.1 | 51.1113 | 50.9986
AE401 | 4.1447 | 4.1474 |  | 4.8015 | 4.1501 | 4.17 | 4.1464 | 4.1447
AE403 | 36.3949 | 36.0086 | 36.39 | 34.2896 | 35.8492 | 35.98 | 36.3722 | 32.3951
AE404 | 100 | 99.9992 | 97.24 | 100 | 98.7059 | 100 | 100 | 96.7661
AE405 | 53.4629 | 53.1717 | 53.52 | 51.8548 | 52.7786 | 53.05 | 53.4325 | 52.6788
AE406 | 100 | 99.9992 | 99.38 | 100 | 99.7649 | 100 | 100 | 99.3471
AE426 | 100 | 99.9992 | 99.58 | 100 | 99.9528 | 100 | 100 | 99.8844
AE445 | 49.575 | 49.2421 | 49.78 | 49.664 | 49.4632 | 49.58 | 49.5567 | 49.3605
Table B16.7.2-14. CV/VAV Supply Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.5616 | 0.56226 | 0.5899 | 0.55556 | 0.58627 | 0.5818 | 0.56149 | 0.58528
AE303 | 0.57122 | 0.57189 | 0.5899 | 0.61111 | 0.58339 | 0.5818 | 0.57113 | 0.58373
AE304 | 0.5706 | 0.57126 | 0.5899 | 0.61111 | 0.5785 | 0.5818 | 0.5705 | 0.57794
AE305 | 0.57101 | 0.57168 | 0.5899 | 0.61111 | 0.58174 | 0.5818 | 0.57091 | 0.58075
AE306 | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57849 | 0.5818 | 0.5705 | 0.57788
AE326 | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57843 | 0.5818 | 0.57048 | 0.57745
AE345 | 0.57119 | 0.57185 | 0.5899 | 0.55556 | 0.58306 | 0.5818 | 0.57106 | 0.58207
AE401 | 0.074611 | 0.086087 | 0.087254 | 0.055556 | 0.086922 | 0.0903 | 0.074852 | 0.062638
AE403 | 0.1135 | 0.13116 | 0.1251 | 0.11111 | 0.1202 | 0.1195 | 0.11296 | 0.086298
AE404 | 0.29723 | 0.31661 | 0.32831 | 0.33333 | 0.30715 | 0.3146 | 0.29011 | 0.2154
AE405 | 0.11338 | 0.13101 | 0.12457 | 0.11111 | 0.11918 | 0.1195 | 0.11281 | 0.085036
AE406 | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11634 | 0.1195 | 0.11249 | 0.083039
AE426 | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11633 | 0.1195 | 0.11216 | 0.083061
AE445 | 0.1134 | 0.12586 | 0.12457 | 0.11111 | 0.11933 | 0.1195 | 0.11252 | 0.085232
Table B16.7.2-15. CV/VAV Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 7.7838 | 7.7845 | 7.8099 | 7.7778 | 7.8063 | 7.8018 | 7.7815 | 7.8075
AE303 | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.7804 | 12.7808 | 12.7861 | 12.7778
AE304 | 12.7778 | 12.7778 | 12.7946 | 12.8333 | 12.7797 | 12.7808 | 12.7819 | 12.7778
AE305 | 12.7778 | 12.7778 | 12.7948 | 12.8889 | 12.7806 | 12.7808 | 12.7841 | 12.7778
AE306 | 12.7778 | 12.7778 | 12.7658 | 12.7778 | 12.7804 | 12.7808 | 12.7843 | 12.7778
AE326 | 12.7778 | 12.7778 | 12.7937 | 12.7778 | 12.7801 | 12.7808 | 12.7705 | 12.778
AE345 | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.78 | 12.7808 | 12.7711 | 12.7778
AE401 | 7.2968 | 7.3083 | 7.3073 | 7.2778 | 7.2901 | 7.3103 | 7.2949 | 7.2849
AE403 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.78 | 12.7795 | 12.7822 | 12.7778
AE404 | 12.7778 | 12.7778 | 12.7916 | 12.7778 | 12.7797 | 12.7846 | 12.7811 | 12.7778
AE405 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825 | 12.7778
AE406 | 12.7778 | 12.7778 | 12.7939 | 12.7778 | 12.78 | 12.7795 | 12.7709 | 12.7778
AE426 | 12.7778 | 12.7778 | 12.782 | 12.7778 | 12.7801 | 12.7795 | 12.7822 | 12.778
AE445 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825 | 12.7778
Table B16.7.2-16. CV/VAV Supply Air Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014958
AE303 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0029334
AE304 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0083798
AE305 | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0057159
AE306 | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.008437
AE326 | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0088403
AE345 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481
AE401 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901
AE403 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | 0.0029334
AE404 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009017 | 0.0087695
AE405 | 0.0048458 | 0.004814 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | 0.0047847
AE406 | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091064 | 0.009175 | 0.0091221 | 0.0090865
AE426 | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.0091238 | 0.009184 | 0.0091292 | 0.0091365
AE445 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481
Table B16.7.2-17. CV/VAV Supply Air Specific Volume (L/kgda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 797.8282 | 797.7263 | 833.33 |  | 830.3519 |  | 793.9174 | 797.9222
AE303 | 815.504 | 815.3446 | 833.33 |  | 830.3519 |  | 811.5517 | 813.9103
AE304 | 821.5223 | 821.4151 | 833.33 |  | 830.3519 |  | 817.5256 | 821.0038
AE305 | 817.5333 | 817.3825 | 833.33 |  | 830.3519 |  | 813.5654 | 817.5342
AE306 | 821.5223 | 821.4151 | 833.33 |  | 830.3519 |  | 817.5341 | 821.0783
AE326 | 821.5223 | 821.4151 | 833.33 |  | 830.3519 |  | 817.4842 | 821.6042
AE345 | 815.8428 | 815.6925 | 833.33 |  | 830.3519 |  | 811.8397 | 815.9259
AE401 | 794.7981 | 794.7275 | 833.33 |  | 830.3519 |  | 794.2783 | 794.858
AE403 | 814.2796 | 814.1232 | 833.33 |  | 830.3519 |  | 813.5066 | 813.9103
AE404 | 821.7345 | 821.6126 | 833.33 |  | 830.3519 |  | 819.6593 | 821.5114
AE405 | 816.3051 | 816.1571 | 833.33 |  | 830.3519 |  | 815.5201 | 816.3214
AE406 | 821.8794 | 821.7587 | 833.33 |  | 830.3519 |  | 821.0663 | 821.9243
AE426 | 821.8794 | 821.7587 | 833.33 |  | 830.3519 |  | 821.1102 | 821.99
AE445 | 815.8428 | 815.6925 | 833.33 |  | 830.3519 |  | 815.0746 | 815.9259
Table B16.7.2-18. CV/VAV Supply Air Enthalpy (J/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 11.726 |  | 11.71 |  | 11.6064 |  | 11.7069 | 11.608
AE303 | 23.5371 |  | 23.55 |  | 23.3653 |  | 23.5569 | 20.2456
AE304 | 35.2043 |  | 34.16 |  | 34.9895 |  | 35.2138 | 33.996
AE305 | 27.4712 |  | 27.49 |  | 27.2729 |  | 27.489 | 27.2704
AE306 | 35.2043 |  | 34.26 |  | 35.0189 |  | 35.2197 | 34.1405
AE326 | 35.2043 |  | 34.93 |  | 35.1723 |  | 35.185 | 35.159
AE345 | 24.194 |  | 24.24 |  | 24.155 |  | 24.186 | 24.1529
AE401 | 7.9923 |  | 8 |  | 7.9766 |  | 7.9897 | 7.9714
AE403 | 21.1635 |  | 21.16 |  | 21.0244 |  | 21.1625 | 20.2456
AE404 | 35.6156 |  | 34.93 |  | 35.2972 |  | 35.6235 | 34.98
AE405 | 25.0901 |  | 25.1 |  | 24.9195 |  | 25.0664 | 24.9194
AE406 | 35.8965 |  | 35.74 |  | 35.8327 |  | 35.8787 | 35.7803
AE426 | 35.8965 |  | 35.76 |  | 35.8769 |  | 35.908 | 35.9068
AE445 | 24.194 |  | 24.24 |  | 24.1552 |  | 24.1977 | 24.1529
Table B16.7.2-19. CV/VAV Supply Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.77054 | 0.77064 | 0.73624 | 0.77088 | 0.73888 | 0.73624 | 0.77055 | 0.73881
AE303 | 0.75384 | 0.75399 | 0.73624 | 0.73193 | 0.73888 | 0.73624 | 0.7538 | 0.73881
AE304 | 0.74832 | 0.74842 | 0.73624 | 0.71109 | 0.73888 | 0.73624 | 0.74829 | 0.73881
AE305 | 0.75197 | 0.75211 | 0.73624 | 0.72126 | 0.73888 | 0.73624 | 0.75194 | 0.73881
AE306 | 0.74832 | 0.74842 | 0.73624 | 0.716 | 0.73888 | 0.73624 | 0.74829 | 0.73881
AE326 | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73881
AE345 | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.73881
AE401 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814 | 0.28416
AE403 | 0.33569 | 0.33612 | 0.3385 | 0.33688 | 0.3351 | 0.33354 | 0.33495 | 0.33634
AE404 | 0.53919 | 0.53988 | 0.54925 | 0.53541 | 0.53845 | 0.54137 | 0.53882 | 0.53949
AE405 | 0.33473 | 0.33516 | 0.33832 | 0.33591 | 0.33415 | 0.33354 | 0.33393 | 0.33437
AE406 | 0.33213 | 0.33253 | 0.33835 | 0.32968 | 0.33145 | 0.33354 | 0.33137 | 0.33164
AE426 | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133 | 0.3317
AE445 | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411 | 0.33468
Table B16.7.2-20. CV/VAV Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.36519 | 0.36519 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36519 | 0.38462
AE303 | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38462
AE304 | 0.36821 | 0.36821 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36821 | 0.38462
AE305 | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38462
AE306 | 0.3689 | 0.3689 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.3689 | 0.38462
AE326 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE345 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE401 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99999 | 1
AE403 | 0.82841 | 0.82752 | 0.83653 | 0.8489 | 0.84805 | 0.84895 | 0.83021 | 0.84486
AE404 | 0.51064 | 0.51006 | 0.51555 | 0.50968 | 0.52778 | 0.52304 | 0.51097 | 0.52677
AE405 | 0.82871 | 0.82782 | 0.83698 | 0.82645 | 0.85046 | 0.84895 | 0.83068 | 0.84992
AE406 | 0.82954 | 0.82866 | 0.83688 | 0.83333 | 0.85738 | 0.84895 | 0.83144 | 0.85693
AE426 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE445 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Table B16.7.2-21. CV/VAV Zone 1 Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 29.2787 | 29.2883 | 29.6699 |  | 29.649 | 29.5754 | 29.27 | 29.6391
AE303 | 19.1796 | 19.1761 | 19.05 |  | 19.1013 | 19.1006 | 19.18 | 19.0797
AE304 | 15.5904 | 15.5808 | 15.3101 |  | 15.485 | 15.4247 | 15.59 | 15.4775
AE305 | 19.1811 | 19.1778 | 19.0515 |  | 19.1133 | 19.1006 | 19.18 | 19.1092
AE306 | 19.1841 | 19.1807 | 19.0246 |  | 19.1369 | 19.1006 | 19.19 | 31.7525
AE326 | 19.1841 | 19.1807 | 19.0525 |  | 19.1373 | 19.1006 | 19.19 | 31.7464
AE345 | 19.1799 | 19.1765 | 19.0515 |  | 19.1037 | 19.1006 | 19.18 | 19.0996
AE401 | 46.92 | 46.9483 | 46.8548 |  | 46.6969 | 46.5047 | 46.8281 | 46.6818
AE403 | 12.7778 | 12.7777 | 12.795 |  | 12.78 | 12.7795 | 12.7822 | 12.7781
AE404 | 12.7778 | 12.7777 | 12.7916 |  | 12.7808 | 12.7846 | 12.7878 | 12.7846
AE405 | 12.7778 | 12.7777 | 12.795 |  | 12.7802 | 12.7795 | 12.7825 | 12.7778
AE406 | 12.7778 | 12.7777 | 12.7939 |  | 12.7899 | 12.7795 | 12.7709 | 12.7783
AE426 | 12.7778 | 12.7777 | 12.782 |  | 12.79 | 12.7795 | 12.7822 | 12.778
AE445 | 12.7778 | 12.7778 | 12.795 |  | 12.7802 | 12.7795 | 12.7825 | 12.7862
Table B16.7.2-22. CV/VAV Zone 1 Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1299 | 21.1106 | 21.1102 | 21.1199
AE303 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3285 | 23.3333
AE304 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.8914 | 23.8893 | 23.8806 | 23.89
AE305 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3269 | 23.3359
AE306 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3339 | 23.341
AE326 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3337 | 23.341
AE345 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.328 | 23.3359
AE401 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1452 | 21.1103 | 21.1151 | 21.1299
AE403 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3302 | 23.3333
AE404 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.9001 | 23.8934 | 23.8829 | 23.8864
AE405 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3319 | 23.3304
AE406 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.318 | 23.3304
AE426 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3286 | 23.3304
AE445 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3321 | 23.3304
Table B16.7.2-23. CV/VAV Zone 1 Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.0021971 | 0.0021972 | 0.0022251 |  | 0.0021723 | 0.002253 | 0.0021868 | 0.0021725
AE303 | 0.0048927 | 0.0048518 | 0.0049298 |  | 0.0048436 | 0.004938 | 0.0048998 | 0.0029334
AE304 | 0.0095185 | 0.0095186 | 0.00914 |  | 0.0094477 | 0.009595 | 0.0095252 | 0.0090551
AE305 | 0.0064526 | 0.0064187 | 0.0064918 |  | 0.0063912 | 0.006499 | 0.0064597 | 0.0063915
AE306 | 0.0095187 | 0.0095189 | 0.00919 |  | 0.0094593 | 0.009592 | 0.0095248 | 0.0091126
AE326 | 0.0095187 | 0.0095189 | 0.0094417 |  | 0.0095202 | 0.009613 | 0.0095166 | 0.0095159
AE345 | 0.0051532 | 0.0051194 | 0.0052044 |  | 0.0051565 | 0.005212 | 0.0051553 | 0.0051566
AE401 | 0.002304 | 0.0023034 | 0.0023324 |  | 0.0022887 | 0.002374 | 0.0022691 | 0.0022891
AE403 | 0.0049701 | 0.00493 | 0.0049958 |  | 0.0049254 | 0.005021 | 0.0049882 | 0.0029334
AE404 | 0.0099076 | 0.0098953 | 0.0096515 |  | 0.009788 | 0.00998 | 0.0099213 | 0.0096746
AE405 | 0.0065301 | 0.006497 | 0.0065572 |  | 0.0064728 | 0.006582 | 0.0065372 | 0.0064717
AE406 | 0.010823 | 0.010812 | 0.010775 |  | 0.010803 | 0.010931 | 0.010838 | 0.010785
AE426 | 0.010823 | 0.010812 | 0.010787 |  | 0.010825 | 0.01094 | 0.010844 | 0.010837
AE445 | 0.0061741 | 0.0061387 | 0.0062162 |  | 0.0061691 | 0.006264 | 0.0061921 | 0.0061658
Table B16.7.2-24. CV/VAV Zone 2 Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 27.8228 | 27.8298 | 28.084 |  | 28.0886 | 28.026 | 27.81 | 28.0732
AE303 | 18.7479 | 18.7408 | 18.57 |  | 18.6401 | 18.637 | 18.75 | 18.6109
AE304 | 16.4644 | 16.4551 | 16.1852 |  | 16.3615 | 16.2939 | 16.48 | 16.3522
AE305 | 18.75 | 18.7428 | 18.572 |  | 18.6566 | 18.6371 | 18.75 | 18.6531
AE306 | 18.7541 | 18.747 | 18.5398 |  | 18.6889 | 18.6371 | 18.76 | 30.2201
AE326 | 18.7541 | 18.747 | 18.5677 |  | 18.6896 | 18.637 | 18.76 | 30.2159
AE345 | 18.7483 | 18.7411 | 18.572 |  | 18.6434 | 18.6371 | 18.75 | 18.64
AE401 | 36.0391 | 36.0548 | 35.9521 |  | 35.8886 | 35.7662 | 35.9884 | 35.8658
AE403 | 12.7778 | 12.7777 | 12.795 |  | 12.78 | 12.7795 | 12.7822 | 12.7781
AE404 | 12.7778 | 12.7777 | 12.7916 |  | 12.7808 | 12.7846 | 12.7878 | 12.7846
AE405 | 12.7778 | 12.7777 | 12.795 |  | 12.7802 | 12.7795 | 12.7825 | 12.7778
AE406 | 12.7778 | 12.7777 | 12.7939 |  | 12.7899 | 12.7795 | 12.7709 | 12.7783
AE426 | 12.7778 | 12.7777 | 12.782 |  | 12.79 | 12.7795 | 12.7822 | 12.778
AE445 | 12.7778 | 12.7778 | 12.795 |  | 12.7802 | 12.7795 | 12.7825 | 12.7862
Table B16.7.2-25. CV/VAV Zone 2 Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2485 | 22.221 | 22.2171 | 22.2336
AE303 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4389 | 24.4444
AE304 | 25 | 25 | 25 | 25 | 25.0047 | 25.001 | 25.0027 | 25.002
AE305 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4367 | 24.4477
AE306 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4427 | 24.4542
AE326 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4424 | 24.4542
AE345 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4382 | 24.4477
AE401 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2593 | 22.2208 | 22.2211 | 22.2381
AE403 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4608 | 24.4431 | 24.4386 | 24.4444
AE404 | 25 | 25 | 25 | 25 | 25.0168 | 25.0043 | 24.9989 | 24.9961
AE405 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4401 | 24.4403
AE406 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4432 | 24.431 | 24.4403
AE426 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4416 | 24.4403
AE445 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.442 | 24.4403
Table B16.7.2-26. CV/VAV Zone 2 Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.0023817 | 0.0023819 | 0.0024213 |  | 0.0023649 | 0.002454 | 0.0023719 | 0.0023652
AE303 | 0.0050812 | 0.0050403 | 0.0051345 |  | 0.0050359 | 0.005139 | 0.0050898 | 0.0029334
AE304 | 0.0097082 | 0.0097084 | 0.00934 |  | 0.00964 | 0.009796 | 0.0097162 | 0.0092474
AE305 | 0.0066415 | 0.0066076 | 0.0066965 |  | 0.0065835 | 0.0067 | 0.0066501 | 0.0065838
AE306 | 0.0097086 | 0.0097087 | 0.00939 |  | 0.0096517 | 0.009793 | 0.0097161 | 0.0093049
AE326 | 0.0097086 | 0.0097087 | 0.00965 |  | 0.0097126 | 0.009814 | 0.009708 | 0.0097083
AE345 | 0.0053417 | 0.0053078 | 0.0054091 |  | 0.0053488 | 0.005413 | 0.0053453 | 0.005349
AE401 | 0.0023101 | 0.0023096 | 0.0023296 |  | 0.0022872 | 0.002374 | 0.0022892 | 0.0022874
AE403 | 0.0050294 | 0.0049886 | 0.0050706 |  | 0.0049851 | 0.005084 | 0.0050489 | 0.0029334
AE404 | 0.010241 | 0.010229 | 0.0099979 |  | 0.010124 | 0.010327 | 0.010261 | 0.010009
AE405 | 0.0065896 | 0.0065555 | 0.006633 |  | 0.0065327 | 0.006645 | 0.006598 | 0.0065313
AE406 | 0.010883 | 0.010871 | 0.010849 |  | 0.010863 | 0.010994 | 0.0109 | 0.010845
AE426 | 0.010883 | 0.010871 | 0.010861 |  | 0.010885 | 0.011003 | 0.010906 | 0.010897
AE445 | 0.0062336 | 0.0061973 | 0.006292 |  | 0.006229 | 0.006327 | 0.006253 | 0.0062255
Table B16.7.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.23072 | 0.23076 | 0.23474 |  | 0.23073 | 0.23922 | 0.22932 | 0.23075
AE303 | 0.23034 | 0.23034 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0
AE304 | 0.23025 | 0.23026 | 0.23699 |  | 0.23026 | 0.23922 | 0.23168 | 0.23028
AE305 | 0.23034 | 0.23035 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.23037
AE306 | 0.23034 | 0.23035 | 0.23732 |  | 0.23036 | 0.23922 | 0.23106 | 0.23037
AE326 | 0.23034 | 0.23035 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.23037
AE345 | 0.23034 | 0.23035 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.23037
AE401 | 0.23072 | 0.23071 | 0.23474 |  | 0.23073 | 0.23923 | 0.22628 | 0.23074
AE403 | 0.23034 | 0.23038 | 0.23627 |  | 0.23035 | 0.23924 | 0.23249 | 0
AE404 | 0.23025 | 0.23022 | 0.23715 |  | 0.23026 | 0.23924 | 0.23217 | 0.23028
AE405 | 0.23034 | 0.23035 | 0.23595 |  | 0.23035 | 0.23924 | 0.23217 | 0.23037
AE406 | 0.23034 | 0.23034 | 0.23595 |  | 0.23035 | 0.23924 | 0.23235 | 0.23037
AE426 | 0.23034 | 0.23034 | 0.23595 |  | 0.23035 | 0.23924 | 0.23216 | 0.23037
AE445 | 0.23034 | 0.23035 | 0.23583 |  | 0.23035 | 0.23924 | 0.23216 | 0.23037
[(Zone Supply Air Mass Flow) × {(Zone Humidity Ratio) – (Zone Supply Air Humidity Ratio )} × 1000 g/kg]
Table B16.7.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.34579 | 0.34587 | 0.35162 |  | 0.34583 | 0.35877 | 0.34437 | 0.34584
AE303 | 0.34523 | 0.34524 | 0.35644 |  | 0.34527 | 0.35877 | 0.34672 | 0
AE304 | 0.34509 | 0.34513 | 0.35577 |  | 0.34513 | 0.35877 | 0.34731 | 0.34514
AE305 | 0.34523 | 0.34522 | 0.35644 |  | 0.34527 | 0.35877 | 0.34672 | 0.34528
AE306 | 0.34523 | 0.34527 | 0.35616 |  | 0.34527 | 0.35877 | 0.34672 | 0.34528
AE326 | 0.34523 | 0.34527 | 0.35784 |  | 0.34527 | 0.35877 | 0.34672 | 0.34528
AE345 | 0.34523 | 0.34522 | 0.35644 |  | 0.34527 | 0.35877 | 0.34672 | 0.34528
AE401 | 0.34579 | 0.3458 | 0.35162 |  | 0.34583 | 0.35883 | 0.34226 | 0.34584
AE403 | 0.34523 | 0.3453 | 0.35691 |  | 0.34527 | 0.35889 | 0.34873 | 0
AE404 | 0.34509 | 0.34509 | 0.35765 |  | 0.34513 | 0.35899 | 0.34827 | 0.34514
AE405 | 0.34523 | 0.34522 | 0.35644 |  | 0.34527 | 0.35889 | 0.34827 | 0.34528
AE406 | 0.34523 | 0.34525 | 0.35644 |  | 0.34527 | 0.35889 | 0.34853 | 0.34528
AE426 | 0.34523 | 0.34525 | 0.35644 |  | 0.34527 | 0.35889 | 0.34827 | 0.34528
AE445 | 0.34523 | 0.34522 | 0.35663 |  | 0.34527 | 0.35889 | 0.34827 | 0.34528
[(Zone Supply Air Mass Flow) × {(Zone Humidity Ratio) – (Zone Supply Air Humidity Ratio )} × 1000 g/kg]
Table B16.7.2-29. CV/VAV Return Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 | 0.34819 | 0.29556 | 0.29495 |  | 0.29272 | 0.2909 | 0.34804 | 0.29222
AE303 | 0.33958 | 0.2976 | 0.29495 |  | 0.29128 | 0.2909 | 0.3394 | 0.29186
AE304 | 0.34187 | 0.29783 | 0.29495 |  | 0.28885 | 0.2909 | 0.34171 | 0.28856
AE305 | 0.33946 | 0.29749 | 0.29495 |  | 0.29046 | 0.2909 | 0.33927 | 0.28997
AE306 | 0.33921 | 0.29727 | 0.29495 |  | 0.28884 | 0.2909 | 0.33905 | 0.28853
AE326 | 0.33921 | 0.29727 | 0.29495 |  | 0.28881 | 0.2909 | 0.33911 | 0.28832
AE345 | 0.33956 | 0.29758 | 0.29495 |  | 0.29112 | 0.2909 | 0.33943 | 0.29062
AE401 | [7 empty] | 0.2012
AE403 | 0.0049809 | 0.030526 | 0.004395 |  | 0.0038467 | 0.0117 | 0.0048549 | 0.20096
AE404 | 0.10655 | 0.11411 | 0.10173 |  | 0.090258 | 0.0986 | 0.10623 | 0.19845
AE405 | 0.0049578 | 0.0068611 | 0.004371 |  | 0.0037075 | 0.0117 | 0.0048189 | 0.19971
AE406 | 0.0048953 | 0.0067188 | 0.004377 |  | 0.0031146 | 0.0117 | 0.0047643 | 0.19809
AE426 | 0.0048953 | 0.0067188 | 0.004377 |  | 0.0031131 | 0.0116 | 0.0047598 | 0.20143
AE445 | 0.0049631 | 0.0068735 | 0.004371 |  | 0.0036902 | 0.0117 | 0.0048202 | 0.19976

## Delta Tables 1
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445
Table B16.7.2-30. CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 - AE401 | -7.3127 | -7.2782 | -6.73 | -7.0293 | -6.7682 | -6.804 | -7.3112 | -6.7654
AE303 - AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 - AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE305 - AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 - AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE326 - AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE345 - AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-31. CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 - AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 - AE403 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278 | 5.0452
AE304 - AE404 | 2.9212 | 2.8821 | 2.6085 | 2.431 | 2.7857 | 2.701 | 2.9287 | 2.7887
AE305 - AE405 | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824 | 5.0995
AE306 - AE406 | 5.2857 | 5.2594 | 5.0718 | 4.9174 | 5.1602 | 5.085 | 5.2853 | 5.1447
AE326 - AE426 | 4.867 | 4.7915 | 4.5396 | 4.5892 | 4.7066 | 4.58 | 4.8855 | 4.6557
AE345 - AE445 | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625 | 5.3703
Table B16.7.2-32. CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 - AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 - AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5791e-17
AE304 - AE404 | 0.33412 | 0.32027 | 0.43027 | 0.29717 | 0.30444 | 0.316 | 0.34014 | 0.49105
AE305 - AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0316e-16
AE306 - AE406 | 0.85526 | 0.83731 | 1.1349 | 0.939 | 0.90886 | 0.882 | 0.85438 | 1.1552
AE326 - AE426 | 7.0651 | 7.0787 | 7.2465 | 6.5238 | 7.1418 | 7.102 | 7.0857 | 7.2143
AE345 - AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0316e-15
Table B16.7.2-33. CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
AE301 - AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 - AE403 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278 | 5.0452
AE304 - AE404 | 3.2553 | 3.2024 | 3.0388 | 2.7282 | 3.0902 | 3.017 | 3.2689 | 3.2798
AE305 - AE405 | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824 | 5.0995
AE306 - AE406 | 6.141 | 6.0968 | 6.2066 | 5.8564 | 6.0691 | 5.968 | 6.1397 | 6.2999
AE326 - AE426 | 11.9321 | 11.8702 | 11.7862 | 11.113 | 11.8484 | 11.682 | 11.9712 | 11.87
AE345 - AE445 | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625 | 5.3703

## Delta Tables 2
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE301 through AE445
Table B16.7.2-34. CV Delta Cooling Coil Load, Economizer Operation (kWh/h)
|  |  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
| Test case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
| AE345-AE305 | Total Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.31146
|  | Sensible Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.31146
|  | Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.638e-15
| AE326 - AE306 | Total Cooling | 6.3983 | 6.3814 | 6.1912 | 5.9124 | 6.2871 | 6.251 | 6.4173 | 6.0479
|  | Sensible Cooling | -0.46026 | -0.51867 | -0.58455 | -0.36605 | -0.49552 | -0.556 | -0.44441 | -0.54242
|  | Latent Cooling | 6.8586 | 6.9001 | 6.7757 | 6.2785 | 6.7827 | 6.808 | 6.8617 | 6.5903
Table B16.7.2-35. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h)
|  |  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | HAP
| Test case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | Carrier
| AE445-AE405 | Total Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834 | 0.040668
|  | Sensible Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834 | 0.040668
|  | Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0316e-16
| AE426 - AE406 | Total Cooling | 0.60713 | 0.60799 | 0.61163 | 0.65589 | 0.50783 | 0.537 | 0.5858 | 0.47786
|  | Sensible Cooling | -0.041587 | -0.050749 | -0.052419 | -0.037806 | -0.041867 | -0.051 | -0.044634 | -0.0534
|  | Latent Cooling | 0.64871 | 0.65874 | 0.66405 | 0.6937 | 0.54969 | 0.588 | 0.63044 | 0.53126
r

## Detailed Location Results
User-definable chart to look at diagnostic results. Allows selection of test case and diagnostic variable; see Cells B4, B5 (instructions in Cells C4, C5). Displays selected case and diagnostic value for all programs by system location. For selection of viewed program results, see Cells A8-A20, A42-A54 (instructions in Cell A4).
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - Detailed Location Results
| AE301 | <== Select Case | Desc: | AE301 CV, Heating, OD/OWB = -29.00/-29.00 °C
| Dry Bulb Temperature (°C) | <== Select Variable | Title | AE301 CV, Heating, OD/OWB = -29.00/-29.00 °C Dry Bulb Temperature (°C)
[16 empty] | Dry Bulb Temperature (°C) | 1
InOut | Tab Name | [12 empty] | OFFSETS |  | Humidity Ratio (g/gda) | 2
1 | QAS | [14 empty] | Specific Volume (L/kgda) | 3
1 | DEEAP | [14 empty] | Enthalpy (J/gda) | 4
1 | DeST | [12 empty] | Summary Outputs | Detailed Outputs | Mass Flow Rate (kgda/s) | 5
1 | DOE22 | [11 empty] | AE301 | 77 | 77
1 | Eplus | [11 empty] | AE303 | 78 | 82
1 | IES-VE | [11 empty] | AE304 | 79 | 87
1 | TRNSYS | [11 empty] | AE305 | 80 | 92
0 | YourData | [11 empty] | AE306 | 81 | 97
0 | Blank | [11 empty] | AE326 | 82 | 102
0 | Blank | [11 empty] | AE345 | 83 | 107
0 | Blank | [11 empty] | AE401 | 125 | 125
0 | Blank | [11 empty] | AE403 | 126 | 130
0 | Blank | [11 empty] | AE404 | 127 | 135
[13 empty] | AE405 | 128 | 140
[13 empty] | AE406 | 129 | 145
[13 empty] | AE426 | 130 | 150
[13 empty] | AE445 | 131 | 155
Table Below
*
*
*
*
\/
|  |  | Results Offset ==> | 77 | Results Row ==> | 1 |  | Result Sets ==> | #N/A | Ret Fan Exists | TRUE
| Result Col Offset==> | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Air Loop Location==> | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
| Air Loop Location==> | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
InOut | Tab Name | Outdoor Air | Mixed Air | Preheat Coil Outlet | Cool Coil Outlet | Supply Air | Zone 1 Supply Air | Zone 2 Supply Air* | Zone 1 Air | Zone 2 Air* | Ret. Fan Inlet | Ret. Fan Outlet
1 | QAS | -29 | 3.4316 | 7.2222 | 7.2222 | 7.7838 | 29.2787 | 27.8228 | 21.1111 | 22.2222 | 21.6708 | 22.019
1 | DEEAP | -29 | 3.3982 | 7.2222 | 7.2222 | 7.7845 | 29.2883 | 27.8298 | 21.1111 | 22.2222 | 21.6708 | 21.9663
1 | DeST | -29 | 2.3874 | 7.22 | 7.22 | 7.8099 | 29.6699 | 28.084 | 21.111 | 22.222 | 21.7092 | 22.0042
1 | DOE22 | -29 | #N/A | 7.2222 | 7.2222 | 7.7778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | 21.9444
1 | Eplus | -29 | 2.4185 | 7.22 | 7.22 | 7.8063 | 29.649 | 28.0886 | 21.1299 | 22.2485 | 21.6893 | 21.982
1 | IES-VE | -29 | 2.3582 | 7.22 | 7.22 | 7.8018 | 29.5754 | 28.026 | 21.1106 | 22.221 | 21.6658 | 21.9567
1 | TRNSYS | -29 | 3.4295 | 7.22 | 7.22 | 7.7815 | 29.27 | 27.81 | 21.1102 | 22.2171 | 21.6678 | 22.0159
0 | YourData | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on A7: Set to 0 to turn off result set.

## Aggregate Results
Output spreadsheet for Airside HVAC BESTEST
[5 empty] | DEEAP | DeST | DOE22 | EPlus | IES-VE
Aggregator Sheet - Collects data from Plots
Cooling Coil- Coil Outlet RH (RHcco) (%) |  | Results Column ==> | 11
OFFSETS
Cells B9:N9 contain the tab name of the results set. By changing the tab name all results for that column are changed and plot data updated. It is possible to change the order or plot multiple new results sets by changing the tab names. Plots currently only address through column I. To plot more than 9 results sets the plot ranges must be adjusted.
Tab Name==> | QAS | DEEAP | DeST | DOE22 | Eplus | IES-VE | TRNSYS | YourData | Blank | Blank | Blank | Blank | Blank |  | Summary Outputs | Detailed Outputs |  |  | Summary Output Columns | Detailed Output Columns
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 24.7331 | 24.7328 | #N/A | 23.9613 | 23.8906 | 24.65 | 24.6351 | 23.8892 | #N/A | #N/A | #N/A | #N/A | #N/A | AE301 | 77 | 77 | CAV Heat | AE301 CV, Heating, OD/OWB = -29.00/-29.00 °C | Zone 1 Sensible Heating Load (QZH1sensible) (kWh/h) | Variable
AE303 Dry Coil 15.5/-3.0 | 48.1495 | 47.6873 | 48.22 | 47.9247 | 47.4569 | 48.02 | 48.1783 | 33.4715 | #N/A | #N/A | #N/A | #N/A | #N/A | AE303 | 78 | 82 | CAV Dry Coil | AE303 CV, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Zone 1 Sensible Cooling Load (QZC1sensible) (kWh/h) | Outdoor Air (oa)
AE304 Wet Coil 26.9/22.1 | 100 | 99.9992 | 95.49 | 100 | 99.1258 | 100 | 100 | 94.7543 | #N/A | #N/A | #N/A | #N/A | #N/A | AE304 | 79 | 87 | CAV Wet Coil | AE304 CV, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Zone 1 Latent Load (QZ1latent) (kWh/h) | Mixed Air (ma)
AE305 Dry Coil 24.9/2.4 No Econo | 65.719 | 65.3364 | 65.84 | 65.5319 | 64.909 | 65.57 | 65.7465 | 64.9185 | #N/A | #N/A | #N/A | #N/A | #N/A | AE305 | 80 | 92 | CAV Dry Coil 2, No Econo | AE305 CV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | Zone 2 Sensible Heating Load (QZH2sensible) (kWh/h) | Preheat Coil Outlet (pco)
AE306 Wet Coil 23.0/20.9 No Econo | 100 | 99.9992 | 96.21 | 100 | 99.2475 | 100 | 100 | 95.3924 | #N/A | #N/A | #N/A | #N/A | #N/A | AE306 | 81 | 97 | CAV Wet Coil 2, No Econo | AE306 CV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | Zone 2 Sensible Cooling Load (QZC2sensible) (kWh/h) | Cool Coil Outlet (cco)
AE326 Wet Coil 23.0/20.9 DB Econo | 100 | 99.9992 | 98.89 | 100 | 99.9275 | 100 | 100 | 99.8848 | #N/A | #N/A | #N/A | #N/A | #N/A | AE326 | 82 | 102 | CAV Dry Coil 2, Dry Bulb Econo | AE326 CV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo. | Zone 2 Latent Load (QZ2latent) (kWh/h) | Supply Air (sa)
AE345 Dry Coil 24.9/2.4 Enth. Eco | 51.0891 | 50.7067 | 51.33 | 51.1359 | 50.9944 | 51.1 | 51.1113 | 50.9986 | #N/A | #N/A | #N/A | #N/A | #N/A | AE345 | 83 | 107 | CAV Wet Coil 2, Enthalpy Econo | AE345 CV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo | Pre-Heating Coil Load (QHpreheat) (kWh/h) | Zone 1 Supply Air (z1s)
AE401 Heat -29.0/-29.0 | 4.1447 | 4.1474 | #N/A | 4.8015 | 4.1501 | 4.17 | 4.1464 | 4.1447 | #N/A | #N/A | #N/A | #N/A | #N/A | AE401 | 125 | 125 | VAV Heat | AE401 VAV, Heating, OD/OWB = -29.00/-29.00 °C | Cooling Coil Loads- Sensible (QCsensible) (kWh/h) | Zone 2 Supply Air (z2s)
AE403 Dry Coil 15.5/-3.0 | 36.3949 | 36.0086 | 36.39 | 34.2896 | 35.8492 | 35.98 | 36.3722 | 32.3951 | #N/A | #N/A | #N/A | #N/A | #N/A | AE403 | 126 | 130 | VAV Dry Coil | AE403 VAV, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Cooling Coil Loads- Latent (QClatent) (kWh/h) | Zone 1 Air (z1)
AE404 Wet Coil 26.9/22.1 | 100 | 99.9992 | 97.24 | 100 | 98.7059 | 100 | 100 | 96.7661 | #N/A | #N/A | #N/A | #N/A | #N/A | AE404 | 127 | 135 | VAV Wet Coil | AE404 VAV, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Cooling Coil Loads- Total (QCtotal) (kWh/h) | Zone 2 Air (z2)
AE405 Dry Coil 24.9/2.4 No Econo | 53.4629 | 53.1717 | 53.52 | 51.8548 | 52.7786 | 53.05 | 53.4325 | 52.6788 | #N/A | #N/A | #N/A | #N/A | #N/A | AE405 | 128 | 140 | VAV Dry Coil 2, No Econo | AE405 VAV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | Cooling Coil- Coil Outlet RH (RHcco) (%) | Return Fan Inlet (rfi)
AE406 Wet Coil 23.0/20.9 No Econo | 100 | 99.9992 | 99.38 | 100 | 99.7649 | 100 | 100 | 99.3471 | #N/A | #N/A | #N/A | #N/A | #N/A | AE406 | 129 | 145 | VAV Wet Coil 2, No Econo | AE406 VAV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | Zone 1 Reheat Load (QH1reheat) (kWh/h) | Return Fan Outlet (rfo)
AE426 Wet Coil 23.0/20.9 DB Econo | 100 | 99.9992 | 99.58 | 100 | 99.9528 | 100 | 100 | 99.8844 | #N/A | #N/A | #N/A | #N/A | #N/A | AE426 | 130 | 150 | VAV Dry Coil 2, Dry Bulb Econo | AE426 VAV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo. | Zone 2 Reheat Load (QH2reheat) (kWh/h)
AE445 Dry Coil 24.9/2.4 Enth. Eco | 49.575 | 49.2421 | 49.78 | 49.664 | 49.4632 | 49.58 | 49.5567 | 49.3605 | #N/A | #N/A | #N/A | #N/A | #N/A | AE445 | 131 | 155 | VAV Wet Coil 2, Enthalpy Econo | AE445 VAV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo
Pre-Heating Coil Load (QHpreheat) (kWh/h) |  | Results Column ==> | 7
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 2.947 | 2.9697 | 3.58 | 3.7882 | 3.5747 | 3.647 | 2.9467 | 3.5822 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 10.2597 | 10.2479 | 10.31 | 10.8176 | 10.343 | 10.451 | 10.2578 | 10.3476 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Sensible (QCsensible) (kWh/h) |  | Results Column ==> | 8
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.4549 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 10.3202 | 10.2556 | 10.0587 | 9.8897 | 10.1563 | 10.034 | 10.315 | 10.0831 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1982 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 8.9211 | 8.8688 | 8.6987 | 8.5975 | 8.7437 | 8.652 | 8.9149 | 8.6909 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 8.4609 | 8.3501 | 8.1141 | 8.2315 | 8.2481 | 8.096 | 8.4705 | 8.1485 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5096 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862 | 7.2943 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296 | 3.5461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849 | 3.4927 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Latent (QClatent) (kWh/h) |  | Results Column ==> | 9
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 6.2583 | 6.2947 | 7.0108 | 6.214 | 6.6217 | 6.629 | 6.2615 | 6.9711 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 5.4432 | 5.4441 | 6.1035 | 5.4338 | 5.7489 | 5.75 | 5.4435 | 6.0483 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 12.3018 | 12.3442 | 12.8792 | 11.7123 | 12.5316 | 12.558 | 12.3053 | 12.6386 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.638e-15 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5791e-17 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 5.9242 | 5.9745 | 6.5805 | 5.9168 | 6.3173 | 6.313 | 5.9214 | 6.48 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0316e-16 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 4.5879 | 4.6068 | 4.9686 | 4.4948 | 4.84 | 4.868 | 4.5892 | 4.8931 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 5.2366 | 5.2655 | 5.6327 | 5.1885 | 5.3897 | 5.456 | 5.2196 | 5.4244 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0633e-16 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Total (QCtotal) (kWh/h) |  | Results Column ==> | 10
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.4549 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 16.5785 | 16.5503 | 17.0695 | 16.1037 | 16.778 | 16.662 | 16.5765 | 17.0541 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1982 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 14.3643 | 14.3129 | 14.8022 | 14.0314 | 14.4926 | 14.403 | 14.3584 | 14.7392 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 20.7626 | 20.6943 | 20.9933 | 19.9438 | 20.7797 | 20.654 | 20.7757 | 20.7871 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5096 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076 | 13.7744 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187 | 8.4392 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045 | 8.9171 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Reheat Load (QH1reheat) (kWh/h) |  | Results Column ==> | 12
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 7.7129 | 7.7075 | 7.4721 | 7.706 | 7.5057 | 7.539 | 7.7093 | 7.501 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 2.2584 | 2.2547 | 2.1363 | 2.15 | 2.1827 | 2.188 | 2.2552 | 2.171 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.99332 | 0.98884 | 0.85904 | 0.79774 | 0.94208 | 0.915 | 0.99153 | 0.93938 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 2.2598 | 2.2561 | 2.1367 | 2.0723 | 2.193 | 2.188 | 2.2567 | 2.1923 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 2.2625 | 2.2588 | 2.1374 | 2.1107 | 2.2136 | 2.188 | 2.2618 | 6.603 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 2.2625 | 2.2588 | 2.1374 | 2.1256 | 2.2141 | 2.188 | 2.2668 | 6.6056 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 2.2587 | 2.255 | 2.1374 | 2.0887 | 2.1849 | 2.188 | 2.2607 | 2.1841 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 4.4994 | 4.4963 | 4.5019 | 4.5839 | 4.5034 | 4.524 | 4.4895 | 4.5018 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Reheat Load (QH2reheat) (kWh/h) |  | Results Column ==> | 13
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 8.3889 | 8.3822 | 8.0774 | 8.3763 | 8.1309 | 8.17 | 8.3843 | 8.1235 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 2.4572 | 2.4515 | 2.3 | 2.3194 | 2.3607 | 2.366 | 2.4545 | 2.3444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 1.519 | 1.5135 | 1.3509 | 1.2681 | 1.4552 | 1.419 | 1.5236 | 1.451 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 2.4589 | 2.4532 | 2.3017 | 2.2232 | 2.3739 | 2.366 | 2.4562 | 2.3735 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 2.4624 | 2.4568 | 2.3004 | 2.2695 | 2.4005 | 2.366 | 2.4621 | 7.0813 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 2.4624 | 2.4568 | 2.3005 | 2.2886 | 2.4012 | 2.366 | 2.4678 | 7.0847 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 2.4575 | 2.4518 | 2.3005 | 2.2414 | 2.3635 | 2.366 | 2.461 | 2.3628 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 4.8772 | 4.8725 | 4.891 | 5.0147 | 4.9022 | 4.926 | 4.8689 | 4.8988 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Detailed Outputs
Outdoor Air Temp |  | Results Column ==> | 1 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio |  | Results Column ==> | 1 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | 0.016772 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | 0.016772 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio (just for 5 cases)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE305 Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Mass Flow Rat |  | Results Column ==> | 1 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.28139 | 0.28143 | 0.28316 | 0.29649 | 0.28418 | 0.28316 | 0.2814 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.27809 | 0.27814 | 0.28316 | 0.28151 | 0.28418 | 0.28316 | 0.27808 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.27554 | 0.27557 | 0.28316 | 0.2735 | 0.28418 | 0.28316 | 0.27553 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.2774 | 0.27745 | 0.28316 | 0.27741 | 0.28418 | 0.28316 | 0.27739 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.27605 | 0.27609 | 0.28316 | 0.27538 | 0.28418 | 0.28316 | 0.27604 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.27809 | 0.27814 | 0.28316 | 0.28597 | 0.28418 | 0.28316 | 0.27808 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.27533 | 0.27537 | 0.28316 | 0.27289 | 0.28418 | 0.28316 | 0.27532 | 0.28419 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.2774 | 0.27745 | 0.28316 | 0.27761 | 0.28418 | 0.28316 | 0.27739 | 0.28419 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.27552 | 0.27556 | 0.28316 | 0.27474 | 0.28418 | 0.28316 | 0.27552 | 0.28419 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133 | 0.3317 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411 | 0.33468 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Temperature |  | Results Column ==> | 5 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 7.7838 | 7.7845 | 7.8099 | 7.7778 | 7.8063 | 7.8018 | 7.7815 | 7.8075 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.7804 | 12.7808 | 12.7861 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 12.7778 | 12.7778 | 12.7946 | 12.8333 | 12.7797 | 12.7808 | 12.7819 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7778 | 12.7948 | 12.8889 | 12.7806 | 12.7808 | 12.7841 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7778 | 12.7658 | 12.7778 | 12.7804 | 12.7808 | 12.7843 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7778 | 12.7937 | 12.7778 | 12.7801 | 12.7808 | 12.7705 | 12.778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.78 | 12.7808 | 12.7711 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 7.2968 | 7.3083 | 7.3073 | 7.2778 | 7.2901 | 7.3103 | 7.2949 | 7.2849 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.78 | 12.7795 | 12.7822 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.7778 | 12.7778 | 12.7916 | 12.7778 | 12.7797 | 12.7846 | 12.7811 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7778 | 12.7939 | 12.7778 | 12.78 | 12.7795 | 12.7709 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7778 | 12.782 | 12.7778 | 12.7801 | 12.7795 | 12.7822 | 12.778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Humidity Ratio |  | Results Column ==> | 5 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014958 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0083798 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0057159 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.008437 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0088403 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009017 | 0.0087695 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0048458 | 0.004814 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | 0.0047847 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091064 | 0.009175 | 0.0091221 | 0.0090865 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.0091238 | 0.009184 | 0.0091292 | 0.0091365 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Specific Volume |  | Results Column ==> | 5 |  | Results Row Offset==> | 2
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 797.8282 | 797.7263 | 833.33 | #N/A | 830.3519 | #N/A | 793.9174 | 797.9222 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 815.504 | 815.3446 | 833.33 | #N/A | 830.3519 | #N/A | 811.5517 | 813.9103 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 821.5223 | 821.4151 | 833.33 | #N/A | 830.3519 | #N/A | 817.5256 | 821.0038 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 817.5333 | 817.3825 | 833.33 | #N/A | 830.3519 | #N/A | 813.5654 | 817.5342 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 821.5223 | 821.4151 | 833.33 | #N/A | 830.3519 | #N/A | 817.5341 | 821.0783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 821.5223 | 821.4151 | 833.33 | #N/A | 830.3519 | #N/A | 817.4842 | 821.6042 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 815.8428 | 815.6925 | 833.33 | #N/A | 830.3519 | #N/A | 811.8397 | 815.9259 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 794.7981 | 794.7275 | 833.33 | #N/A | 830.3519 | #N/A | 794.2783 | 794.858 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 814.2796 | 814.1232 | 833.33 | #N/A | 830.3519 | #N/A | 813.5066 | 813.9103 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 821.7345 | 821.6126 | 833.33 | #N/A | 830.3519 | #N/A | 819.6593 | 821.5114 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 816.3051 | 816.1571 | 833.33 | #N/A | 830.3519 | #N/A | 815.5201 | 816.3214 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 821.8794 | 821.7587 | 833.33 | #N/A | 830.3519 | #N/A | 821.0663 | 821.9243 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 821.8794 | 821.7587 | 833.33 | #N/A | 830.3519 | #N/A | 821.1102 | 821.99 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 815.8428 | 815.6925 | 833.33 | #N/A | 830.3519 | #N/A | 815.0746 | 815.9259 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Enthalpy |  | Results Column ==> | 5 |  | Results Row Offset==> | 3
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 11.726 | #N/A | 11.71 | #N/A | 11.6064 | #N/A | 11.7069 | 11.608 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 23.5371 | #N/A | 23.55 | #N/A | 23.3653 | #N/A | 23.5569 | 20.2456 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 35.2043 | #N/A | 34.16 | #N/A | 34.9895 | #N/A | 35.2138 | 33.996 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 27.4712 | #N/A | 27.49 | #N/A | 27.2729 | #N/A | 27.489 | 27.2704 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 35.2043 | #N/A | 34.26 | #N/A | 35.0189 | #N/A | 35.2197 | 34.1405 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 35.2043 | #N/A | 34.93 | #N/A | 35.1723 | #N/A | 35.185 | 35.159 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 24.194 | #N/A | 24.24 | #N/A | 24.155 | #N/A | 24.186 | 24.1529 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 7.9923 | #N/A | 8 | #N/A | 7.9766 | #N/A | 7.9897 | 7.9714 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 21.1635 | #N/A | 21.16 | #N/A | 21.0244 | #N/A | 21.1625 | 20.2456 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 35.6156 | #N/A | 34.93 | #N/A | 35.2972 | #N/A | 35.6235 | 34.98 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 25.0901 | #N/A | 25.1 | #N/A | 24.9195 | #N/A | 25.0664 | 24.9194 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 35.8965 | #N/A | 35.74 | #N/A | 35.8327 | #N/A | 35.8787 | 35.7803 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 35.8965 | #N/A | 35.76 | #N/A | 35.8769 | #N/A | 35.908 | 35.9068 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 24.194 | #N/A | 24.24 | #N/A | 24.1552 | #N/A | 24.1977 | 24.1529 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Mass Flow Rate |  | Results Column ==> | 5 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.77054 | 0.77064 | 0.73624 | 0.77088 | 0.73888 | 0.73624 | 0.77055 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.75384 | 0.75399 | 0.73624 | 0.73193 | 0.73888 | 0.73624 | 0.7538 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.74832 | 0.74842 | 0.73624 | 0.71109 | 0.73888 | 0.73624 | 0.74829 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.75197 | 0.75211 | 0.73624 | 0.72126 | 0.73888 | 0.73624 | 0.75194 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.74832 | 0.74842 | 0.73624 | 0.716 | 0.73888 | 0.73624 | 0.74829 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.73881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814 | 0.28416 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.33569 | 0.33612 | 0.3385 | 0.33688 | 0.3351 | 0.33354 | 0.33495 | 0.33634 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.53919 | 0.53988 | 0.54925 | 0.53541 | 0.53845 | 0.54137 | 0.53882 | 0.53949 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.33473 | 0.33516 | 0.33832 | 0.33591 | 0.33415 | 0.33354 | 0.33393 | 0.33437 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.33213 | 0.33253 | 0.33835 | 0.32968 | 0.33145 | 0.33354 | 0.33137 | 0.33164 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133 | 0.3317 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411 | 0.33468 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Air Temperature |  | Results Column ==> | 8 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1299 | 21.1106 | 21.1102 | 21.1199 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3285 | 23.3333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.8914 | 23.8893 | 23.8806 | 23.89 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3269 | 23.3359 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3339 | 23.341 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3337 | 23.341 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.328 | 23.3359 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1452 | 21.1103 | 21.1151 | 21.1299 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3302 | 23.3333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.9001 | 23.8934 | 23.8829 | 23.8864 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3319 | 23.3304 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.318 | 23.3304 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3286 | 23.3304 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3321 | 23.3304 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Supply Air Temperature |  | Results Column ==> | 6 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 29.2787 | 29.2883 | 29.6699 | #N/A | 29.649 | 29.5754 | 29.27 | 29.6391 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 19.1796 | 19.1761 | 19.05 | #N/A | 19.1013 | 19.1006 | 19.18 | 19.0797 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 15.5904 | 15.5808 | 15.3101 | #N/A | 15.485 | 15.4247 | 15.59 | 15.4775 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 19.1811 | 19.1778 | 19.0515 | #N/A | 19.1133 | 19.1006 | 19.18 | 19.1092 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 19.1841 | 19.1807 | 19.0246 | #N/A | 19.1369 | 19.1006 | 19.19 | 31.7525 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 19.1841 | 19.1807 | 19.0525 | #N/A | 19.1373 | 19.1006 | 19.19 | 31.7464 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 19.1799 | 19.1765 | 19.0515 | #N/A | 19.1037 | 19.1006 | 19.18 | 19.0996 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 46.92 | 46.9483 | 46.8548 | #N/A | 46.6969 | 46.5047 | 46.8281 | 46.6818 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.7778 | 12.7777 | 12.795 | #N/A | 12.78 | 12.7795 | 12.7822 | 12.7781 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.7778 | 12.7777 | 12.7916 | #N/A | 12.7808 | 12.7846 | 12.7878 | 12.7846 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7777 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7777 | 12.7939 | #N/A | 12.7899 | 12.7795 | 12.7709 | 12.7783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7777 | 12.782 | #N/A | 12.79 | 12.7795 | 12.7822 | 12.778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | 12.7862 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Supply Air Humidity Ratio |  | Results Column ==> | 6 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014958 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0083798 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0057159 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.008437 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0088403 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00026343 | 0.00025901 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009021 | 0.0087824 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0048458 | 0.0048143 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | 0.0047847 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091018 | 0.009175 | 0.0091221 | 0.0090851 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.009124 | 0.009184 | 0.0091292 | 0.0091365 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Air Temperature |  | Results Column ==> | 9 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2485 | 22.221 | 22.2171 | 22.2336 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4389 | 24.4444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 25 | 25 | 25 | 25 | 25.0047 | 25.001 | 25.0027 | 25.002 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4367 | 24.4477 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4427 | 24.4542 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4424 | 24.4542 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4382 | 24.4477 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2593 | 22.2208 | 22.2211 | 22.2381 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4608 | 24.4431 | 24.4386 | 24.4444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 25 | 25 | 25 | 25 | 25.0168 | 25.0043 | 24.9989 | 24.9961 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4401 | 24.4403 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4432 | 24.431 | 24.4403 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4416 | 24.4403 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.442 | 24.4403 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Supply Air Temperature |  | Results Column ==> | 7 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 27.8228 | 27.8298 | 28.084 | #N/A | 28.0886 | 28.026 | 27.81 | 28.0732 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 18.7479 | 18.7408 | 18.57 | #N/A | 18.6401 | 18.637 | 18.75 | 18.6109 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 16.4644 | 16.4551 | 16.1852 | #N/A | 16.3615 | 16.2939 | 16.48 | 16.3522 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 18.75 | 18.7428 | 18.572 | #N/A | 18.6566 | 18.6371 | 18.75 | 18.6531 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 18.7541 | 18.747 | 18.5398 | #N/A | 18.6889 | 18.6371 | 18.76 | 30.2201 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 18.7541 | 18.747 | 18.5677 | #N/A | 18.6896 | 18.637 | 18.76 | 30.2159 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 18.7483 | 18.7411 | 18.572 | #N/A | 18.6434 | 18.6371 | 18.75 | 18.64 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 36.0391 | 36.0548 | 35.9521 | #N/A | 35.8886 | 35.7662 | 35.9884 | 35.8658 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.7778 | 12.7777 | 12.795 | #N/A | 12.78 | 12.7795 | 12.7822 | 12.7781 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.7778 | 12.7777 | 12.7916 | #N/A | 12.7808 | 12.7846 | 12.7878 | 12.7846 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7777 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | 12.7778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7777 | 12.7939 | #N/A | 12.7899 | 12.7795 | 12.7709 | 12.7783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7777 | 12.782 | #N/A | 12.79 | 12.7795 | 12.7822 | 12.778 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | 12.7862 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Supply Air Humidity Ratio |  | Results Column ==> | 7 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014958 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0083798 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0057159 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.008437 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0088403 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009021 | 0.0087824 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0048458 | 0.0048143 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | 0.0047847 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091018 | 0.009175 | 0.0091221 | 0.0090851 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.009124 | 0.009184 | 0.0091292 | 0.0091365 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Outlet Air Temperature |  | Results Column ==> | 4 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.22 | 7.22 | 7.22 | 7.2222 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 12.2066 | 12.2059 | 12.2049 | 12.1667 | 12.197 | 12.199 | 12.215 | 12.1941 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 12.2072 | 12.2065 | 12.2047 | 12.2222 | 12.2012 | 12.199 | 12.2114 | 12.1999 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 12.2068 | 12.2061 | 12.2049 | 12.2778 | 12.1989 | 12.199 | 12.2132 | 12.197 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 12.2072 | 12.2065 | 12.1759 | 12.2222 | 12.2019 | 12.199 | 12.2138 | 12.1999 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 12.2072 | 12.2065 | 12.2038 | 12.2222 | 12.2017 | 12.199 | 12.2 | 12.2005 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 12.2066 | 12.2059 | 12.2049 | 12.2222 | 12.197 | 12.199 | 12.2 | 12.1957 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.2031 | 7.22 | 7.22 | 7.2222 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.6643 | 12.6466 | 12.6699 | 12.6667 | 12.6598 | 12.66 | 12.6692 | 12.6915 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.4805 | 12.4612 | 12.4633 | 12.4444 | 12.4725 | 12.47 | 12.491 | 12.5624 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.6644 | 12.6468 | 12.6704 | 12.6667 | 12.661 | 12.66 | 12.6697 | 12.6927 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.6647 | 12.6472 | 12.6693 | 12.6667 | 12.6637 | 12.66 | 12.6584 | 12.6947 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.6647 | 12.6472 | 12.6574 | 12.6667 | 12.6638 | 12.66 | 12.67 | 12.6949 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.6644 | 12.6519 | 12.6704 | 12.6667 | 12.6608 | 12.66 | 12.67 | 12.6925 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Humidity Ratio |  | Results Column ==> | 8 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0021971 | 0.0021972 | 0.0022251 | #N/A | 0.0021723 | 0.002253 | 0.0021868 | 0.0021725 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0048927 | 0.0048518 | 0.0049298 | #N/A | 0.0048436 | 0.004938 | 0.0048998 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0095185 | 0.0095186 | 0.00914 | #N/A | 0.0094477 | 0.009595 | 0.0095252 | 0.0090551 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0064526 | 0.0064187 | 0.0064918 | #N/A | 0.0063912 | 0.006499 | 0.0064597 | 0.0063915 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0095187 | 0.0095189 | 0.00919 | #N/A | 0.0094593 | 0.009592 | 0.0095248 | 0.0091126 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0095187 | 0.0095189 | 0.0094417 | #N/A | 0.0095202 | 0.009613 | 0.0095166 | 0.0095159 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0051532 | 0.0051194 | 0.0052044 | #N/A | 0.0051565 | 0.005212 | 0.0051553 | 0.0051566 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.002304 | 0.0023034 | 0.0023324 | #N/A | 0.0022887 | 0.002374 | 0.0022691 | 0.0022891 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0049701 | 0.00493 | 0.0049958 | #N/A | 0.0049254 | 0.005021 | 0.0049882 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0099076 | 0.0098953 | 0.0096515 | #N/A | 0.009788 | 0.00998 | 0.0099213 | 0.0096746 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0065301 | 0.006497 | 0.0065572 | #N/A | 0.0064728 | 0.006582 | 0.0065372 | 0.0064717 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.010823 | 0.010812 | 0.010775 | #N/A | 0.010803 | 0.010931 | 0.010838 | 0.010785 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.010823 | 0.010812 | 0.010787 | #N/A | 0.010825 | 0.01094 | 0.010844 | 0.010837 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0061741 | 0.0061387 | 0.0062162 | #N/A | 0.0061691 | 0.006264 | 0.0061921 | 0.0061658 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Humidity Ratio |  | Results Column ==> | 9 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0023817 | 0.0023819 | 0.0024213 | #N/A | 0.0023649 | 0.002454 | 0.0023719 | 0.0023652 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0050812 | 0.0050403 | 0.0051345 | #N/A | 0.0050359 | 0.005139 | 0.0050898 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0097082 | 0.0097084 | 0.00934 | #N/A | 0.00964 | 0.009796 | 0.0097162 | 0.0092474 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0066415 | 0.0066076 | 0.0066965 | #N/A | 0.0065835 | 0.0067 | 0.0066501 | 0.0065838 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0097086 | 0.0097087 | 0.00939 | #N/A | 0.0096517 | 0.009793 | 0.0097161 | 0.0093049 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0097086 | 0.0097087 | 0.00965 | #N/A | 0.0097126 | 0.009814 | 0.009708 | 0.0097083 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0053417 | 0.0053078 | 0.0054091 | #N/A | 0.0053488 | 0.005413 | 0.0053453 | 0.005349 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.0023101 | 0.0023096 | 0.0023296 | #N/A | 0.0022872 | 0.002374 | 0.0022892 | 0.0022874 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0050294 | 0.0049886 | 0.0050706 | #N/A | 0.0049851 | 0.005084 | 0.0050489 | 0.0029334 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.010241 | 0.010229 | 0.0099979 | #N/A | 0.010124 | 0.010327 | 0.010261 | 0.010009 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0065896 | 0.0065555 | 0.006633 | #N/A | 0.0065327 | 0.006645 | 0.006598 | 0.0065313 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.010883 | 0.010871 | 0.010849 | #N/A | 0.010863 | 0.010994 | 0.0109 | 0.010845 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.010883 | 0.010871 | 0.010861 | #N/A | 0.010885 | 0.011003 | 0.010906 | 0.010897 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0062336 | 0.0061973 | 0.006292 | #N/A | 0.006229 | 0.006327 | 0.006253 | 0.0062255 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.5616 | 0.56226 | 0.5899 | 0.55556 | 0.58627 | 0.5818 | 0.56149 | 0.58528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.57122 | 0.57189 | 0.5899 | 0.61111 | 0.58339 | 0.5818 | 0.57113 | 0.58373 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.5706 | 0.57126 | 0.5899 | 0.61111 | 0.5785 | 0.5818 | 0.5705 | 0.57794 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.57101 | 0.57168 | 0.5899 | 0.61111 | 0.58174 | 0.5818 | 0.57091 | 0.58075 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57849 | 0.5818 | 0.5705 | 0.57788 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57843 | 0.5818 | 0.57048 | 0.57745 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.57119 | 0.57185 | 0.5899 | 0.55556 | 0.58306 | 0.5818 | 0.57106 | 0.58207 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.074611 | 0.086087 | 0.087254 | 0.055556 | 0.086922 | 0.0903 | 0.074852 | 0.062638 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.1135 | 0.13116 | 0.1251 | 0.11111 | 0.1202 | 0.1195 | 0.11296 | 0.086298 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.29723 | 0.31661 | 0.32831 | 0.33333 | 0.30715 | 0.3146 | 0.29011 | 0.2154 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.11338 | 0.13101 | 0.12457 | 0.11111 | 0.11918 | 0.1195 | 0.11281 | 0.085036 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11634 | 0.1195 | 0.11249 | 0.083039 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11633 | 0.1195 | 0.11216 | 0.083061 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.1134 | 0.12586 | 0.12457 | 0.11111 | 0.11933 | 0.1195 | 0.11252 | 0.085232 | #N/A | #N/A | #N/A | #N/A | #N/A
Return Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.34819 | 0.29556 | 0.29495 | #N/A | 0.29272 | 0.2909 | 0.34804 | 0.29222 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.33958 | 0.2976 | 0.29495 | #N/A | 0.29128 | 0.2909 | 0.3394 | 0.29186 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.34187 | 0.29783 | 0.29495 | #N/A | 0.28885 | 0.2909 | 0.34171 | 0.28856 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.33946 | 0.29749 | 0.29495 | #N/A | 0.29046 | 0.2909 | 0.33927 | 0.28997 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.33921 | 0.29727 | 0.29495 | #N/A | 0.28884 | 0.2909 | 0.33905 | 0.28853 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.33921 | 0.29727 | 0.29495 | #N/A | 0.28881 | 0.2909 | 0.33911 | 0.28832 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.33956 | 0.29758 | 0.29495 | #N/A | 0.29112 | 0.2909 | 0.33943 | 0.29062 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.2012 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0049809 | 0.030526 | 0.004395 | #N/A | 0.0038467 | 0.0117 | 0.0048549 | 0.20096 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.10655 | 0.11411 | 0.10173 | #N/A | 0.090258 | 0.0986 | 0.10623 | 0.19845 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0049578 | 0.0068611 | 0.004371 | #N/A | 0.0037075 | 0.0117 | 0.0048189 | 0.19971 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.0048953 | 0.0067188 | 0.004377 | #N/A | 0.0031146 | 0.0117 | 0.0047643 | 0.19809 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.0048953 | 0.0067188 | 0.004377 | #N/A | 0.0031131 | 0.0116 | 0.0047598 | 0.20143 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0049631 | 0.0068735 | 0.004371 | #N/A | 0.0036902 | 0.0117 | 0.0048202 | 0.19976 | #N/A | #N/A | #N/A | #N/A | #N/A
Aggregate Coil Load (Heating and Cooling) |  | Results Column ==> |  |  | Results Row Offset==>
abs of sum of heating (negative) and cooling (positive)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 19.2067 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 10.9704 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 19.0908 | 19.0527 | 19.2794 | 18.1695 | 19.1753 | 18.996 | 19.0917 | 19.4445 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.764 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 19.0892 | 19.0285 | 19.24 | 18.4116 | 19.1067 | 18.957 | 19.0823 | 28.4234 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 25.4875 | 25.4099 | 25.4312 | 24.358 | 25.395 | 25.208 | 25.5104 | 34.4774 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163 | 19.7482 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076 | 13.7744 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187 | 8.4392 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045 | 8.9171 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393 | #N/A | #N/A | #N/A | #N/A | #N/A
Aggregate Sensible Coil Load (Heating and Cooling) |  | Results Column ==> |  |  | Results Row Offset==>
abs of sum of heating (negative) and cooling (positive)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 19.2067 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 10.9704 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 12.8325 | 12.7579 | 12.2686 | 11.9555 | 12.5536 | 12.368 | 12.8301 | 12.4735 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.764 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 13.646 | 13.5844 | 13.1365 | 12.9778 | 13.3578 | 13.206 | 13.6388 | 22.3751 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 13.1857 | 13.0657 | 12.552 | 12.6457 | 12.8634 | 12.65 | 13.2051 | 21.8388 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163 | 19.7482 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | 1.4098 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862 | 7.2943 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | 4.0987 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296 | 3.5461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849 | 3.4927 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | 4.1393 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Fraction
Fraction of supply air mass flow that is outdoor air
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.36519 | 0.36519 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36519 | 0.38462 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38462 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.36821 | 0.36821 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36821 | 0.38462 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38462 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.3689 | 0.3689 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.3689 | 0.38462 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99999 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.82841 | 0.82752 | 0.83653 | 0.8489 | 0.84805 | 0.84895 | 0.83021 | 0.84486 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.51064 | 0.51006 | 0.51555 | 0.50968 | 0.52778 | 0.52304 | 0.51097 | 0.52677 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.82871 | 0.82782 | 0.83698 | 0.82645 | 0.85046 | 0.84895 | 0.83068 | 0.84992 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.82954 | 0.82866 | 0.83688 | 0.83333 | 0.85738 | 0.84895 | 0.83144 | 0.85693 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A

## Delta Results
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - DELTA RESULTS for Delta Plots
DELTA 300-400
Pre-Heating Coil Load (QHpreheat) (kWh/h)
Tab Name==> | QAS | DEEAP | DeST | DOE22 | Eplus | IES-VE | TRNSYS | YourData | Blank | Blank | Blank | Blank | Blank
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | -7.3127 | -7.2782 | -6.73 | -7.0293 | -6.7682 | -6.804 | -7.3112 | -6.7654 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Sensible (QCsensible) (kWh/h)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278 | 5.0452 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 2.9212 | 2.8821 | 2.6085 | 2.431 | 2.7857 | 2.701 | 2.9287 | 2.7887 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824 | 5.0995 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 5.2857 | 5.2594 | 5.0718 | 4.9174 | 5.1602 | 5.085 | 5.2853 | 5.1447 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 4.867 | 4.7915 | 4.5396 | 4.5892 | 4.7066 | 4.58 | 4.8855 | 4.6557 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625 | 5.3703 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Latent (QClatent) (kWh/h)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5791e-17 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 0.33412 | 0.32027 | 0.43027 | 0.29717 | 0.30444 | 0.316 | 0.34014 | 0.49105 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0316e-16 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 0.85526 | 0.83731 | 1.1349 | 0.939 | 0.90886 | 0.882 | 0.85438 | 1.1552 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 7.0651 | 7.0787 | 7.2465 | 6.5238 | 7.1418 | 7.102 | 7.0857 | 7.2143 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0316e-15 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Total (QCtotal) (kWh/h)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278 | 5.0452 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 3.2553 | 3.2024 | 3.0388 | 2.7282 | 3.0902 | 3.017 | 3.2689 | 3.2798 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824 | 5.0995 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 6.141 | 6.0968 | 6.2066 | 5.8564 | 6.0691 | 5.968 | 6.1397 | 6.2999 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 11.9321 | 11.8702 | 11.7862 | 11.113 | 11.8484 | 11.682 | 11.9712 | 11.87 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625 | 5.3703 | #N/A | #N/A | #N/A | #N/A | #N/A
Economizer 300
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
Total Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.31146 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.31146 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.638e-15 | #N/A | #N/A | #N/A | #N/A | #N/A
Total Cooling | 6.3983 | 6.3814 | 6.1912 | 5.9124 | 6.2871 | 6.251 | 6.4173 | 6.0479 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.46026 | -0.51867 | -0.58455 | -0.36605 | -0.49552 | -0.556 | -0.44441 | -0.54242 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 6.8586 | 6.9001 | 6.7757 | 6.2785 | 6.7827 | 6.808 | 6.8617 | 6.5903 | #N/A | #N/A | #N/A | #N/A | #N/A
Economizer 400
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
Total Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834 | 0.040668 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834 | 0.040668 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0316e-16 | #N/A | #N/A | #N/A | #N/A | #N/A
Total Cooling | 0.60713 | 0.60799 | 0.61163 | 0.65589 | 0.50783 | 0.537 | 0.5858 | 0.47786 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.041587 | -0.050749 | -0.052419 | -0.037806 | -0.041867 | -0.051 | -0.044634 | -0.0534 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0.64871 | 0.65874 | 0.66405 | 0.6937 | 0.54969 | 0.588 | 0.63044 | 0.53126 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Supply Air W minus System Supply Air W (should be zero)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0% | 0.001287% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 1.739% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0% | 0% | 0% | 0% | -0.0002003% | 0% | 0.04436% | 0.1463% | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0% | 0.006872% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0% | 0% | 0% | 0% | -0.05064% | 0% | 0% | -0.016% | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0% | 0% | 0% | 0% | 0.002223% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Supply Air W minus System Supply Air W ( should be zero)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0% | 0.001287% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0% | 0% | 0% | 0% | -0.0002003% | 0% | 0.04436% | 0.1463% | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0% | 0.006872% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0% | 0% | 0% | 0% | -0.05064% | 0% | 0% | -0.016% | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0% | 0% | 0% | 0% | 0.002223% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 delta humidity ratio
Increase in humidity ratio from supply air to zone
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.00064875 | 0.00064878 | 0.00069081 | #N/A | 0.00067657 | 0.000704 | 0.00064486 | 0.0006767 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.00066204 | 0.00066191 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066419 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.00066666 | 0.00066659 | 0.00069744 | #N/A | 0.00067521 | 0.000704 | 0.00067088 | 0.00067533 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.00066369 | 0.00066359 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066584 | 0.0006756 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.00066693 | 0.00066686 | 0.00069842 | #N/A | 0.00067548 | 0.000704 | 0.00066908 | 0.0006756 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.00066693 | 0.00066686 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066904 | 0.0006756 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.00066232 | 0.00066221 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066443 | 0.0006756 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.0020451 | 0.0020448 | 0.0020724 | #N/A | 0.0020297 | 0.002112 | 0.0020057 | 0.0020301 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0016795 | 0.001678 | 0.0017081 | #N/A | 0.0016843 | 0.001756 | 0.0016993 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.00089288 | 0.00089161 | 0.00090227 | #N/A | 0.00089367 | 0.000924 | 0.00090036 | 0.00089224 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0016843 | 0.0016827 | 0.0017062 | #N/A | 0.0016891 | 0.001756 | 0.0017023 | 0.001687 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.0016975 | 0.0016958 | 0.001707 | #N/A | 0.0017009 | 0.001756 | 0.0017162 | 0.0017002 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.0016975 | 0.0016958 | 0.001707 | #N/A | 0.0017009 | 0.001756 | 0.0017152 | 0.0017004 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0016832 | 0.0016816 | 0.0017062 | #N/A | 0.0016882 | 0.001756 | 0.0017012 | 0.0016847 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 delta humidity ratio
Increase in humidity ratio from supply air to zone
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.00083342 | 0.0008335 | 0.00088697 | #N/A | 0.00086923 | 0.000905 | 0.00082994 | 0.00086933 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.00085051 | 0.00085035 | 0.00089913 | #N/A | 0.00086783 | 0.000905 | 0.00085415 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.00085644 | 0.00085641 | 0.00089744 | #N/A | 0.00086748 | 0.000905 | 0.0008619 | 0.00086758 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.00085262 | 0.00085244 | 0.00089913 | #N/A | 0.00086783 | 0.000905 | 0.00085627 | 0.00086793 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.00085679 | 0.00085676 | 0.00089842 | #N/A | 0.00086783 | 0.000905 | 0.00086044 | 0.00086792 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.00085679 | 0.00085676 | 0.00090265 | #N/A | 0.00086783 | 0.000905 | 0.00086039 | 0.00086792 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.00085086 | 0.00085066 | 0.00089913 | #N/A | 0.00086783 | 0.000905 | 0.00085445 | 0.00086793 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.0020512 | 0.002051 | 0.0020696 | #N/A | 0.0020282 | 0.002112 | 0.0020302 | 0.0020284 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0017389 | 0.0017367 | 0.001783 | #N/A | 0.0017441 | 0.001819 | 0.00176 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0012267 | 0.0012252 | 0.0012487 | #N/A | 0.0012291 | 0.001271 | 0.0012396 | 0.0012265 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0017438 | 0.0017413 | 0.001782 | #N/A | 0.001749 | 0.001819 | 0.001763 | 0.0017467 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.0017575 | 0.0017552 | 0.001781 | #N/A | 0.0017614 | 0.001819 | 0.0017783 | 0.0017604 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.0017575 | 0.0017552 | 0.001781 | #N/A | 0.0017615 | 0.001819 | 0.0017771 | 0.0017606 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0017427 | 0.0017401 | 0.001782 | #N/A | 0.001748 | 0.001819 | 0.0017621 | 0.0017444 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Latent Gain (gw/s)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.23072 | 0.23076 | 0.23474 | #N/A | 0.23073 | 0.23922 | 0.22932 | 0.23075 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.23034 | 0.23034 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.23025 | 0.23026 | 0.23699 | #N/A | 0.23026 | 0.23922 | 0.23168 | 0.23028 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.23034 | 0.23035 | 0.23732 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.23072 | 0.23071 | 0.23474 | #N/A | 0.23073 | 0.23923 | 0.22628 | 0.23074 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.23034 | 0.23038 | 0.23627 | #N/A | 0.23035 | 0.23924 | 0.23249 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.23025 | 0.23022 | 0.23715 | #N/A | 0.23026 | 0.23924 | 0.23217 | 0.23028 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23035 | 0.23924 | 0.23217 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.23034 | 0.23034 | 0.23595 | #N/A | 0.23035 | 0.23924 | 0.23235 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.23034 | 0.23034 | 0.23595 | #N/A | 0.23035 | 0.23924 | 0.23216 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.23034 | 0.23035 | 0.23583 | #N/A | 0.23035 | 0.23924 | 0.23216 | 0.23037 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Latent Gain (gw/s)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.34579 | 0.34587 | 0.35162 | #N/A | 0.34583 | 0.35877 | 0.34437 | 0.34584 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.34523 | 0.34524 | 0.35644 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.34509 | 0.34513 | 0.35577 | #N/A | 0.34513 | 0.35877 | 0.34731 | 0.34514 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.34523 | 0.34522 | 0.35644 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.34523 | 0.34527 | 0.35616 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.34523 | 0.34527 | 0.35784 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.34523 | 0.34522 | 0.35644 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.34579 | 0.3458 | 0.35162 | #N/A | 0.34583 | 0.35883 | 0.34226 | 0.34584 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.34523 | 0.3453 | 0.35691 | #N/A | 0.34527 | 0.35889 | 0.34873 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.34509 | 0.34509 | 0.35765 | #N/A | 0.34513 | 0.35899 | 0.34827 | 0.34514 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.34523 | 0.34522 | 0.35644 | #N/A | 0.34527 | 0.35889 | 0.34827 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.34523 | 0.34525 | 0.35644 | #N/A | 0.34527 | 0.35889 | 0.34853 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.34523 | 0.34525 | 0.35644 | #N/A | 0.34527 | 0.35889 | 0.34827 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.34523 | 0.34522 | 0.35663 | #N/A | 0.34527 | 0.35889 | 0.34827 | 0.34528 | #N/A | #N/A | #N/A | #N/A | #N/A
Total Zone Latent Gain (gw/s)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | HAP/Carrier | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.57651 | 0.57663 | 0.58636 | #N/A | 0.57656 | 0.59799 | 0.57369 | 0.57658 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.57557 | 0.57558 | 0.59239 | #N/A | 0.57563 | 0.59799 | 0.57778 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.57534 | 0.57538 | 0.59276 | #N/A | 0.5754 | 0.59799 | 0.57899 | 0.57542 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.57557 | 0.57557 | 0.59239 | #N/A | 0.57563 | 0.59799 | 0.57778 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.57557 | 0.57562 | 0.59349 | #N/A | 0.57563 | 0.59799 | 0.57777 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.57557 | 0.57562 | 0.59378 | #N/A | 0.57563 | 0.59799 | 0.57777 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.57557 | 0.57556 | 0.59239 | #N/A | 0.57563 | 0.59799 | 0.57778 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.57651 | 0.57651 | 0.58636 | #N/A | 0.57655 | 0.59806 | 0.56854 | 0.57658 | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.57557 | 0.57568 | 0.59318 | #N/A | 0.57563 | 0.59813 | 0.58122 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.57534 | 0.57532 | 0.5948 | #N/A | 0.57539 | 0.59824 | 0.58044 | 0.57542 | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.57557 | 0.57557 | 0.59239 | #N/A | 0.57563 | 0.59813 | 0.58043 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.57557 | 0.57559 | 0.59239 | #N/A | 0.57563 | 0.59813 | 0.58088 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.57557 | 0.57559 | 0.59239 | #N/A | 0.57563 | 0.59813 | 0.58043 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.57557 | 0.57557 | 0.59246 | #N/A | 0.57563 | 0.59813 | 0.58043 | 0.57565 | #N/A | #N/A | #N/A | #N/A | #N/A

## QAS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Quasi-Analytical Solution V2 | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: |  |  |  | 2014-10-10 |  | Modeler Organization for Tables and Charts (short): |  |  |  | PSU-TAMU-NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | QAS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | QAS/PSU-TAMU-NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | Quasi-analytic Solution
| Version: | V2
| Date: | 2014-11-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.4195 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0034 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.78348 | 0 | 0.78348 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.4965 | 2.0543 | 5.5508 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.1625 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0513 | 33.5916 | 33.5916 | 34.2029 | 27.0907 | 27.0907
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5042 | 19.088 | 23.3333 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 838.437 | 838.437 | 831.9622 | 833.6275 | 846.6514 | 846.6514
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8833 | 31.8833 | 29.5815 | 30.1736 | 36.2004 | 36.2004
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8678 | 24.8678 | 14.9386 | 15.5144 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 861.9632 | 861.9632 | 830.0307 | 831.6898 | 856.7312 | 856.7312
[16 empty] | Enthalpy (J/gda) | 69.8513 | 58.2685 | 58.2685 | 41.8451 | 42.4358 | 52.7436 | 52.7436
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3599 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1826 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111 | 21.3832
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.85614 | 0 | 0.85614 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304 | 0.002304
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5739 | 2.0543 | 5.6282 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.6715 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895 | 837.4631
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9163 | 0 | 1.9163 | 44.5612 | [6 empty] | Enthalpy (J/gda) | -28.5429 | 8.2324 | 33.5942 | 33.5942 | 34.2055 | 27.0925 | 27.0925 | 27.3675
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7064 | 0.97038 | 2.6768 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681 | 0.21681
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5618 | 1.7999 | 3.3617 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9845 | 20.9845 | 18.5042 | 19.088 | 23.3333 | 23.3333 | 23.6459
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2077 | 0 | 2.2077 | 34.0915 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0374 | 839.0374 | 831.9622 | 833.6275 | 846.6514 | 846.6514 | 847.5441
[16 empty] | Enthalpy (J/gda) | 23.0217 | 32.0985 | 32.0985 | 29.5832 | 30.1752 | 36.2025 | 36.2025 | 36.5199
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888 | 0.22888
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.088 | 25.088 | 14.9386 | 15.5144 | 23.8889 | 23.8889 | 24.215
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.5998 | 862.5998 | 830.0307 | 831.6898 | 856.7312 | 856.7312 | 857.6719
[16 empty] | Enthalpy (J/gda) | 69.8537 | 58.4974 | 58.4974 | 41.8464 | 42.4371 | 52.7457 | 52.7457 | 53.0807
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098 | 0.23098
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0556 | 24.0556 | 18.506 | 19.0896 | 23.3333 | 23.3333 | 23.6458
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0065621 | 0.0065621 | 0.0065621
[16 empty] | Specific volume (L/kgda) | 850.4314 | 849.9075 | 849.9075 | 834.0374 | 835.7063 | 848.7583 | 848.7583 | 849.6529
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.1804 | 39.1804 | 33.5362 | 34.1298 | 40.172 | 40.172 | 40.4903
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33952 | #N/A | 0.22831 | 0.22831
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4335 | 23.4335 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014546 | 0.014546 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.8306 | 859.8306 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.5901 | 60.5901 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5044 | 19.0882 | 23.3333 | 23.3333 | 23.6459
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051678 | 0.0051678 | 0.0051678
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 832.1827 | 833.8485 | 846.8753 | 846.8753 | 847.7683
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 30.0033 | 30.5955 | 36.6243 | 36.6243 | 36.9419
[16 empty] | Mass flow rate (kgda/s) | 0.34027 | 0.34027 | 0.34027 | 0.34027 | 0.34027 | #N/A | 0.22882 | 0.22882
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load | Load | Load | Load | Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 2.947 | 0 | 0 | 0 | 24.7331 | 7.7129 | 8.3889 | AE301 | Dry bulb temperature (°C) | -29 | 3.4316 | 7.2222 | 7.2222 | 7.7838 | 29.2787 | 27.8228 | 21.1111 | 22.2222 | 21.6708 | 22.019
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.7354 | 0 | 6.7354 | 48.1495 | 2.2584 | 2.4572 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0021971 | 0.0023817 | 0.0022901 | 0.0022901
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.3202 | 6.2583 | 16.5785 | 100 | 0.99332 | 1.519 |  | Specific volume (L/kgda) | 691.9314 | 785.4683 | 796.2333 | 796.2333 | 797.8282 | 858.8717 | 854.7372 | 836.5461 | 839.9533 | 838.262 | 839.252
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.3829 | 0 | 9.3829 | 65.719 | 2.2598 | 2.4589 |  | Enthalpy (J/gda) | -28.5429 | 7.3347 | 11.1593 | 11.1593 | 11.726 | 33.4136 | 31.9447 | 26.8208 | 28.4127 | 27.6225 | 27.9743
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9211 | 5.4432 | 14.3643 | 100 | 2.2625 | 2.4624 |  | Mass flow rate (kgda/s) | 0.28139 | 0.77054 | 0.77054 | 0.77054 | 0.77054 | 0.35564 | 0.41491 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.4609 | 12.3018 | 20.7626 | 100 | 2.2625 | 2.4624 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.0184 | 21.0184 | 12.2066 | 12.7778 | 19.1796 | 18.7479 | 23.3333 | 24.4444 | 23.8924 | 24.232
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.7029 | 0 | 9.7029 | 51.0891 | 2.2587 | 2.4575 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0048927 | 0.0050812 | 0.0049876 | 0.0049876
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0074 | 839.0074 | 813.8748 | 815.504 | 833.7629 | 832.5316 | 846.5039 | 849.9317 | 848.2283 | 849.198
[16 empty] | Enthalpy (J/gda) | 23.0217 | 31.8928 | 31.8928 | 22.9579 | 23.5371 | 30.0283 | 29.5906 | 35.9245 | 37.5324 | 36.7334 | 37.0782
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.75384 | 0.75384 | 0.75384 | 0.75384 | 0.34793 | 0.40591 | #N/A | #N/A | 0.47575 | 0.47575
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5732 | 25.5732 | 12.2072 | 12.7778 | 15.5904 | 16.4644 | 23.8889 | 25 | 24.4481 | 24.7899
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.01225 | 0.01225 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095185 | 0.0097082 | 0.0096139 | 0.0096139
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.9099 | 862.9099 | 819.8829 | 821.5223 | 829.6035 | 832.1147 | 854.3485 | 857.802 | 856.0862 | 857.0696
[16 empty] | Enthalpy (J/gda) | 69.8537 | 56.9493 | 56.9493 | 34.6208 | 35.2043 | 38.0804 | 38.9741 | 48.2629 | 49.8839 | 49.0785 | 49.4286
[16 empty] | Mass flow rate (kgda/s) | 0.27554 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47278 | 0.47278
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4777 | 24.4777 | 12.2068 | 12.7778 | 19.1811 | 18.75 | 23.3333 | 24.4444 | 23.8924 | 24.2318
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0064526 | 0.0066415 | 0.0065476 | 0.0065476
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.9862 | 850.9862 | 815.9007 | 817.5333 | 835.842 | 834.6093 | 848.6104 | 852.0467 | 850.3391 | 851.3109
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.3684 | 39.3684 | 26.8906 | 27.4712 | 33.9825 | 33.5441 | 39.8934 | 41.5057 | 40.7045 | 41.0501
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.75197 | 0.75197 | 0.75197 | 0.75197 | 0.34706 | 0.40491 | #N/A | #N/A | 0.47457 | 0.47457
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7742 | 23.7742 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.011806 | 0.011806 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 857.1123 | 857.1123 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 53.9677 | 53.9677 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.27605 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2066 | 12.7778 | 19.1799 | 18.7483 | 23.3333 | 24.4444 | 23.8924 | 24.2319
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051532 | 0.0053417 | 0.005248 | 0.005248
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 814.213 | 815.8428 | 834.11 | 832.8785 | 846.8556 | 850.2849 | 848.5808 | 849.5508
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 23.6145 | 24.194 | 30.6885 | 30.2507 | 36.5871 | 38.1958 | 37.3964 | 37.7413
[16 empty] | Mass flow rate (kgda/s) | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.34778 | 0.40575 | #N/A | #N/A | 0.47555 | 0.47555
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 |  | Zone 1 | Zone 2 |  | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible |  | Latent | Sensible |  | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load |  | Load | Load |  | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZC1sensible) |  | (QZ1latent) | (QZC2sensible) |  | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) |  | (kWh/h) | (kWh/h) |  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.2597 | 0 | 0 | 0 | 4.1447 | 4.4994 | 4.8772 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.2968 | 46.92 | 36.0391 | 21.1111 | 22.2222 | #N/A | #N/A
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.458 | 0 | 1.458 | 36.3949 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.002304 | 0.0023101 | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.399 | 5.9242 | 13.3232 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9314 | 691.9314 | 794.5867 | 794.5867 | 794.7981 | 907.0919 | 876.2548 | 836.6895 | 839.8569 | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1023 | 0 | 4.1023 | 53.4629 | 0 | 0 |  | Enthalpy (J/gda) | -28.5429 | -28.5429 | 7.9172 | 7.9172 | 7.9923 | 47.8758 | 36.9234 | 27.0925 | 28.2306 | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6354 | 4.5879 | 8.2233 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.11281 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.5938 | 5.2366 | 8.8305 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9553 | 16.9553 | 12.6643 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9545
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1575 | 0 | 4.1575 | 49.575 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0049701 | 0.0050294 | 0.005003 | 0.005003
[16 empty] | Specific volume (L/kgda) | 821.5658 | 826.1765 | 826.1765 | 813.9564 | 814.2796 | 814.2796 | 814.2796 | 846.6083 | 849.8616 | 848.4124 | 848.4267
[16 empty] | Enthalpy (J/gda) | 23.0217 | 25.392 | 25.392 | 21.0486 | 21.1635 | 21.1635 | 21.1635 | 36.1213 | 37.4006 | 36.8307 | 36.8358
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.13715 | 0.19854 | #N/A | #N/A | 0.057601 | 0.057601
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7259 | 25.7259 | 12.4805 | 12.7778 | 12.7778 | 12.7778 | 23.8889 | 25 | 24.3792 | 24.4858
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013486 | 0.013486 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0099076 | 0.010241 | 0.010055 | 0.010055
[16 empty] | Specific volume (L/kgda) | 872.9245 | 865.0327 | 865.0327 | 820.8802 | 821.7345 | 821.7345 | 821.7345 | 854.875 | 858.5261 | 856.4857 | 856.7924
[16 empty] | Enthalpy (J/gda) | 69.8537 | 60.2554 | 60.2554 | 35.3116 | 35.6156 | 35.6156 | 35.6156 | 49.2534 | 51.2422 | 50.1307 | 50.2399
[16 empty] | Mass flow rate (kgda/s) | 0.27533 | 0.53919 | 0.53919 | 0.53919 | 0.53919 | 0.25787 | 0.28132 | #N/A | #N/A | 0.26386 | 0.26386
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7375 | 24.7375 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0065301 | 0.0065896 | 0.0065631 | 0.0065631
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4494 | 850.4494 | 815.9814 | 816.3051 | 816.3051 | 816.3051 | 848.715 | 851.9764 | 850.5234 | 850.5376
[16 empty] | Enthalpy (J/gda) | 36.4912 | 37.2305 | 37.2305 | 24.975 | 25.0901 | 25.0901 | 25.0901 | 40.0906 | 41.3736 | 40.802 | 40.807
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.33473 | 0.33473 | 0.33473 | 0.33473 | 0.13676 | 0.19797 | #N/A | #N/A | 0.057335 | 0.057335
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1615 | 23.1615 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014755 | 0.014755 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.3233 | 859.3233 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.8393 | 60.8393 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061741 | 0.0062336 | 0.0062071 | 0.0062071
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 815.5192 | 815.8428 | 815.8428 | 815.8428 | 848.2342 | 851.4937 | 850.0416 | 850.0558
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 24.0789 | 24.194 | 24.194 | 24.194 | 39.1847 | 40.4668 | 39.8956 | 39.9007
[16 empty] | Mass flow rate (kgda/s) | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13685 | 0.1981 | #N/A | #N/A | 0.057395 | 0.057395
* n/a = not applicable

## DEEAP
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | AAON Detailed Energy and Economic Analysis Program 1.1.2 | [5 empty] | AAON Inc.
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | AAON
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DEEAP
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2012-12-10 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DEEAP/AAON
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | G latent gains updated slightly
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9309 |  | 0.58608 | 8.4133 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0029 | 29.3262 | 29.3262 | 29.9328 | 21.1111
| AE103 |  | 1.4649 | 0.586 | 0 | 0.78407 | 0 | 0.78407 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016042 | 0.0023041
| AE104 |  | 2.9303 | 0.58608 | 0 | 3.4882 | 2.0648 | 5.553 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.0586 | 858.9719 | 858.9719 | 860.6945 | 836.5805
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5 | 19.0845 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.2732 | 838.2732 | 831.7876 | 833.4546 | 846.4857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.8642 | 24.8642 | 14.9302 | 15.5066 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.010599 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 861.8387 | 861.8387 | 829.891 | 831.5517 | 856.6119
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9309 |  | 0.58608 | 8.3488 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1972 | 29.3262 | 29.3262 | 29.9328 | 21.1111 | 21.1111 | 21.4061
| AE203 |  | 1.4649 | 0.586 | 0 | 0.85303 | 0 | 0.85303 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0023041 | 0.0023041 | 0.0023041
| AE204 |  | 2.9303 | 0.58608 | 0 | 3.5587 | 2.0648 | 5.6234 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.6103 | 858.9719 | 858.9719 | 860.6945 | 836.5805 | 836.5805 | 837.4192
| AE205 |  | 1.4642 | 0.58608 | 0 | 1.9099 | 0 | 1.9099 | 44.3101 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 |  | 1.4644 | 0.58608 | 0 | 1.7005 | 0.9632 | 2.6637 | 99.9992 | [6 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A | 0.21683 | 0.21683
| AE226 |  | 1.4644 | 0.58608 | 0 | 1.5568 | 1.7782 | 3.335 | 99.9992 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9741 | 20.9741 | 18.5 | 19.0845 | 23.3333 | 23.3333 | 23.6304
| AE245 |  | 1.4642 | 0.58608 | 0 | 2.202 | 0 | 2.202 | 33.8389 | [6 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042845 | 0.0049611 | 0.0049611 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.8436 | 838.8436 | 831.7876 | 833.4546 | 846.4857 | 846.4857 | 847.3338
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A | 0.22893 | 0.22893
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.0648 | 25.0648 | 14.9302 | 15.5066 | 23.8889 | 23.8889 | 24.186
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.0106 | 0.011274 | 0.011274 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.4186 | 862.4186 | 829.891 | 831.5517 | 856.6119 | 856.6119 | 857.4688
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A | 0.23102 | 0.23102
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0415 | 24.0415 | 18.5041 | 19.0883 | 23.3333 | 23.3333 | 23.6303
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0058499 | 0.0058499 | 0.0058499 | 0.00585 | 0.0065284 | 0.0065284 | 0.0065284
[16 empty] | Specific volume (L/kgda) | 850.243 | 849.7105 | 849.7105 | 833.8783 | 835.549 | 848.6018 | 848.6018 | 849.4517
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11123 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | #N/A | 0.22835 | 0.22835
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4231 | 23.4231 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014534 | 0.014534 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.6718 | 859.6718 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10991 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33555 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.5025 | 19.0888 | 23.3333 | 23.3333 | 23.6304
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.005134 | 0.005134 | 0.005134
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 832.0238 | 833.6965 | 846.7192 | 846.7192 | 847.5674
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.34033 | 0.34033 | 0.34033 | 0.34033 | 0.34033 | #N/A | 0.22886 | 0.22886
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9309 |  | 0.58608 | 2.3449 |  | 0.87918 | 2.9697 | 0 | 0 | 0 | 24.7328 | 7.7075 | 8.3822 | AE301 | Dry bulb temperature (°C) | -29 | 3.3982 | 7.2222 | 7.2222 | 7.7845 | 29.2883 | 27.8298 | 21.1111 | 22.2222 | 21.6708 | 21.9663
| AE303 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 6.7082 | 0 | 6.7082 | 47.6873 | 2.2547 | 2.4515 |  | Humidity ratio (g/gda) | 0.00025894 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0021972 | 0.0023819 | 0.0022902 | 0.0022902
| AE304 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 10.2556 | 6.2947 | 16.5503 | 99.9992 | 0.98884 | 1.5135 |  | Specific volume (L/kgda) | 691.8414 | 785.2713 | 796.1298 | 796.1298 | 797.7263 | 858.7874 | 854.646 | 836.4373 | 839.8441 | 838.1531 | 838.9934
| AE305 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.3496 | 0 | 9.3496 | 65.3364 | 2.2561 | 2.4532 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.8688 | 5.4441 | 14.3129 | 99.9992 | 2.2588 | 2.4568 |  | Mass flow rate (kgda/s) | 0.28143 | 0.77064 | 0.77064 | 0.77064 | 0.77064 | 0.35568 | 0.41496 | #N/A | #N/A | 0.48921 | 0.48921
| AE326 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.3501 | 12.3442 | 20.6943 | 99.9992 | 2.2588 | 2.4568 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.9919 | 20.9919 | 12.2059 | 12.7778 | 19.1761 | 18.7408 | 23.3333 | 24.4444 | 23.8924 | 24.19
| AE345 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.6843 | 0 | 9.6843 | 50.7067 | 2.255 | 2.4518 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0048518 | 0.0050403 | 0.0049466 | 0.0049466
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.7678 | 838.7678 | 813.7138 | 815.3446 | 833.59 | 832.3485 | 846.3382 | 849.7654 | 848.0623 | 848.912
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.75399 | 0.75399 | 0.75399 | 0.75399 | 0.348 | 0.40599 | #N/A | #N/A | 0.47585 | 0.47585
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5414 | 25.5414 | 12.2065 | 12.7778 | 15.5808 | 16.4551 | 23.8889 | 25 | 24.4481 | 24.7459
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.012254 | 0.012254 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095186 | 0.0097084 | 0.0096141 | 0.0096141
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.7095 | 862.7095 | 819.774 | 821.4151 | 829.4677 | 831.9792 | 854.2369 | 857.69 | 855.9744 | 856.831
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27557 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47284 | 0.47284
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4471 | 24.4471 | 12.2061 | 12.7778 | 19.1778 | 18.7428 | 23.3333 | 24.4444 | 23.8924 | 24.1899
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0064187 | 0.0066076 | 0.0065137 | 0.0065137
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.7417 | 850.7417 | 815.7483 | 817.3825 | 835.6783 | 834.4349 | 848.4538 | 851.8894 | 850.1822 | 851.0336
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.34713 | 0.40498 | #N/A | #N/A | 0.47466 | 0.47466
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7478 | 23.7478 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.011794 | 0.011794 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 856.9076 | 856.9076 | 819.774 | 821.4151 | 839.8095 | 839.8095 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27609 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 819.774 | 821.4151 | 839.8095 | 838.5636 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2059 | 12.7778 | 19.1765 | 18.7411 | 23.3333 | 24.4444 | 23.8924 | 24.19
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0051194 | 0.0053078 | 0.0052142 | 0.0052142
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 814.0611 | 815.6925 | 833.9468 | 832.7047 | 846.6994 | 850.1279 | 848.4242 | 849.2742
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.34785 | 0.40582 | #N/A | #N/A | 0.47566 | 0.47566
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9309 |  | 0.58608 | 2.3448 |  | 0.87918 | 10.2479 | 0 | 0 | 0 | 4.1474 | 4.4963 | 4.8725 | AE401 | Dry bulb temperature (°C) | -29 | -28.9957 | 7.2222 | 7.2222 | 7.3083 | 46.9483 | 36.0548 | 21.1111 | 22.2222 | #N/A | #N/A | Aug 7, 2015: Blank entries replaced with "NA" by JN
| AE403 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 1.4663 | 0 | 1.4663 | 36.0086 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025894 | 0.00025911 | 0.00025911 | 0.00025911 | 0.00025861 | 0.00025861 | 0.00025861 | 0.0023034 | 0.0023096 | #N/A | #N/A | Makes output as blank rather than "0", as participant intended.
| AE404 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 7.3735 | 5.9745 | 13.348 | 99.9992 | 0 | 0 |  | Specific volume (L/kgda) | 691.8414 | 691.8536 | 794.4835 | 794.4835 | 794.7275 | 907.0536 | 876.1849 | 836.5796 | 839.7468 | #N/A | #N/A
| AE405 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1049 | 0 | 4.1049 | 53.1717 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.6094 | 4.6068 | 8.2162 | 99.9992 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.11283 | 0.1686 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.5586 | 5.2655 | 8.8241 | 99.9992 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9621 | 16.9621 | 12.6466 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.981
| AE445 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1596 | 0 | 4.1596 | 49.2421 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.00493 | 0.0049886 | 0.0049625 | 0.0049625
[16 empty] | Specific volume (L/kgda) | 821.4055 | 826.0373 | 826.0373 | 813.7497 | 814.1232 | 814.1236 | 814.1236 | 846.4437 | 849.6953 | 848.2496 | 848.3367
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.33612 | 0.33612 | 0.33612 | 0.33612 | 0.13729 | 0.19883 | #N/A | #N/A | 0.057974 | 0.057974
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.91 | 25.91 | 12.4612 | 12.7778 | 12.7777 | 12.7777 | 23.8889 | 25 | 24.3794 | 24.4935
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.01348 | 0.01348 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0098953 | 0.010229 | 0.010042 | 0.010042
[16 empty] | Specific volume (L/kgda) | 872.7897 | 864.9025 | 864.9025 | 820.7028 | 821.6126 | 821.6122 | 821.6122 | 854.7464 | 858.3966 | 856.3573 | 856.6857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27537 | 0.53988 | 0.53988 | 0.53988 | 0.53988 | 0.25821 | 0.28167 | #N/A | #N/A | 0.2645 | 0.2645
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.728 | 24.728 | 12.6468 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.004814 | 0.004814 | 0.004814 | 0.004814 | 0.0048143 | 0.0048143 | 0.006497 | 0.0065555 | 0.0065295 | 0.0065295
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.268 | 850.268 | 815.7831 | 816.1571 | 816.1574 | 816.1574 | 848.5594 | 851.8189 | 850.3696 | 850.3892
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.13689 | 0.19826 | #N/A | #N/A | 0.057705 | 0.057705
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1628 | 23.1628 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014721 | 0.014721 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.169 | 859.169 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27556 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6519 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0061387 | 0.0061973 | 0.0061712 | 0.0061712
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 815.3186 | 815.6925 | 815.6925 | 815.6925 | 848.0757 | 851.3333 | 849.8849 | 849.9045
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.13698 | 0.19839 | #N/A | #N/A | 0.057768 | 0.057768
* n/a = not applicable

## DeST
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Designer's Simulation Toolkit 2 | [5 empty] | Tsinghua University / Lawarence Berkeley National Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TsinghuaU-LBNL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DeST
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2013-11-21 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DeST/TsinghuaU-LBNL
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
Software:
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.93 |  | 0.5867 | 8.4521 | 0 | 0 | 0 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4073 | 29.0892 | 29.0892 | 29.6791 | 21.0991 | 21.0991
| AE103 |  | 1.4666 | 0.58971 | 0 | 0.7777 | 0 | 0.7777 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324
| AE104 |  | 2.9311 | 0.58578 | 0 | 3.5428 | 2.293 | 5.8358 | 98.66 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | -28.5113 | 8.55 | 33.4266 | 33.4266 | 34.02 | 27.1262 | 27.1262
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.722 | 20.722 | 18.4621 | 19.052 | 23.3479 | 23.3479
[16 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.83 | 31.83 | 29.54 | 30.14 | 36.26 | 36.26
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8861 | 24.8861 | 14.7013 | 15.2912 | 23.8764 | 23.8764
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012947 | 0.012947 | 0.010296 | 0.010296 | 0.010986 | 0.010986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 57.97 | 57.97 | 40.79 | 41.4 | 51.94 | 51.94
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 |  | 0.59 | 8.3847 | 0 | 0 | 0 | [6 empty] | AET201a | Dry bulb temperature (°C) | -29 | 4.604 | 29.0892 | 29.0892 | 29.6791 | 21.099 | 21.099 | 21.3939
| AE203 |  | 1.4666 | 0.58971 | 0 | 0.84533 | 0 | 0.84533 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324 | 0.0023324
| AE204 |  | 2.9311 | 0.58578 | 0 | 3.6078 | 2.2888 | 5.8966 | 98.62 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE205 |  | 1.47 | 0.59 | 0 | 1.9287 | 0 | 1.9287 | 44.81 | [6 empty] | Enthalpy (J/gda) | -28.5113 | 8.75 | 33.43 | 33.43 | 34.02 | 27.13 | 27.13 | 27.42
| AE206 |  | 1.47 | 0.59 | 0 | 1.7314 | 1.0866 | 2.8181 | 99.36 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 |  | 1.4655 | 0.58971 | 0 | 1.593 | 2.0498 | 3.6428 | 99.65 | [5 empty] | AET203a | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.4622 | 19.0521 | 23.3481 | 23.3481 | 23.643
| AE245 |  | 1.4663 | 0.58971 | 0 | 2.2158 | 0 | 2.2158 | 34.33 | [6 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 32.02 | 32.02 | 29.54 | 30.14 | 36.26 | 36.26 | 36.56
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET204a | Dry bulb temperature (°C) | 26.9 | 25.0935 | 25.0935 | 14.7219 | 15.3118 | 23.897 | 23.897 | 24.192
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012952 | 0.012952 | 0.010306 | 0.010306 | 0.010995 | 0.010995 | 0.011319
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 58.2 | 58.2 | 40.84 | 41.44 | 51.99 | 51.99 | 52.29
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET205a | Dry bulb temperature (°C) | 24.9 | 24.052 | 24.052 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6428
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0058987 | 0.0058987 | 0.0058987 | 0.0059 | 0.0065931 | 0.0065931 | 0.00659
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5 | 39.18 | 39.18 | 33.5 | 34.1 | 40.23 | 40.23 | 40.53
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET206a | Dry bulb temperature (°C) | 23 | 23.4067 | 23.4067 | 18.4552 | 19.0451 | 23.3378 | 23.3378 | 23.6328
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014484 | 0.014484 | 0.013227 | 0.013227 | 0.013921 | 0.013921 | 0.013921
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 60.36 | 60.36 | 52.06 | 52.67 | 58.85 | 58.85 | 59.16
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET226a | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4446 | 19.0345 | 23.3272 | 23.3272 | 23.6221
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.013257 | 0.013257 | 0.013951 | 0.013951 | 0.013951
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 52.13 | 52.74 | 58.92 | 58.92 | 58.92
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET245a | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6429
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0052044 | 0.0052044
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.51 | 36.51 | 36.51 | 29.98 | 30.58 | 36.7 | 36.7 | 36.7
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 3.58 | 0 | 0 | 0 |  | 7.4721 | 8.0774 | AET301 | Dry bulb temperature (°C) | -29 | 2.3874 | 7.22 | 7.22 | 7.8099 | 29.6699 | 28.084 | 21.111 | 22.222 | 21.7092 | 22.0042
| AE303 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 6.4595 | 0 | 6.4595 | 48.22 | 2.1363 | 2.3 |  | Humidity ratio (g/gda) | 0.00026 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0022251 | 0.0024213 | 0.0023308 | 0.0023308
| AE304 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 10.0587 | 7.0108 | 17.0695 | 95.49 | 0.85904 | 1.3509 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE305 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.1806 | 0 | 9.1806 | 65.84 | 2.1367 | 2.3017 |  | Enthalpy (J/gda) | -28.5113 | 6.24 | 11.11 | 11.11 | 11.71 | 33.74 | 32.14 | 26.8658 | 28.4854 | 27.74 | 28.04
| AE306 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.6987 | 6.1035 | 14.8022 | 96.21 | 2.1374 | 2.3004 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
| AE326 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.1141 | 12.8792 | 20.9933 | 98.89 | 2.1374 | 2.3005 | AET303 | Dry bulb temperature (°C) | 15.5 | 20.87 | 20.87 | 12.2049 | 12.7948 | 19.05 | 18.57 | 23.333 | 24.444 | 23.9462 | 24.2412
| AE345 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.4684 | 0 | 9.4684 | 51.33 | 2.1374 | 2.3005 |  | Humidity ratio (g/gda) | 0.002948 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0049298 | 0.0051345 | 0.00504 | 0.0049864
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.73 | 31.73 | 22.95 | 23.55 | 29.88 | 29.4 | 35.99 | 37.63 | 36.89 | 37.19
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET304 | Dry bulb temperature (°C) | 26.9 | 25.5957 | 25.5957 | 12.2047 | 12.7946 | 15.3101 | 16.1852 | 23.889 | 25 | 24.502 | 24.7969
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012182 | 0.012182 | 0.0084426 | 0.0084426 | 0.0084426 | 0.0084426 | 0.00914 | 0.00934 | 0.0092505 | 0.0092505
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 56.75 | 56.75 | 33.56 | 34.16 | 36.73 | 37.62 | 47.2602 | 48.9046 | 48.17 | 48.47
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET305 | Dry bulb temperature (°C) | 24.9 | 24.4854 | 24.4854 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0064918 | 0.0066965 | 0.006602 | 0.006602
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 39.36 | 39.36 | 26.89 | 27.49 | 33.84 | 33.36 | 39.96 | 41.61 | 40.86 | 41.16
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET306 | Dry bulb temperature (°C) | 23 | 23.7552 | 23.7552 | 12.1759 | 12.7658 | 19.0246 | 18.5398 | 23.333 | 24.444 | 23.9171 | 24.2121
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.011752 | 0.011752 | 0.0084916 | 0.0084916 | 0.0084916 | 0.0084916 | 0.00919 | 0.00939 | 0.0092962 | 0.009673
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 53.77 | 53.77 | 33.66 | 34.26 | 40.65 | 40.15 | 46.81 | 48.47 | 47.69 | 47.99
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2038 | 12.7937 | 19.0525 | 18.5677 | 23.333 | 24.444 | 23.9451 | 24.24
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0094417 | 0.00965 | 0.009552 | 0.009552
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 34.33 | 34.93 | 41.32 | 40.8278 | 47.45 | 49.14 | 48.37 | 48.37
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0054091 | 0.0053146 | 0.0053146
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 23.64 | 24.24 | 30.55 | 30.07 | 36.68 | 38.33 | 37.59 | 37.59
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 10.31 | 0 | 0 | 0 |  | 4.5019 | 4.891 | AET401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3073 | 46.8548 | 35.9521 | 21.111 | 22.222 | #N/A | #N/A | Aug 7, 2015: Entries replaced with "NA" by JN
| AE403 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 1.4433 | 0 | 1.4433 | 36.39 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.0023324 | 0.0023296 | #N/A | #N/A | Air property output not appropriate for 0 RA mass flow.
| AE404 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 7.4502 | 6.5805 | 14.0307 | 97.24 | 0 | 0 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | #N/A | #N/A
| AE405 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1432 | 0 | 4.1432 | 53.52 | 0 | 0 |  | Enthalpy (J/gda) | -28.5113 | -28.5113 | 7.91 | 7.91 | 8 | 47.76 | 36.8 | 27.1382 | 28.2525 | #N/A | #N/A
| AE406 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.6269 | 4.9686 | 8.5955 | 99.38 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.5745 | 5.6327 | 9.2072 | 99.58 | 0 | 0 | AET403 | Dry bulb temperature (°C) | 15.5 | 16.888 | 16.888 | 12.6699 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.005 | 24.0094
| AE445 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1914 | 0 | 4.1914 | 49.78 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002948 | 0.00329 | 0.00329 | 0.00329 | 0.0032876 | 0.0032876 | 0.0032876 | 0.0049958 | 0.0050706 | 0.00504 | 0.00504
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 25.3 | 25.3 | 21.03 | 21.16 | 21.16 | 21.16 | 36.1476 | 37.47 | 36.95 | 36.95
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.13832 | 0.20018 | #N/A | #N/A | 0.055336 | 0.055336
[15 empty] | AET404 | Dry bulb temperature (°C) | 26.9 | 25.7508 | 25.7508 | 12.4633 | 12.7916 | 12.7916 | 12.7916 | 23.889 | 25 | 24.48 | 24.5817
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.013454 | 0.013454 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0096515 | 0.0099979 | 0.0098321 | 0.0098321
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 60.15 | 60.15 | 34.6 | 34.93 | 34.93 | 34.93 | 48.56 | 50.58 | 49.63 | 49.73
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54925 | 0.54925 | 0.54925 | 0.54925 | 0.26284 | 0.28641 | #N/A | #N/A | 0.26609 | 0.26609
[15 empty] | AET405 | Dry bulb temperature (°C) | 24.9 | 24.7517 | 24.7517 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 23.9959 | 24.0003
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.0065572 | 0.006633 | 0.0065986 | 0.0065986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 37.2162 | 37.2162 | 24.97 | 25.1 | 25.1 | 25.1 | 40.1156 | 41.45 | 40.92 | 40.92
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13829 | 0.20003 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET406 | Dry bulb temperature (°C) | 23 | 23.1638 | 23.1638 | 12.6693 | 12.7939 | 12.7939 | 12.7939 | 23.333 | 24.444 | 24.0041 | 24.0085
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014845 | 0.014845 | 0.0090684 | 0.0090684 | 0.0090684 | 0.0090684 | 0.010775 | 0.010849 | 0.010819 | 0.010819
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 61.03 | 61.03 | 35.62 | 35.74 | 35.74 | 35.74 | 50.85 | 52.18 | 51.65 | 51.65
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055191 | 0.055191
[15 empty] | AET426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6574 | 12.782 | 12.782 | 12.782 | 23.333 | 24.444 | 23.9922 | 23.9966
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0090802 | 0.0090802 | 0.0090802 | 0.0090802 | 0.010787 | 0.010861 | 0.010831 | 0.010831
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 35.63 | 35.76 | 35.76 | 35.76 | 50.88 | 52.2078 | 51.67 | 51.67
[16 empty] | Mass flow rate (kgda/s) | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.0049 | 24.0093
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0062162 | 0.006292 | 0.006261 | 0.006261
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 24.11 | 24.24 | 24.24 | 24.24 | 39.26 | 40.58 | 40.05 | 40.06
[16 empty] | Mass flow rate (kgda/s) | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
* n/a = not applicable

## DOE22
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | DOE-2.2 V48L | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DOE-2.2
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-03-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DOE-2.2/NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | DOE2.2 Design Day
| Version: | 2.2-48L
| Date: | 2015-03-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone |  | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible |  | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Load |  | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) |  | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh) |  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.7675 | 0 | 0 | 0 | 6.4033 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3889 | 29.2222 | 29.2222 | 29.2222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.77693 | 0 | 0.77693 | 31.6536 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.521 | 2.0119 | 5.5329 | 99.9615 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11954 | 0.35862 | 0.35862 | 0.35862 | 0.35862 | 0.35862 | 0.23908
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.6889 | 21.2778 | 19 | 19 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11241 | 0.33724 | 0.33724 | 0.33724 | 0.33724 | 0.33724 | 0.22483
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.9056 | 25.5 | 15.2222 | 15.2222 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0132 | 0.0132 | 0.0108 | 0.0108 | 0.0115 | 0.0115
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10928 | 0.32785 | 0.32785 | 0.32785 | 0.32785 | 0.32785 | 0.21857
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.7092 | 0 | 0 | 0 | 6.6125 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6111 | 28.6667 | 28.6667 | #N/A | 21.1111 | 21.1111 | 21.3889
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.84024 | 0 | 0.84024 | 32.7731 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022 | 0.0022
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5901 | 2.1212 | 5.7114 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9085 | 0 | 1.9085 | 44.8531 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7233 | 1.0082 | 2.7314 | 99.9317 | [6 empty] | Mass flow rate (kgda/s) | 0.1197 | 0.35909 | 0.35909 | 0.35909 | 0.35909 | 0.35909 | 0.2394 | 0.2394
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5972 | 1.8077 | 3.4049 | 99.9317 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.8889 | 20.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.1878 | 0 | 2.1878 | 34.2864 | [6 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11256 | 0.33768 | 0.33768 | 0.33768 | 0.33768 | 0.33768 | 0.22512 | 0.22512
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.1111 | 25.1111 | 14.6111 | #N/A | 23.8889 | 23.8889 | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.013 | 0.013 | 0.0104 | 0.0104 | 0.0111 | 0.0111 | 0.0111
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10948 | 0.32843 | 0.32843 | 0.32843 | 0.32843 | 0.32843 | 0.21895 | 0.21895
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0556 | 24.0556 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0059 | 0.0059 | 0.0059 | 0.0059 | 0.0066 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11109 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.22218 | 0.22218
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4444 | 23.4444 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0145 | 0.0145 | 0.0133 | 0.0133 | 0.014 | 0.014 | 0.014
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10983 | 0.32948 | 0.32948 | 0.32948 | 0.32948 | 0.32948 | 0.21965 | 0.21965
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0133 | 0.0133 | 0.0141 | 0.0141 | 0.0141
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.21961 | 0.21961
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0052 | 0.0052 | 0.0052
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.22206 | 0.22206
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 3.7882 | 0 | 0 | 0 | 23.9613 | 7.706 | 8.3763 | AE301 | Dry bulb temperature (°C) | -29 | #N/A | 7.2222 | 7.2222 | 7.7778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | 21.9444
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.4197 | 0 | 6.4197 | 47.9247 | 2.15 | 2.3194 |  | Humidity ratio (g/gda) | 0.0003 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | #N/A | #N/A | 0.0022 | 0.0022
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 9.8897 | 6.214 | 16.1037 | 100 | 0.79774 | 1.2681 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9287 | 0 | 8.9287 | 65.5319 | 2.0723 | 2.2232 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.5975 | 5.4338 | 14.0314 | 100 | 2.1107 | 2.2695 |  | Mass flow rate (kgda/s) | 0.29649 | 0.77088 | 0.77088 | 0.77088 | 0.77088 | 0.35579 | 0.41509 | #N/A | #N/A | 0.47438 | 0.47438
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.2315 | 11.7123 | 19.9438 | 100 | 2.1256 | 2.2886 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8333 | 20.8333 | 12.1667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.2222
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.2851 | 0 | 9.2851 | 51.1359 | 2.0887 | 2.2414 |  | Humidity ratio (g/gda) | 0.0029 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | #N/A | #N/A | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28151 | 0.73193 | 0.73193 | 0.73193 | 0.73193 | 0.33781 | 0.39412 | #N/A | #N/A | 0.45042 | 0.45042
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5556 | 25.5556 | 12.2222 | 12.8333 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.7222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0124 | 0.0124 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.2735 | 0.71109 | 0.71109 | 0.71109 | 0.71109 | 0.32819 | 0.38289 | #N/A | #N/A | 0.43759 | 0.43759
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4444 | 24.4444 | 12.2778 | 12.8889 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | #N/A | #N/A | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27741 | 0.72126 | 0.72126 | 0.72126 | 0.72126 | 0.33289 | 0.38837 | #N/A | #N/A | 0.44385 | 0.44385
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7222 | 23.7222 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.012 | 0.012 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27538 | 0.716 | 0.716 | 0.716 | 0.716 | 0.33046 | 0.38554 | n/a* | n/a* | 0.44061 | 0.44061
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.32941 | 0.38431 | #N/A | #N/A | 0.43921 | 0.43921
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0053 | 0.0053
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.33309 | 0.3886 | #N/A | #N/A | 0.44412 | 0.44412
* =na()
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo) | Sep 6, 2015: AE401 Tma deleted per email with M. Kennedy of Sep 3, 2015.
| AE401 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 10.8176 | 0 | 0 | 0 | 4.8015 | 4.5839 | 5.0147 | AE401 | Dry bulb temperature (°C) | -29 | #N/A | 7.2222 | 7.2222 | 7.2778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | #N/A | #N/A
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.4021 | 0 | 1.4021 | 34.2896 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | #N/A | #N/A | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.4587 | 5.9168 | 13.3755 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1138 | 0 | 4.1138 | 51.8548 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6801 | 4.4948 | 8.1749 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.11883 | 0.17824 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6423 | 5.1885 | 8.8308 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7778 | 16.7778 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 7.6667
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1701 | 0 | 4.1701 | 49.664 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | #N/A | #N/A | 0.0041 | 0.0041
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28597 | 0.33688 | 0.33688 | 0.33688 | 0.33688 | 0.13784 | 0.19904 | #N/A | #N/A | 0.050903 | 0.050903
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.7222 | 25.7222 | 12.4444 | 12.7778 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.5 | -0.72222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0135 | 0.0135 | 0.009 | 0.009 | 0.009 | 0.009 | #N/A | #N/A | 0.0101 | 0.0101
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27289 | 0.53541 | 0.53541 | 0.53541 | 0.53541 | 0.25542 | 0.27998 | #N/A | #N/A | 0.26252 | 0.26252
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.7222 | 24.7222 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.27778
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | #N/A | #N/A | 0.0059 | 0.0059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27761 | 0.33591 | 0.33591 | 0.33591 | 0.33591 | 0.13714 | 0.19877 | #N/A | #N/A | 0.058299 | 0.058299
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1667 | 23.1667 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.2778
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0147 | 0.0147 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0103 | 0.0103
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27474 | 0.32968 | 0.32968 | 0.32968 | 0.32968 | 0.13462 | 0.19506 | #N/A | #N/A | 0.054947 | 0.054947
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.4444
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0104 | 0.0104
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.13451 | 0.1949 | #N/A | #N/A | 0.054902 | 0.054902
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.44444
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0057 | 0.0057
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.13712 | 0.19874 | #N/A | #N/A | 0.05829 | 0.05829
* =na()

## Eplus
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | EnergyPlus 8.2.0 | [5 empty] | GARD Analytics
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | GARD
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | EnergyPlus
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-01-14 |  | Model / Organization Indentifier for Charts (short): |  |  |  | EnergyPlus/GARD
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | EnergyPlus
| Version: | 8.2.0
| Date: | 1/14/2015 w/ post proc correction 20Aug2015, see Q130
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 |  | 0.5861 | 8.4534 | 0 | 0 | 0 | 6.5151 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4539 | 29.0494 | 29.0494 | 29.6355 | 21.1183 | 21.1183
| AE103 |  | 1.465 | 0.5861 | 0 | 0.76554 | 0 | 0.76554 | 32.5142 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887
| AE104 |  | 2.931 | 0.5861 | 0 | 3.4986 | 2.1742 | 5.6728 | 99.6158 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5207 | 33.309 | 33.309 | 33.8997 | 27.0344 | 27.0344
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.726 | 20.726 | 18.5095 | 19.0928 | 23.3293 | 23.3293
[16 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7063 | 31.7063 | 29.4615 | 30.0522 | 36.0616 | 36.0616
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8949 | 24.8949 | 14.9265 | 15.5032 | 23.8823 | 23.8823
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013079 | 0.013079 | 0.010558 | 0.010558 | 0.011233 | 0.011233
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.3316 | 58.3316 | 41.6971 | 42.2878 | 52.5907 | 52.5907
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | -2.931 |  | 0.5861 | 8.387 | 8.048e-08 | 1.8383e-05 | 1.8464e-05 | 6.5149 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6476 | 29.0498 | 29.0498 | 29.6359 | 21.1187 | 21.1187 | 21.4084
| AE203 |  | 1.465 | 0.5861 | 0 | 0.83269 | 0 | 0.83269 | 32.5148 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887 | 0.0022887
| AE204 |  | 2.931 | 0.5861 | 0 | 3.5657 | 2.1735 | 5.7392 | 99.6397 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE205 |  | 1.465 | 0.5861 | 0 | 1.9127 | 0 | 1.9127 | 44.111 | [6 empty] | Enthalpy (J/gda) | -28.5066 | 8.7159 | 33.3094 | 33.3094 | 33.9001 | 27.0348 | 27.0348 | 27.3272
| AE206 |  | 1.465 | 0.5861 | 0 | 1.6967 | 1.0417 | 2.7383 | 99.0255 | [6 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
| AE226 |  | 1.465 | 0.5861 | 0 | 1.5548 | 1.8634 | 3.4182 | 99.8073 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9201 | 20.9201 | 18.5093 | 19.0925 | 23.3288 | 23.3288 | 23.6201
| AE245 |  | 1.465 | 0.5861 | 0 | 2.2073 | 0 | 2.2073 | 33.9915 | [6 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.9029 | 31.9029 | 29.4612 | 30.0519 | 36.0611 | 36.0611 | 36.3565
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0862 | 25.0862 | 14.9264 | 15.5031 | 23.8822 | 23.8822 | 24.1702
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013081 | 0.013081 | 0.010561 | 0.010561 | 0.011236 | 0.011236 | 0.011236
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.5327 | 58.5327 | 41.7033 | 42.2941 | 52.5969 | 52.5969 | 52.8923
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0456 | 24.0456 | 18.5236 | 19.1052 | 23.3296 | 23.3296 | 23.62
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.005832 | 0.005832 | 0.005832 | 0.005832 | 0.0065075 | 0.0065075 | 0.0065075
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.0081 | 39.0081 | 33.3995 | 33.9902 | 39.9994 | 39.9994 | 40.2948
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4106 | 23.4106 | 18.5888 | 19.1626 | 23.33 | 23.33 | 23.6165
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014507 | 0.014507 | 0.013302 | 0.013302 | 0.013978 | 0.013978 | 0.013978
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 60.4363 | 60.4363 | 52.4066 | 52.9973 | 59.0066 | 59.0066 | 59.302
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5897 | 19.1634 | 23.33 | 23.33 | 23.6164
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.01341 | 0.01341 | 0.014086 | 0.014086 | 0.014086
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 52.6815 | 53.2723 | 59.2816 | 59.2816 | 59.5769
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5115 | 19.0946 | 23.3294 | 23.3294 | 23.6205
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0051565 | 0.0051565
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 29.962 | 30.5528 | 36.562 | 36.562 | 36.8573
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
* n/a = not applicable
Note: Aug 2015 - Preheat Coil Outlet Temp was linked to wrong output variable, i.e. Preheat Coil Outlet Setpoint Temp. Link corrected.
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 3.5747 | 0 | 0 | 0 | 23.8906 | 7.5057 | 8.1309 | AE301 | Dry bulb temperature (°C) | -29 | 2.4185 | 7.22 | 7.22 | 7.8063 | 29.649 | 28.0886 | 21.1299 | 22.2485 | 21.6893 | 21.982
| AE303 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 6.4764 | 0 | 6.4764 | 47.4569 | 2.1827 | 2.3607 |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0021723 | 0.0023649 | 0.0022686 | 0.0022686
| AE304 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 10.1563 | 6.6217 | 16.778 | 99.1258 | 0.94208 | 1.4552 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE305 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.1994 | 0 | 9.1994 | 64.909 | 2.193 | 2.3739 |  | Enthalpy (J/gda) | -28.5066 | 6.1776 | 11.0156 | 11.0156 | 11.6064 | 33.6155 | 32.0433 | 26.7502 | 28.3684 | 27.5593 | 27.8547
| AE306 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.7437 | 5.7489 | 14.4926 | 99.2475 | 2.2136 | 2.4005 |  | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
| AE326 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.2481 | 12.5316 | 20.7797 | 99.9275 | 2.2141 | 2.4012 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8531 | 20.8531 | 12.197 | 12.7804 | 19.1013 | 18.6401 | 23.3385 | 24.4517 | 23.8952 | 24.1865
| AE345 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.5096 | 0 | 9.5096 | 50.9944 | 2.1849 | 2.3635 |  | Humidity ratio (g/gda) | 0.0029334 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0048436 | 0.0050359 | 0.0049397 | 0.0049397
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.5397 | 31.5397 | 22.7746 | 23.3653 | 29.7658 | 29.2989 | 35.775 | 37.3934 | 36.5842 | 36.8796
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5756 | 25.5756 | 12.2012 | 12.7797 | 15.485 | 16.3615 | 23.8914 | 25.0047 | 24.4481 | 24.737
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012324 | 0.012324 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0094477 | 0.00964 | 0.0095439 | 0.0095439
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 57.1062 | 57.1062 | 34.3988 | 34.9895 | 37.752 | 38.6471 | 48.0548 | 49.6829 | 48.8688 | 49.1642
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4598 | 24.4598 | 12.1989 | 12.7806 | 19.1133 | 18.6566 | 23.3385 | 24.4517 | 23.8952 | 24.1857
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0063912 | 0.0065835 | 0.0064873 | 0.0064873
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.1326 | 39.1326 | 26.6821 | 27.2729 | 33.7034 | 33.2397 | 39.7127 | 41.3343 | 40.5235 | 40.8188
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7256 | 23.7256 | 12.2019 | 12.7804 | 19.1369 | 18.6889 | 23.3385 | 24.4517 | 23.8952 | 24.1841
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.011867 | 0.011867 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0094593 | 0.0096517 | 0.0095555 | 0.0095555
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 54.0424 | 54.0424 | 34.4281 | 35.0189 | 41.5099 | 41.0525 | 47.5192 | 49.1471 | 48.3331 | 48.6285
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2017 | 12.7801 | 19.1373 | 18.6896 | 23.3385 | 24.4517 | 23.8952 | 24.184
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0095202 | 0.0097126 | 0.0096164 | 0.0096164
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 34.5816 | 35.1723 | 41.6648 | 41.2075 | 47.6741 | 49.3022 | 48.4881 | 48.7835
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.197 | 12.78 | 19.1037 | 18.6434 | 23.3385 | 24.4517 | 23.8952 | 24.1863
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0053488 | 0.0052527 | 0.0052527
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 23.5643 | 24.155 | 30.562 | 30.0957 | 36.5712 | 38.1903 | 37.3807 | 37.6761
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
* n/a = not applicable
Note: Aug 2015 - Preheat Coil Outlet Temp was linked to wrong output variable, i.e. Preheat Coil Outlet Setpoint Temp. Link corrected.
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 10.343 | 0 | 0 | 0 | 4.1501 | 4.5034 | 4.9022 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2031 | 7.2031 | 7.2901 | 46.6969 | 35.8886 | 21.1452 | 22.2593 | #N/A | #N/A | Aug 21, 2015: Entries replaced with "NA" by JN
| AE403 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 1.3987 | 0 | 1.3987 | 35.8492 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022887 | 0.0022872 | #N/A | #N/A | Air property output not appropriate for 0 RA mass flow.
| AE404 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 7.3706 | 6.3173 | 13.6879 | 98.7059 | 0 | 0 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | #DIV/0! | #DIV/0! | #N/A | #N/A
| AE405 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.0977 | 0 | 4.0977 | 52.7786 | 0 | 0 |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.8892 | 7.8892 | 7.9766 | 47.5931 | 36.7273 | 27.0614 | 28.1819 | #N/A | #N/A
| AE406 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5834 | 4.84 | 8.4235 | 99.7649 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.11367 | 0.17051 | n/a* | n/a* | 0 | 0
| AE426 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5416 | 5.3897 | 8.9313 | 99.9528 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7888 | 16.7888 | 12.6598 | 12.78 | 12.78 | 12.78 | 23.3441 | 24.4608 | 23.9508 | 23.9546
| AE445 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.1451 | 0 | 4.1451 | 49.4632 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029334 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.0049254 | 0.0049851 | 0.0049578 | 0.0049578
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 25.0767 | 25.0767 | 20.9029 | 21.0244 | 21.0244 | 21.0244 | 35.9889 | 37.2733 | 36.6866 | 36.6905
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.13676 | 0.19796 | n/a* | n/a* | 0.050546 | 0.050919
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7623 | 25.7623 | 12.4725 | 12.7797 | 12.7808 | 12.7808 | 23.9001 | 25.0168 | 24.3846 | 24.4749
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013543 | 0.013543 | 0.0088944 | 0.0088944 | 0.0088944 | 0.0088944 | 0.009788 | 0.010124 | 0.0099335 | 0.0099335
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 60.4045 | 60.4045 | 34.9834 | 35.2972 | 35.2982 | 35.2982 | 48.93 | 50.9269 | 49.7961 | 49.8885
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.53845 | 0.53845 | 0.53845 | 0.53845 | 0.25766 | 0.28079 | n/a* | n/a* | 0.25427 | 0.25427
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.758 | 24.758 | 12.661 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9497 | 23.9534
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0064728 | 0.0065327 | 0.0065053 | 0.0065053
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 37.0618 | 37.0618 | 24.7987 | 24.9195 | 24.9195 | 24.9195 | 39.9261 | 41.2141 | 40.6246 | 40.6284
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.13638 | 0.19741 | n/a* | n/a* | 0.049606 | 0.049969
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1345 | 23.1345 | 12.6637 | 12.78 | 12.7899 | 12.7899 | 23.3441 | 24.4607 | 23.9468 | 23.95
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014891 | 0.014891 | 0.0091064 | 0.0091064 | 0.0091018 | 0.0091018 | 0.010803 | 0.010863 | 0.010835 | 0.010835
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 61.1277 | 61.1277 | 35.7139 | 35.8327 | 35.8312 | 35.8312 | 50.9427 | 52.2412 | 51.6436 | 51.6468
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.13543 | 0.19602 | n/a* | n/a* | 0.047271 | 0.047271
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6638 | 12.7801 | 12.79 | 12.79 | 23.3441 | 24.4607 | 23.9468 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0091238 | 0.0091238 | 0.009124 | 0.009124 | 0.010825 | 0.010885 | 0.010858 | 0.010858
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 35.758 | 35.8769 | 35.8875 | 35.8875 | 50.9995 | 52.2981 | 51.7004 | 51.7036
[16 empty] | Mass flow rate (kgda/s) | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.13543 | 0.19601 | n/a* | n/a* | 0.047261 | 0.047261
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6608 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9499 | 23.9536
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0061691 | 0.006229 | 0.0062016 | 0.0062016
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 24.0343 | 24.1552 | 24.1552 | 24.1552 | 39.1535 | 40.4408 | 39.8519 | 39.8557
[16 empty] | Mass flow rate (kgda/s) | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.13645 | 0.19752 | n/a* | n/a* | 0.049791 | 0.050091
* n/a = not applicable
EnergyPlus 4-Pipe Fan Coil
| Last Hour of Simulation - Summary Outputs - Fan Coil Air System | [13 empty] | EnergyPlus 4-Pipe Fan Coil
|  | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AET101a | -2.931 | 0.5861 | 8.4527 | 0 | 0 | 0 | 29.9418 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4496 | 29.6291 | 5.0358 | 29.6291 | 21.1119 | 21.1119
| AET103a | 1.465 | 0.5861 | 0 | 0.76509 | 0 | 0.76509 | 31.3427 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022888 | 0.0022888
| AET104a | 2.931 | 0.5861 | 0 | 3.4965 | 2.1082 | 5.6047 | 98.0115 | [7 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5164 | 33.8933 | 9.1072 | 33.8933 | 27.0279 | 27.0279
| Notes: | [14 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
| 1) EnergyPlus 4-Pipe Fan Coil model only allows a blow-through configuration with the heating coil placed after the cooling coil | [13 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.7283 | 19.0965 | 19.0965 | 19.0965 | 23.3328 | 23.3328
| 2) Outdoor air and exhaust air interchange takes place automatically within the fan coil unit without the aid of an exhaust fan | [14 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049598 | 0.0049598
| and therefore the fan coil return air flow rate is always equal to the supply air flow rate | [14 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7087 | 30.0559 | 30.0559 | 30.0559 | 36.0651 | 36.0651
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8985 | 15.5126 | 15.5126 | 15.5126 | 23.8882 | 23.8882
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013235 | 0.010791 | 0.010791 | 0.010791 | 0.011466 | 0.011466
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.7307 | 42.8864 | 42.8864 | 42.8864 | 53.1892 | 53.1892
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
* n/a = not applicable

## IES-VE
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Integrated Environmental Solutions Virtual Environment IES-VE 2014.2 | [5 empty] | Integrated Environmental Solutions
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | IES
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | IES-VE
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-02-20 |  | Model / Organization Indentifier for Charts (short): |  |  |  | IES-VE/IES
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | IES-VE
| Version: | <VE>2014.2
| Date: | 2015-02-20
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.513 | 0 | 0 | 0 | 6.75 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4073 | 28.994 | 28.994 | 29.5758 | 21.111 | 21.111
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.762 | 0 | 0.762 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.00237 | 0.002374
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.48 | 2.127 | 5.607 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7214 | 20.7214 | 18.5195 | 19.1013 | 23.3321 | 23.3321
[16 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8934 | 24.8934 | 14.8437 | 15.4255 | 23.8901 | 23.8901
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013136 | 0.013136 | 0.010581 | 0.010581 | 0.011285 | 0.011285
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.446 | 0 | 0 | 0 | 6.75 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6011 | 28.9937 | 28.9937 | 29.5755 | 21.1107 | 21.1107 | 21.4016
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.83 | 0 | 0.83 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.002374 | 0.002374 | 0.002374
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.547 | 2.128 | 5.675 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.915 | 0 | 1.915 | 44.59 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.695 | 1 | 2.696 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.552 | 1.825 | 3.377 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9148 | 20.9148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
| AE245 | 0 | 1.564 | 0.5861 | 0 | 2.21 | 0 | 2.21 | 34.06 | [6 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0861 | 25.0861 | 14.8418 | 15.4236 | 23.8882 | 23.8882 | 24.1791
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013135 | 0.013135 | 0.01058 | 0.01058 | 0.011284 | 0.011284 | 0.011284
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0481 | 24.0481 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005916 | 0.005916 | 0.005916 | 0.005916 | 0.00662 | 0.00662 | 0.00662
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4148 | 23.4148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014624 | 0.014624 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005212 | 0.005212
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
* n/a = not applicable
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 3.647 | 0 | 0 | 0 | 24.65 | 7.539 | 8.17 | AE301 | Dry bulb temperature (°C) | -29 | 2.3582 | 7.22 | 7.22 | 7.8018 | 29.5754 | 28.026 | 21.1106 | 22.221 | 21.6658 | 21.9567
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.483 | 0 | 6.483 | 48.02 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.000262 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.002253 | 0.002454 | 0.002354 | 0.002354
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.034 | 6.629 | 16.662 | 100 | 0.915 | 1.419 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.195 | 0 | 9.195 | 65.57 | 2.188 | 2.366 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.652 | 5.75 | 14.403 | 100 | 2.188 | 2.366 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307 | Aug 7, 2015: Zone air mass flows set to "NA" by JN
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.096 | 12.558 | 20.654 | 100 | 2.188 | 2.366 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8401 | 20.8401 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776 | Matches most recent output template.
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.529 | 0 | 9.529 | 51.1 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.002947 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004938 | 0.005139 | 0.005039 | 0.005039
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5681 | 25.5681 | 12.199 | 12.7808 | 15.4247 | 16.2939 | 23.8893 | 25.001 | 24.4447 | 24.7356
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.012443 | 0.012443 | 0.008891 | 0.008891 | 0.008891 | 0.008891 | 0.009595 | 0.009796 | 0.009695 | 0.009695
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4554 | 24.4554 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.006499 | 0.0067 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7247 | 23.7247 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.011971 | 0.011971 | 0.008888 | 0.008888 | 0.008888 | 0.008888 | 0.009592 | 0.009793 | 0.009693 | 0.009693
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.008909 | 0.008909 | 0.008909 | 0.008909 | 0.009613 | 0.009814 | 0.009713 | 0.009713
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005413 | 0.005312 | 0.005312
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.451 | 0 | 0 | 0 | 4.17 | 4.524 | 4.926 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3103 | 46.5047 | 35.7662 | 21.1103 | 22.2208 | #N/A | #N/A
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.399 | 0 | 1.399 | 35.98 | 0 | 0 |  | Humidity ratio (g/gda) | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.002374 | 0.002374 | #N/A | #N/A
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.333 | 6.313 | 13.645 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.111 | 0 | 4.111 | 53.05 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.567 | 4.868 | 8.435 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.516 | 5.456 | 8.972 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7759 | 16.7759 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.16 | 0 | 4.16 | 49.58 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002947 | 0.003265 | 0.003265 | 0.00326 | 0.003265 | 0.003265 | 0.003265 | 0.005021 | 0.005084 | 0.005037 | 0.005055
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05055 | 0.05037
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.744 | 25.744 | 12.47 | 12.7846 | 12.7846 | 12.7846 | 23.8934 | 25.0043 | 24.3776 | 24.4762
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013639 | 0.013639 | 0.009056 | 0.009056 | 0.009056 | 0.009056 | 0.00998 | 0.010327 | 0.010131 | 0.010131
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54137 | 0.54137 | 0.54137 | 0.54137 | 0.25892 | 0.28245 | #N/A | #N/A | 0.25821 | 0.25821
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7562 | 24.7562 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004826 | 0.004826 | 0.00482 | 0.004826 | 0.004826 | 0.004826 | 0.006582 | 0.006645 | 0.006616 | 0.006616
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1432 | 23.1432 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4432 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014914 | 0.014914 | 0.009175 | 0.009175 | 0.009175 | 0.009175 | 0.010931 | 0.010994 | 0.010966 | 0.010966
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9481
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.009184 | 0.009184 | 0.009184 | 0.009184 | 0.01094 | 0.011003 | 0.010974 | 0.010974
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.006264 | 0.006327 | 0.006298 | 0.006298
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
* n/a = not applicable

## TRNSYS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | TRNSYS 17.01.0028 with TESS Libraries (and custom types) | [5 empty] | Thermal Energy System Specialists
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TESS
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | TRNSYS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-18 |  | Model / Organization Indentifier for Charts (short): |  |  |  | TRNSYS/TESS
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | TRNSYS with TESS Libraries
| Version: | 17.01.0028
| Date: | 2014-11-18
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.4159 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0054 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.78002 | 0 | 0.78002 | 32.8657 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.4932 | 2.0544 | 5.5475 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.163 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0312 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7694 | 20.7694 | 18.5094 | 19.0931 | 23.3325 | 23.3325
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 838.436 | 838.436 | 831.9891 | 829.5769 | 846.6643 | 846.6643
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8897 | 31.8897 | 29.598 | 30.1899 | 36.2163 | 36.2163
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8689 | 24.8689 | 14.9489 | 15.5247 | 23.8905 | 23.8905
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 861.9835 | 861.9835 | 830.0764 | 827.6673 | 856.7579 | 856.7579
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.2895 | 58.2895 | 41.874 | 42.4646 | 52.7745 | 52.7745
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3563 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1845 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138 | 21.3858
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.85249 | 0 | 0.85249 | 32.8591 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906 | 0.0022906
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.5705 | 2.0544 | 5.6249 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.6718 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855 | 835.563
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.9128 | 0 | 1.9128 | 44.5861 | [6 empty] | Enthalpy (J/gda) | -28.5404 | 8.2119 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593 | 27.3341
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.7033 | 0.96766 | 2.6709 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683 | 0.21683
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5603 | 1.7951 | 3.3553 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9827 | 20.9827 | 18.5127 | 19.0964 | 23.3358 | 23.3358 | 23.6483
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.209 | 0 | 2.209 | 34.1009 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0444 | 839.0444 | 831.9985 | 829.5862 | 846.6738 | 846.6738 | 845.3778
[16 empty] | Enthalpy (J/gda) | 23.0203 | 32.106 | 32.106 | 29.6013 | 30.1932 | 36.2197 | 36.2197 | 36.537
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887 | 0.22887
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.089 | 25.089 | 14.949 | 15.5247 | 23.8905 | 23.8905 | 24.2165
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.62 | 862.62 | 830.0765 | 827.6674 | 856.758 | 856.758 | 855.3891
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.5163 | 58.5163 | 41.8741 | 42.4647 | 52.7746 | 52.7746 | 53.1094
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097 | 0.23097
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0489 | 24.0489 | 18.5089 | 19.0924 | 23.3302 | 23.3302 | 23.6425
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0065687 | 0.0065687 | 0.0065687
[16 empty] | Specific volume (L/kgda) | 850.4379 | 849.9007 | 849.9007 | 834.0579 | 831.6391 | 848.7645 | 848.7645 | 847.465
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.1826 | 39.1826 | 33.5487 | 34.1421 | 40.1835 | 40.1835 | 40.5015
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33951 | #N/A | 0.2283 | 0.2283
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4334 | 23.4334 | 18.5234 | 19.1059 | 23.3365 | 23.3365 | 23.6483
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014551 | 0.014551 | 0.013376 | 0.013376 | 0.014065 | 0.014065 | 0.014065
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.8435 | 859.8435 | 844.0471 | 841.5963 | 858.9055 | 858.9055 | 857.5889
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.6005 | 60.6005 | 52.5481 | 53.1486 | 59.2623 | 59.2623 | 59.5841
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.3355 | 0.3355 | 0.3355 | 0.33549 | #N/A | 0.2256 | 0.2256
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.52 | 19.1025 | 23.3331 | 23.3331 | 23.6449
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013373 | 0.013373 | 0.014062 | 0.014062 | 0.014062
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 844.0335 | 841.5827 | 858.8916 | 858.8916 | 857.5751
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 52.5373 | 53.1378 | 59.2514 | 59.2514 | 59.5732
[16 empty] | Mass flow rate (kgda/s) | 0.3355 | 0.3355 | 0.3355 | 0.3355 | 0.3355 | #N/A | 0.2256 | 0.2256
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5 | 19.0837 | 23.3227 | 23.3227 | 23.6352
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.00517 | 0.00517 | 0.00517
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 832.1765 | 829.7636 | 846.8544 | 846.8544 | 845.558
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 29.9972 | 30.5893 | 36.617 | 36.617 | 36.9343
[16 empty] | Mass flow rate (kgda/s) | 0.34028 | 0.34028 | 0.34028 | 0.34028 | 0.34028 | #N/A | 0.22882 | 0.22882
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 2.9467 | 0 | 0 | 0 | 24.6351 | 7.7093 | 8.3843 | AE301 | Dry bulb temperature (°C) | -29 | 3.4295 | 7.22 | 7.22 | 7.7815 | 29.27 | 27.81 | 21.1102 | 22.2171 | 21.6678 | 22.0159
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.7255 | 0 | 6.7255 | 48.1783 | 2.2552 | 2.4545 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0021868 | 0.0023719 | 0.00228 | 0.00228
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.315 | 6.2615 | 16.5765 | 100 | 0.99153 | 1.5236 |  | Specific volume (L/kgda) | 691.9366 | 785.4602 | 796.2249 | 796.2249 | 793.9174 | 858.8449 | 854.6986 | 836.5361 | 839.9318 | 838.2465 | 836.8112
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.3734 | 0 | 9.3734 | 65.7465 | 2.2567 | 2.4562 |  | Enthalpy (J/gda) | -28.5404 | 7.3163 | 11.1404 | 11.1404 | 11.7069 | 33.386 | 31.913 | 26.7919 | 28.3805 | 27.592 | 27.9436
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.9149 | 5.4435 | 14.3584 | 100 | 2.2618 | 2.4621 |  | Mass flow rate (kgda/s) | 0.2814 | 0.77055 | 0.77055 | 0.77055 | 0.77055 | 0.35561 | 0.41494 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.4705 | 12.3053 | 20.7757 | 100 | 2.2668 | 2.4678 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.015 | 21.015 | 12.215 | 12.7861 | 19.18 | 18.75 | 23.3285 | 24.4389 | 23.8872 | 24.2266
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.7073 | 0 | 9.7073 | 51.1113 | 2.2607 | 2.461 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0048998 | 0.0050898 | 0.0049954 | 0.0049954
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0106 | 839.0106 | 813.9115 | 811.5517 | 833.7769 | 832.5505 | 846.506 | 849.9339 | 848.2307 | 846.8233
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.9 | 31.9 | 22.9778 | 23.5569 | 30.0395 | 29.6035 | 35.9355 | 37.5464 | 36.746 | 37.0906
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.34788 | 0.40592 | #N/A | #N/A | 0.47572 | 0.47572
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5714 | 25.5714 | 12.2114 | 12.7819 | 15.59 | 16.48 | 23.8806 | 25.0027 | 24.4454 | 24.7871
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.012255 | 0.012255 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0095252 | 0.0097162 | 0.0096213 | 0.0096213
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.9176 | 862.9176 | 819.9046 | 817.5256 | 829.612 | 832.1692 | 854.3402 | 857.8271 | 856.095 | 854.6649
[16 empty] | Enthalpy (J/gda) | 69.8514 | 56.9571 | 56.9571 | 34.6305 | 35.2138 | 38.085 | 38.995 | 48.2695 | 49.9048 | 49.0924 | 49.4423
[16 empty] | Mass flow rate (kgda/s) | 0.27553 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34534 | 0.40296 | #N/A | #N/A | 0.47277 | 0.47277
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4732 | 24.4732 | 12.2132 | 12.7841 | 19.18 | 18.75 | 23.3269 | 24.4367 | 23.8854 | 24.2247
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0064597 | 0.0066501 | 0.0065555 | 0.0065555
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.9864 | 850.9864 | 815.9317 | 813.5654 | 835.8517 | 834.6222 | 848.608 | 852.0428 | 850.3362 | 848.9249
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.3742 | 39.3742 | 26.9085 | 27.489 | 33.9922 | 33.555 | 39.9028 | 41.5175 | 40.7152 | 41.0606
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.75194 | 0.75194 | 0.75194 | 0.75194 | 0.34702 | 0.40492 | #N/A | #N/A | 0.47454 | 0.47454
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7738 | 23.7738 | 12.2138 | 12.7843 | 19.19 | 18.76 | 23.3339 | 24.4427 | 23.8919 | 24.2309
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.01181 | 0.01181 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0095248 | 0.0097161 | 0.0096211 | 0.0096211
[16 empty] | Specific volume (L/kgda) | 859.942 | 857.1235 | 857.1235 | 819.9131 | 817.5341 | 839.9574 | 838.7219 | 852.7674 | 856.2158 | 854.5024 | 853.0834
[16 empty] | Enthalpy (J/gda) | 62.7079 | 53.9762 | 53.9762 | 34.6363 | 35.2197 | 41.7693 | 41.3297 | 47.7088 | 49.3311 | 48.525 | 48.8722
[16 empty] | Mass flow rate (kgda/s) | 0.27604 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34533 | 0.40295 | #N/A | #N/A | 0.47224 | 0.47224
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2 | 12.7705 | 19.19 | 18.76 | 23.3337 | 24.4424 | 23.8916 | 24.2307
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0095166 | 0.009708 | 0.0096129 | 0.0096129
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 819.863 | 817.4842 | 839.9466 | 838.7111 | 852.7558 | 856.2039 | 854.4907 | 853.0715
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 34.6018 | 35.185 | 41.7487 | 41.3091 | 47.6878 | 49.31 | 48.504 | 48.8512
[16 empty] | Mass flow rate (kgda/s) | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.34536 | 0.40298 | #N/A | #N/A | 0.47229 | 0.47229
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2 | 12.7711 | 19.18 | 18.75 | 23.328 | 24.4382 | 23.8867 | 24.2261
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051553 | 0.0053453 | 0.0052509 | 0.0052509
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 814.2005 | 811.8397 | 834.1168 | 832.8898 | 846.8497 | 850.2785 | 848.5748 | 847.1665
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 23.6068 | 24.186 | 30.687 | 30.2508 | 36.5851 | 38.1965 | 37.3958 | 37.7406
[16 empty] | Mass flow rate (kgda/s) | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.34776 | 0.40578 | #N/A | #N/A | 0.47557 | 0.47557
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.2578 | 0 | 0 | 0 | 4.1464 | 4.4895 | 4.8689 | AE401 | Dry bulb temperature (°C) | -29 | -28.9976 | 7.22 | 7.22 | 7.2949 | 46.8281 | 35.9884 | 21.1151 | 22.2211 | #N/A | #N/A | Aug 7, 2015: Entries replaced with "NA" by JN
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.4476 | 0 | 1.4476 | 36.3722 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025899 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00026343 | 0.00025893 | 0.0022691 | 0.0022892 | #N/A | #N/A | Air property output not appropriate for 0 RA mass flow.
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.3862 | 5.9214 | 13.3076 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9366 | 691.9435 | 794.5864 | 794.5864 | 794.2783 | 906.845 | 876.1179 | 836.6603 | 839.8318 | #N/A | #N/A
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.091 | 0 | 4.091 | 53.4325 | 0 | 0 |  | Enthalpy (J/gda) | -28.5404 | -28.5378 | 7.9144 | 7.9144 | 7.9897 | 47.7909 | 36.8692 | 27.006 | 28.1742 | #N/A | #N/A
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.6296 | 4.5892 | 8.2187 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.11282 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.5849 | 5.2196 | 8.8045 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9405 | 16.9405 | 12.6692 | 12.7822 | 12.7822 | 12.7822 | 23.3302 | 24.4386 | 23.9452 | 23.95
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.1448 | 0 | 4.1448 | 49.5567 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032912 | 0.0032912 | 0.0032904 | 0.0032889 | 0.0032889 | 0.0032889 | 0.0049882 | 0.0050489 | 0.0050219 | 0.0050219
[16 empty] | Specific volume (L/kgda) | 821.5721 | 826.1416 | 826.1416 | 813.9765 | 813.5066 | 814.2962 | 814.2962 | 846.6302 | 849.8778 | 848.4319 | 848.4118
[16 empty] | Enthalpy (J/gda) | 23.0203 | 25.3772 | 25.3772 | 21.0521 | 21.1625 | 21.1625 | 21.1625 | 36.1621 | 37.442 | 36.8722 | 36.8771
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13681 | 0.19814 | #N/A | #N/A | 0.056872 | 0.056872
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.721 | 25.721 | 12.491 | 12.7811 | 12.7878 | 12.7878 | 23.8829 | 24.9989 | 24.3678 | 24.474
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013494 | 0.013494 | 0.009021 | 0.009017 | 0.009021 | 0.009021 | 0.0099213 | 0.010261 | 0.010067 | 0.010067
[16 empty] | Specific volume (L/kgda) | 872.9312 | 865.0361 | 865.0361 | 820.9246 | 819.6593 | 821.7776 | 821.7776 | 854.883 | 858.5556 | 856.4754 | 856.0296
[16 empty] | Enthalpy (J/gda) | 69.8514 | 60.2687 | 60.2687 | 35.3369 | 35.6235 | 35.6405 | 35.6405 | 49.2802 | 51.2876 | 50.1471 | 50.256
[16 empty] | Mass flow rate (kgda/s) | 0.27532 | 0.53883 | 0.53883 | 0.53883 | 0.53882 | 0.25786 | 0.28097 | #N/A | #N/A | 0.2635 | 0.2635
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7397 | 24.7397 | 12.6697 | 12.7825 | 12.7825 | 12.7825 | 23.3319 | 24.4401 | 23.9467 | 23.9515
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.0065372 | 0.006598 | 0.0065709 | 0.0065709
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4473 | 850.4473 | 815.9886 | 815.5201 | 816.3107 | 816.3107 | 848.7271 | 851.9817 | 850.5325 | 850.5124
[16 empty] | Enthalpy (J/gda) | 36.4891 | 37.2029 | 37.2029 | 24.9519 | 25.0664 | 25.0664 | 25.0664 | 40.1052 | 41.3882 | 40.8169 | 40.8218
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.13639 | 0.19754 | #N/A | #N/A | 0.056539 | 0.056539
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1572 | 23.1606 | 12.6584 | 12.7709 | 12.7709 | 12.7709 | 23.318 | 24.431 | 23.9345 | 23.9393
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014766 | 0.014801 | 0.0091221 | 0.0091221 | 0.0091221 | 0.0091221 | 0.010838 | 0.0109 | 0.010873 | 0.010873
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.3332 | 859.3905 | 821.5375 | 821.0663 | 821.8609 | 821.8609 | 854.4955 | 857.7874 | 856.3189 | 856.2989
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.8624 | 60.9557 | 35.7636 | 35.8787 | 35.8787 | 35.8787 | 51.0348 | 52.3348 | 51.7549 | 51.7598
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.13538 | 0.19599 | #N/A | #N/A | 0.055858 | 0.055858
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.67 | 12.7822 | 12.7822 | 12.7822 | 23.3286 | 24.4416 | 23.9452 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0091292 | 0.0091292 | 0.0091292 | 0.0091292 | 0.010844 | 0.010906 | 0.010879 | 0.010879
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 821.58 | 821.1102 | 821.9025 | 821.9025 | 854.534 | 857.8259 | 856.3576 | 856.3375
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 35.7933 | 35.908 | 35.908 | 35.908 | 51.0608 | 52.3607 | 51.7809 | 51.7858
[16 empty] | Mass flow rate (kgda/s) | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.13536 | 0.19597 | #N/A | #N/A | 0.055831 | 0.055831
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.67 | 12.7825 | 12.7825 | 12.7825 | 23.3321 | 24.442 | 23.9476 | 23.9524
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061921 | 0.006253 | 0.0062259 | 0.0062259
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 815.5415 | 815.0746 | 815.8626 | 815.8626 | 848.2614 | 851.5195 | 850.0683 | 850.0482
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 24.0835 | 24.1977 | 24.1977 | 24.1977 | 39.2271 | 40.5117 | 39.9395 | 39.9444
[16 empty] | Mass flow rate (kgda/s) | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.13647 | 0.19764 | #N/A | #N/A | 0.056569 | 0.056569
* n/a = not applicable

## Blank
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Blank
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | Blank
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | Blank
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: | [5 empty] | Model / Organization Indentifier for Charts (short): |  |  |  | Blank/Blank
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
Software:
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1)
| AE101 | 2.93 | [12 empty] | AE101 | Dry bulb temperature (°C)
| AE103 | [14 empty] | Humidity ratio (g/gda)
| AE104 | [14 empty] | Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE103 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE104 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 | [12 empty] | AE201 | Dry bulb temperature (°C)
| AE203 | [14 empty] | Humidity ratio (g/gda)
| AE204 | [14 empty] | Specific volume (L/kgda)
| AE205 | [14 empty] | Enthalpy (J/gda)
| AE206 | [14 empty] | Mass flow rate (kgda/s)
| AE226 | [13 empty] | AE203 | Dry bulb temperature (°C)
| AE245 | [14 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE204 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE205 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE206 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE226 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE245 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 |  |  | 2.3446 | [9 empty] | AE301 | Dry bulb temperature (°C)
| AE303 | [14 empty] | Humidity ratio (g/gda)
| AE304 | [14 empty] | Specific volume (L/kgda)
| AE305 | [14 empty] | Enthalpy (J/gda)
| AE306 | [14 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
| AE326 | [13 empty] | AE303 | Dry bulb temperature (°C)
| AE345 | [14 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE304 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE305 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE306 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE326 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE345 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
* =na()
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 |  |  | 2.3446 | [9 empty] | AE401 | Dry bulb temperature (°C)
| AE403 | [14 empty] | Humidity ratio (g/gda)
| AE404 | [14 empty] | Specific volume (L/kgda)
| AE405 | [14 empty] | Enthalpy (J/gda)
| AE406 | [14 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
| AE426 | [13 empty] | AE403 | Dry bulb temperature (°C)
| AE445 | [14 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE404 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE405 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE406 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE426 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE445 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
* =na()