## Read Me
ASHRAE Standard 140-2017
Informative Annex B16, Section B16.7.1 Example Results
for
Section 5.5, Airside HVAC Tests: Fan Coil and Single Zone Systems
AE101 through AE245
This spreadsheet contains the Informative Annex B16, Section B16.7.1 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results; see instructions on page.
"Program List" : Documentation of simulation programs used to produce Informative Annex B16, Section B16.7.1 example results
"Table List": List of Informative Annex B16, Section B16.7.1 Tables in workbook with locations.
"Figure List": List of Informative Annex B16, Section B16.7.1 Figures in workbook with locations.
"Tables 1" through "Delta Tables 1" : Formatted result tables
"Fig B16.7.1-1 HeatCoil" through "Fig B16.7.1-22 Delta Econo" : Figures
"Detailed Location Results": Tool to compare detailed results
"Aggregate Results Final" : Unformatted results for use in tables and charts.
"Delta Results Final": Unformatted delta results for use in tables and charts.
Individual Example Results Worksheets as follows:
QAS: QAS model results set, 12Nov2014. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
DEEAP: DEEAP model results set, 10Dec2012. Submitted by AAON, Inc., Tulsa, Oklahoma, United States.
DeST: DeST 2 model results set, 21Nov2013. Submitted by Tsinghua University, Beijing, China.
DOE22: DOE-2.2 model results set, 10Mar2015. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
EPlus: EnergyPlus 8.2 model results set, 15Jan2015. Submitted by GARD Analytics, Arlington Heights, Illinois, United States.
IES-VE: IES-VE model results set, 20Feb2015. Submitted by Integrated Environmental Solutions, Glasgow, United Kingdom.
LCEM: LCEM model results set, 14Jan2015. Submitted by Ministry of Land, Infrastructure, Transportation and Tourism, Tokyo, Japan.
TRNSYS: TRNSYS-17 with TESS libraries model results set, 18Nov2014. Submitted by TESS, Madison, Wisconsin, United States.

## Adding Results
Output spreadsheet for Airside HVAC Equipment Diagnostic Tests: AE101 through AE445
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell C50 of Sec5-5out.xlsx is in C50 of Sheet "YourData"
Check that the summary results for Case AE101 start at YourData!C61.
Data should flow to "YourData" cells as tabulated below. Your data will then appear in the rightmost column
of each table on sheets "Tables 1" to "Delta Tables 1". Charts are also updated with "your data" automatically.
Complete the program information block on "YourData", which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT SHEETS AND NEW RESULTS
Gives locations for data in "YourData" sheet and in participant sheets.
Program Information Block - complete blue boxes to identify program and organization for report
| Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
| I5 | [5 empty] | O5
| Program Version Release Date: |  |  |  | I6 |  | Modeler Organization for Tables and Charts (short): |  |  |  | O6
| Program Name for Tables and Charts (short): |  |  |  | I7
| Results Submission Date: |  |  |  | I8 |  | Model / Organization Indentifier for Charts (short): |  |  |  | O8 | defaults to short program name / short organization name
Results
| Software: | C50
| Version: | C51
| Date: | C52
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | C61 | D61 | E61 | F61 | G61 | H61 | I61 | J61 | [5 empty] | AE101 | Dry bulb temperature (°C) | S61 | T61 | U61 | V61 | W61 | X61 | Y61
| AE103 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | [6 empty] | Humidity ratio (g/gda) | S62 | T62 | U62 | V62 | W62 | X62 | Y62
| AE104 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | [6 empty] | Specific volume (L/kgda) | S63 | T63 | U63 | V63 | W63 | X63 | Y63
[16 empty] | Enthalpy (J/gda) | S64 | T64 | U64 | V64 | W64 | X64 | Y64
[16 empty] | Mass flow rate (kgda/s) | S65 | T65 | U65 | V65 | W65 | #N/A | Y65
[15 empty] | AE103 | Dry bulb temperature (°C) | S66 | T66 | U66 | V66 | W66 | X66 | Y66
[16 empty] | Humidity ratio (g/gda) | S67 | T67 | U67 | V67 | W67 | X67 | Y67
[16 empty] | Specific volume (L/kgda) | S68 | T68 | U68 | V68 | W68 | X68 | Y68
[16 empty] | Enthalpy (J/gda) | S69 | T69 | U69 | V69 | W69 | X69 | Y69
[16 empty] | Mass flow rate (kgda/s) | S70 | T70 | U70 | V70 | W70 | #N/A | Y70
[15 empty] | AE104 | Dry bulb temperature (°C) | S71 | T71 | U71 | V71 | W71 | X71 | Y71
[16 empty] | Humidity ratio (g/gda) | S72 | T72 | U72 | V72 | W72 | X72 | Y72
[16 empty] | Specific volume (L/kgda) | S73 | T73 | U73 | V73 | W73 | X73 | Y73
[16 empty] | Enthalpy (J/gda) | S74 | T74 | U74 | V74 | W74 | X74 | Y74
[16 empty] | Mass flow rate (kgda/s) | S75 | T75 | U75 | V75 | W75 | #N/A | Y75
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | [5 empty] | AE201 | Dry bulb temperature (°C) | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89
| AE203 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | [6 empty] | Humidity ratio (g/gda) | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90
| AE204 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | [6 empty] | Specific volume (L/kgda) | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91
| AE205 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | [6 empty] | Enthalpy (J/gda) | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92
| AE206 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | [6 empty] | Mass flow rate (kgda/s) | S93 | T93 | U93 | V93 | W93 | #N/A | Y93 | Z93
| AE226 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | [5 empty] | AE203 | Dry bulb temperature (°C) | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94
| AE245 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | [6 empty] | Humidity ratio (g/gda) | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95
[16 empty] | Specific volume (L/kgda) | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96
[16 empty] | Enthalpy (J/gda) | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97
[16 empty] | Mass flow rate (kgda/s) | S98 | T98 | U98 | V98 | W98 | #N/A | Y98 | Z98
[15 empty] | AE204 | Dry bulb temperature (°C) | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99
[16 empty] | Humidity ratio (g/gda) | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100
[16 empty] | Specific volume (L/kgda) | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101
[16 empty] | Enthalpy (J/gda) | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102
[16 empty] | Mass flow rate (kgda/s) | S103 | T103 | U103 | V103 | W103 | #N/A | Y103 | Z103
[15 empty] | AE205 | Dry bulb temperature (°C) | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104
[16 empty] | Humidity ratio (g/gda) | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105
[16 empty] | Specific volume (L/kgda) | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106
[16 empty] | Enthalpy (J/gda) | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107
[16 empty] | Mass flow rate (kgda/s) | S108 | T108 | U108 | V108 | W108 | #N/A | Y108 | Z108
[15 empty] | AE206 | Dry bulb temperature (°C) | S109 | T109 | U109 | V109 | W109 | X109 | Y109 | Z109
[16 empty] | Humidity ratio (g/gda) | S110 | T110 | U110 | V110 | W110 | X110 | Y110 | Z110
[16 empty] | Specific volume (L/kgda) | S111 | T111 | U111 | V111 | W111 | X111 | Y111 | Z111
[16 empty] | Enthalpy (J/gda) | S112 | T112 | U112 | V112 | W112 | X112 | Y112 | Z112
[16 empty] | Mass flow rate (kgda/s) | S113 | T113 | U113 | V113 | W113 | #N/A | Y113 | Z113
[15 empty] | AE226 | Dry bulb temperature (°C) | S114 | T114 | U114 | V114 | W114 | X114 | Y114 | Z114
[16 empty] | Humidity ratio (g/gda) | S115 | T115 | U115 | V115 | W115 | X115 | Y115 | Z115
[16 empty] | Specific volume (L/kgda) | S116 | T116 | U116 | V116 | W116 | X116 | Y116 | Z116
[16 empty] | Enthalpy (J/gda) | S117 | T117 | U117 | V117 | W117 | X117 | Y117 | Z117
[16 empty] | Mass flow rate (kgda/s) | S118 | T118 | U118 | V118 | W118 | #N/A | Y118 | Z118
[15 empty] | AE245 | Dry bulb temperature (°C) | S119 | T119 | U119 | V119 | W119 | X119 | Y119 | Z119
[16 empty] | Humidity ratio (g/gda) | S120 | T120 | U120 | V120 | W120 | X120 | Y120 | Z120
[16 empty] | Specific volume (L/kgda) | S121 | T121 | U121 | V121 | W121 | X121 | Y121 | Z121
[16 empty] | Enthalpy (J/gda) | S122 | T122 | U122 | V122 | W122 | X122 | Y122 | Z122
[16 empty] | Mass flow rate (kgda/s) | S123 | T123 | U123 | V123 | W123 | #N/A | Y123 | Z123
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | C137 | D137 | E137 | F137 | G137 | H137 | I137 | J137 | K137 | L137 | M137 | N137 | O137 | AE301 | Dry bulb temperature (°C) | S137 | T137 | U137 | V137 | W137 | X137 | Y137 | Z137 | AA137 | AB137 | AC137
| AE303 | C138 | D138 | E138 | F138 | G138 | H138 | I138 | J138 | K138 | L138 | M138 | N138 | O138 |  | Humidity ratio (g/gda) | S138 | T138 | U138 | V138 | W138 | X138 | Y138 | Z138 | AA138 | AB138 | AC138
| AE304 | C139 | D139 | E139 | F139 | G139 | H139 | I139 | J139 | K139 | L139 | M139 | N139 | O139 |  | Specific volume (L/kgda) | S139 | T139 | U139 | V139 | W139 | X139 | Y139 | Z139 | AA139 | AB139 | AC139
| AE305 | C140 | D140 | E140 | F140 | G140 | H140 | I140 | J140 | K140 | L140 | M140 | N140 | O140 |  | Enthalpy (J/gda) | S140 | T140 | U140 | V140 | W140 | X140 | Y140 | Z140 | AA140 | AB140 | AC140
| AE306 | C141 | D141 | E141 | F141 | G141 | H141 | I141 | J141 | K141 | L141 | M141 | N141 | O141 |  | Mass flow rate (kgda/s) | S141 | T141 | U141 | V141 | W141 | X141 | Y141 | #N/A | #N/A | AB141 | AC141
| AE326 | C142 | D142 | E142 | F142 | G142 | H142 | I142 | J142 | K142 | L142 | M142 | N142 | O142 | AE303 | Dry bulb temperature (°C) | S142 | T142 | U142 | V142 | W142 | X142 | Y142 | Z142 | AA142 | AB142 | AC142
| AE345 | C143 | D143 | E143 | F143 | G143 | H143 | I143 | J143 | K143 | L143 | M143 | N143 | O143 |  | Humidity ratio (g/gda) | S143 | T143 | U143 | V143 | W143 | X143 | Y143 | Z143 | AA143 | AB143 | AC143
[16 empty] | Specific volume (L/kgda) | S144 | T144 | U144 | V144 | W144 | X144 | Y144 | Z144 | AA144 | AB144 | AC144
[16 empty] | Enthalpy (J/gda) | S145 | T145 | U145 | V145 | W145 | X145 | Y145 | Z145 | AA145 | AB145 | AC145
[16 empty] | Mass flow rate (kgda/s) | S146 | T146 | U146 | V146 | W146 | X146 | Y146 | #N/A | #N/A | AB146 | AC146
[15 empty] | AE304 | Dry bulb temperature (°C) | S147 | T147 | U147 | V147 | W147 | X147 | Y147 | Z147 | AA147 | AB147 | AC147
[16 empty] | Humidity ratio (g/gda) | S148 | T148 | U148 | V148 | W148 | X148 | Y148 | Z148 | AA148 | AB148 | AC148
[16 empty] | Specific volume (L/kgda) | S149 | T149 | U149 | V149 | W149 | X149 | Y149 | Z149 | AA149 | AB149 | AC149
[16 empty] | Enthalpy (J/gda) | S150 | T150 | U150 | V150 | W150 | X150 | Y150 | Z150 | AA150 | AB150 | AC150
[16 empty] | Mass flow rate (kgda/s) | S151 | T151 | U151 | V151 | W151 | X151 | Y151 | #N/A | #N/A | AB151 | AC151
[15 empty] | AE305 | Dry bulb temperature (°C) | S152 | T152 | U152 | V152 | W152 | X152 | Y152 | Z152 | AA152 | AB152 | AC152
[16 empty] | Humidity ratio (g/gda) | S153 | T153 | U153 | V153 | W153 | X153 | Y153 | Z153 | AA153 | AB153 | AC153
[16 empty] | Specific volume (L/kgda) | S154 | T154 | U154 | V154 | W154 | X154 | Y154 | Z154 | AA154 | AB154 | AC154
[16 empty] | Enthalpy (J/gda) | S155 | T155 | U155 | V155 | W155 | X155 | Y155 | Z155 | AA155 | AB155 | AC155
[16 empty] | Mass flow rate (kgda/s) | S156 | T156 | U156 | V156 | W156 | X156 | Y156 | #N/A | #N/A | AB156 | AC156
[15 empty] | AE306 | Dry bulb temperature (°C) | S157 | T157 | U157 | V157 | W157 | X157 | Y157 | Z157 | AA157 | AB157 | AC157
[16 empty] | Humidity ratio (g/gda) | S158 | T158 | U158 | V158 | W158 | X158 | Y158 | Z158 | AA158 | AB158 | AC158
[16 empty] | Specific volume (L/kgda) | S159 | T159 | U159 | V159 | W159 | X159 | Y159 | Z159 | AA159 | AB159 | AC159
[16 empty] | Enthalpy (J/gda) | S160 | T160 | U160 | V160 | W160 | X160 | Y160 | Z160 | AA160 | AB160 | AC160
[16 empty] | Mass flow rate (kgda/s) | S161 | T161 | U161 | V161 | W161 | X161 | Y161 | #N/A | #N/A | AB161 | AC161
[15 empty] | AE326 | Dry bulb temperature (°C) | S162 | T162 | U162 | V162 | W162 | X162 | Y162 | Z162 | AA162 | AB162 | AC162
[16 empty] | Humidity ratio (g/gda) | S163 | T163 | U163 | V163 | W163 | X163 | Y163 | Z163 | AA163 | AB163 | AC163
[16 empty] | Specific volume (L/kgda) | S164 | T164 | U164 | V164 | W164 | X164 | Y164 | Z164 | AA164 | AB164 | AC164
[16 empty] | Enthalpy (J/gda) | S165 | T165 | U165 | V165 | W165 | X165 | Y165 | Z165 | AA165 | AB165 | AC165
[16 empty] | Mass flow rate (kgda/s) | S166 | T166 | U166 | V166 | W166 | X166 | Y166 | #N/A | #N/A | AB166 | AC166
[15 empty] | AE345 | Dry bulb temperature (°C) | S167 | T167 | U167 | V167 | W167 | X167 | Y167 | Z167 | AA167 | AB167 | AC167
[16 empty] | Humidity ratio (g/gda) | S168 | T168 | U168 | V168 | W168 | X168 | Y168 | Z168 | AA168 | AB168 | AC168
[16 empty] | Specific volume (L/kgda) | S169 | T169 | U169 | V169 | W169 | X169 | Y169 | Z169 | AA169 | AB169 | AC169
[16 empty] | Enthalpy (J/gda) | S170 | T170 | U170 | V170 | W170 | X170 | Y170 | Z170 | AA170 | AB170 | AC170
[16 empty] | Mass flow rate (kgda/s) | S171 | T171 | U171 | V171 | W171 | X171 | Y171 | #N/A | #N/A | AB171 | AC171
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | C164 | D164 | E164 | F164 | G164 | H164 | I164 | J164 | K164 | L164 | M164 | N164 | O164 | AE401 | Dry bulb temperature (°C) | S185 | T185 | U185 | V185 | W185 | X185 | Y185 | Z185 | AA185 | AB185 | AC185
| AE403 | C165 | D165 | E165 | F165 | G165 | H165 | I165 | J165 | K165 | L165 | M165 | N165 | O165 |  | Humidity ratio (g/gda) | S186 | T186 | U186 | V186 | W186 | X186 | Y186 | Z186 | AA186 | AB186 | AC186
| AE404 | C166 | D166 | E166 | F166 | G166 | H166 | I166 | J166 | K166 | L166 | M166 | N166 | O166 |  | Specific volume (L/kgda) | S187 | T187 | U187 | V187 | W187 | X187 | Y187 | Z187 | AA187 | AB187 | AC187
| AE405 | C167 | D167 | E167 | F167 | G167 | H167 | I167 | J167 | K167 | L167 | M167 | N167 | O167 |  | Enthalpy (J/gda) | S188 | T188 | U188 | V188 | W188 | X188 | Y188 | Z188 | AA188 | AB188 | AC188
| AE406 | C168 | D168 | E168 | F168 | G168 | H168 | I168 | J168 | K168 | L168 | M168 | N168 | O168 |  | Mass flow rate (kgda/s) | S189 | T189 | U189 | V189 | W189 | X189 | Y189 | #N/A | #N/A | AB189 | AC189
| AE426 | C169 | D169 | E169 | F169 | G169 | H169 | I169 | J169 | K169 | L169 | M169 | N169 | O169 | AE403 | Dry bulb temperature (°C) | S190 | T190 | U190 | V190 | W190 | X190 | Y190 | Z190 | AA190 | AB190 | AC190
| AE445 | C170 | D170 | E170 | F170 | G170 | H170 | I170 | J170 | K170 | L170 | M170 | N170 | O170 |  | Humidity ratio (g/gda) | S191 | T191 | U191 | V191 | W191 | X191 | Y191 | Z191 | AA191 | AB191 | AC191
[16 empty] | Specific volume (L/kgda) | S192 | T192 | U192 | V192 | W192 | X192 | Y192 | Z192 | AA192 | AB192 | AC192
[16 empty] | Enthalpy (J/gda) | S193 | T193 | U193 | V193 | W193 | X193 | Y193 | Z193 | AA193 | AB193 | AC193
[16 empty] | Mass flow rate (kgda/s) | S194 | T194 | U194 | V194 | W194 | X194 | Y194 | #N/A | #N/A | AB194 | AC194
[15 empty] | AE404 | Dry bulb temperature (°C) | S195 | T195 | U195 | V195 | W195 | X195 | Y195 | Z195 | AA195 | AB195 | AC195
[16 empty] | Humidity ratio (g/gda) | S196 | T196 | U196 | V196 | W196 | X196 | Y196 | Z196 | AA196 | AB196 | AC196
[16 empty] | Specific volume (L/kgda) | S197 | T197 | U197 | V197 | W197 | X197 | Y197 | Z197 | AA197 | AB197 | AC197
[16 empty] | Enthalpy (J/gda) | S198 | T198 | U198 | V198 | W198 | X198 | Y198 | Z198 | AA198 | AB198 | AC198
[16 empty] | Mass flow rate (kgda/s) | S199 | T199 | U199 | V199 | W199 | X199 | Y199 | #N/A | #N/A | AB199 | AC199
[15 empty] | AE405 | Dry bulb temperature (°C) | S200 | T200 | U200 | V200 | W200 | X200 | Y200 | Z200 | AA200 | AB200 | AC200
[16 empty] | Humidity ratio (g/gda) | S201 | T201 | U201 | V201 | W201 | X201 | Y201 | Z201 | AA201 | AB201 | AC201
[16 empty] | Specific volume (L/kgda) | S202 | T202 | U202 | V202 | W202 | X202 | Y202 | Z202 | AA202 | AB202 | AC202
[16 empty] | Enthalpy (J/gda) | S203 | T203 | U203 | V203 | W203 | X203 | Y203 | Z203 | AA203 | AB203 | AC203
[16 empty] | Mass flow rate (kgda/s) | S204 | T204 | U204 | V204 | W204 | X204 | Y204 | #N/A | #N/A | AB204 | AC204
[15 empty] | AE406 | Dry bulb temperature (°C) | S205 | T205 | U205 | V205 | W205 | X205 | Y205 | Z205 | AA205 | AB205 | AC205
[16 empty] | Humidity ratio (g/gda) | S206 | T206 | U206 | V206 | W206 | X206 | Y206 | Z206 | AA206 | AB206 | AC206
[16 empty] | Specific volume (L/kgda) | S207 | T207 | U207 | V207 | W207 | X207 | Y207 | Z207 | AA207 | AB207 | AC207
[16 empty] | Enthalpy (J/gda) | S208 | T208 | U208 | V208 | W208 | X208 | Y208 | Z208 | AA208 | AB208 | AC208
[16 empty] | Mass flow rate (kgda/s) | S209 | T209 | U209 | V209 | W209 | X209 | Y209 | #N/A | #N/A | AB209 | AC209
[15 empty] | AE426 | Dry bulb temperature (°C) | S210 | T210 | U210 | V210 | W210 | X210 | Y210 | Z210 | AA210 | AB210 | AC210
[16 empty] | Humidity ratio (g/gda) | S211 | T211 | U211 | V211 | W211 | X211 | Y211 | Z211 | AA211 | AB211 | AC211
[16 empty] | Specific volume (L/kgda) | S212 | T212 | U212 | V212 | W212 | X212 | Y212 | Z212 | AA212 | AB212 | AC212
[16 empty] | Enthalpy (J/gda) | S213 | T213 | U213 | V213 | W213 | X213 | Y213 | Z213 | AA213 | AB213 | AC213
[16 empty] | Mass flow rate (kgda/s) | S214 | T214 | U214 | V214 | W214 | X214 | Y214 | #N/A | #N/A | AB214 | AC214
[15 empty] | AE445 | Dry bulb temperature (°C) | S215 | T215 | U215 | V215 | W215 | X215 | Y215 | Z215 | AA215 | AB215 | AC215
[16 empty] | Humidity ratio (g/gda) | S216 | T216 | U216 | V216 | W216 | X216 | Y216 | Z216 | AA216 | AB216 | AC216
[16 empty] | Specific volume (L/kgda) | S217 | T217 | U217 | V217 | W217 | X217 | Y217 | Z217 | AA217 | AB217 | AC217
[16 empty] | Enthalpy (J/gda) | S218 | T218 | U218 | V218 | W218 | X218 | Y218 | Z218 | AA218 | AB218 | AC218
[16 empty] | Mass flow rate (kgda/s) | S219 | T219 | U219 | V219 | W219 | X219 | Y219 | #N/A | #N/A | AB219 | AC219

## YourData
Output spreadsheet for Airside HVAC Equipment Diagnostic Tests: AE101 through AE445
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | Carrier Hourly Analysis Program 6.2 | [5 empty] | Carrier Global Corporation
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2024-04-15 |  | Modeler Organization for Tables and Charts (short): |  |  |  | Carrier
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | HAP
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2024-06-15 |  | Model / Organization Indentifier for Charts (short): |  |  |  | HAP/Carrier | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | Carrier HAP
| Version: | 6.2
| Date: | 2024-04-15
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.452 | 0 | 0 | 0 | 29.9492 | [6 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4491 | 29.6284 | 5.0343 | 29.6284 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.76511 | 1.8758e-15 | 0.76511 | 31.3461 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0022891 | 0.0022891
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.48 | 2.2377 | 5.7177 | 94.5132 | [7 empty] | Specific volume (L/kgda) | 692.013 | 788.5318 | 860.0546 | 790.1939 | 860.0546 | 836.768 | 836.768
[17 empty] | Enthalpy (J/gda) | -28.5066 | 8.5165 | 33.8932 | 9.1063 | 33.8932 | 27.0281 | 27.0281
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
[16 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7287 | 19.0955 | 19.0955 | 19.0955 | 23.3333 | 23.3333
[17 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0049602 | 0.0049602
[17 empty] | Specific volume (L/kgda) | 821.6592 | 838.3518 | 833.6929 | 833.6929 | 833.6929 | 846.6945 | 846.6945
[17 empty] | Enthalpy (J/gda) | 22.9959 | 31.7097 | 30.0557 | 30.0557 | 30.0557 | 36.0667 | 36.0667
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
[16 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.9003 | 15.5085 | 15.5085 | 15.5085 | 23.8902 | 23.8902
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012972 | 0.010397 | 0.010397 | 0.010397 | 0.011072 | 0.011072
[17 empty] | Specific volume (L/kgda) | 873.0237 | 862.0467 | 831.4967 | 831.4967 | 831.4967 | 856.5543 | 856.5543
[17 empty] | Enthalpy (J/gda) | 69.814 | 58.0633 | 41.8848 | 41.8848 | 41.8848 | 52.188 | 52.188
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3852 | 0 | 0 | 0 | 30.7672 | [6 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6484 | 29.048 | 4.6484 | 29.6281 | 21.1108 | 21.1108 | 21.4096
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.83367 | 3.4106e-16 | 0.83367 | 32.5083 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0022891 | 0.0022891 | 0.0022891
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5482 | 2.273 | 5.8212 | 96.8838 | [7 empty] | Specific volume (L/kgda) | 692.013 | 789.0978 | 858.4059 | 789.0978 | 860.0537 | 836.767 | 836.767 | 837.6168
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9136 | 6.8212e-16 | 1.9136 | 44.1036 | [7 empty] | Enthalpy (J/gda) | -28.5066 | 8.7174 | 33.3082 | 8.7174 | 33.8928 | 27.0277 | 27.0277 | 27.3293
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.6939 | 1.5538 | 3.2477 | 86.2414 | [7 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5476 | 2.3544 | 3.902 | 95.7376 | [6 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9272 | 18.5133 | 18.5133 | 19.0955 | 23.3333 | 23.3333 | 23.6307
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2059 | 6.0633e-16 | 2.2059 | 33.9841 | [7 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0049602 | 0.0049602 | 0.0049602
[17 empty] | Specific volume (L/kgda) | 821.6592 | 838.9181 | 832.0318 | 832.0318 | 833.6929 | 846.6945 | 846.6945 | 847.5438
[17 empty] | Enthalpy (J/gda) | 22.9959 | 31.9108 | 29.4659 | 29.4659 | 30.0557 | 36.0667 | 36.0667 | 36.3682
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.1021 | 14.9397 | 14.9397 | 15.5154 | 23.899 | 23.899 | 24.1937
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012889 | 0.010273 | 0.010273 | 0.010273 | 0.010948 | 0.010948 | 0.010948
[17 empty] | Specific volume (L/kgda) | 873.0237 | 862.518 | 829.6955 | 829.6955 | 831.3537 | 856.412 | 856.412 | 857.2616
[17 empty] | Enthalpy (J/gda) | 69.814 | 58.0604 | 40.9888 | 40.9888 | 41.5784 | 51.8815 | 51.8815 | 52.1836
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0522 | 18.5269 | 18.5269 | 19.1075 | 23.3333 | 23.3333 | 23.6299
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0058322 | 0.0058322 | 0.0058322 | 0.0058322 | 0.0065079 | 0.0065079 | 0.0065079
[17 empty] | Specific volume (L/kgda) | 850.518 | 849.928 | 834.1269 | 834.1269 | 835.7874 | 848.7846 | 848.7846 | 849.6336
[17 empty] | Enthalpy (J/gda) | 36.4347 | 39.0155 | 33.4035 | 33.4035 | 33.9933 | 40.0043 | 40.0043 | 40.3059
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4171 | 18.5766 | 18.5766 | 19.1512 | 23.3334 | 23.3334 | 23.6269
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.013335 | 0.011544 | 0.011544 | 0.011544 | 0.01222 | 0.01222 | 0.01222
[17 empty] | Specific volume (L/kgda) | 860.0491 | 858.2471 | 841.8594 | 841.8594 | 843.5176 | 856.4988 | 856.4988 | 857.3466
[17 empty] | Enthalpy (J/gda) | 62.7052 | 57.461 | 47.9365 | 47.9365 | 48.5263 | 54.5373 | 54.5373 | 54.8389
[17 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 18.5882 | 18.5882 | 19.1615 | 23.3338 | 23.3338 | 23.6265
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.012851 | 0.012851 | 0.012851 | 0.013527 | 0.013527 | 0.013527
[17 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 843.6297 | 843.6297 | 845.2874 | 858.2649 | 858.2649 | 859.1125
[17 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 51.2622 | 51.2622 | 51.8519 | 57.863 | 57.863 | 58.1646
[17 empty] | Mass flow rate (kgda/s) | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[16 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 18.515 | 18.515 | 19.0971 | 23.3333 | 23.3333 | 23.6306
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051566 | 0.0051566 | 0.0051566
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 832.2977 | 832.2977 | 833.9587 | 846.9598 | 846.9598 | 847.809
[17 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 29.9656 | 29.9656 | 30.5554 | 36.5664 | 36.5664 | 36.868
[17 empty] | Mass flow rate (kgda/s) | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 3.5822 | 0 | 0 | 0 | 23.8892 | 7.501 | 8.1235 |  | AE301 | Dry bulb temperature (°C) | -29 | 2.4103 | 7.2222 | 7.2222 | 7.8075 | 29.6391 | 28.0732 | 21.1199 | 22.2336 | 21.6769 | 21.9691
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 5.4503 | -1.819e-15 | 5.4503 | 47.4856 | 1.4144 | 1.4645 |  |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0021725 | 0.0023652 | 0.0022689 | 0.0022689
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.0847 | 6.8981 | 16.9828 | 95.878 | 0.94009 | 1.4519 |  |  | Specific volume (L/kgda) | 692.013 | 782.5942 | 796.2601 | 796.2601 | 797.9222 | 859.9241 | 855.477 | 836.6368 | 840.0622 | 838.3495 | 839.1805
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.1982 | -1.819e-15 | 9.1982 | 64.9185 | 2.1923 | 2.3735 |  |  | Enthalpy (J/gda) | -28.5066 | 6.1697 | 11.0183 | 11.0183 | 11.608 | 33.6059 | 32.0281 | 26.7408 | 28.3541 | 27.5475 | 27.8423
| AE306 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 0 | 8.6922 | 5.9861 | 14.6783 | 96.351 | 6.6035 | 7.082 |  |  | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
| AE326 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 0 | 8.1485 | 12.6387 | 20.7872 | 99.8848 | 6.6056 | 7.0847 |  | AE303 | Dry bulb temperature (°C) | 15.5 | 19.481 | 19.481 | 12.1956 | 12.7778 | 16.8741 | 16.4133 | 21.1128 | 22.2243 | 21.6686 | 21.9599
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.5096 | -3.638e-15 | 9.5096 | 50.9986 | 2.1841 | 2.3628 |  |  | Humidity ratio (g/gda) | 0.0029334 | 0.0041703 | 0.0041703 | 0.0041703 | 0.0041703 | 0.0041703 | 0.0041703 | 0.004847 | 0.0050396 | 0.0049433 | 0.0049433
[17 empty] | Specific volume (L/kgda) | 821.6592 | 834.6399 | 834.6399 | 813.8606 | 815.5212 | 827.2046 | 825.8903 | 840.2012 | 843.634 | 841.9176 | 842.7495
[17 empty] | Enthalpy (J/gda) | 22.9959 | 30.1558 | 30.1558 | 22.7787 | 23.3682 | 27.5161 | 27.0495 | 33.5271 | 35.1438 | 34.3354 | 34.6308
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5744 | 25.5744 | 12.2 | 12.7778 | 15.4791 | 16.3538 | 23.89 | 25.002 | 24.4461 | 24.7346
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012144 | 0.012144 | 0.0084806 | 0.0084806 | 0.0084806 | 0.0084806 | 0.0091559 | 0.0093481 | 0.009252 | 0.009252
[17 empty] | Specific volume (L/kgda) | 873.0237 | 862.87 | 862.87 | 819.4756 | 821.1351 | 828.8927 | 831.4048 | 853.9611 | 857.4192 | 855.6902 | 856.5197
[17 empty] | Enthalpy (J/gda) | 69.814 | 56.6475 | 56.6475 | 33.6607 | 34.2504 | 37.0074 | 37.9001 | 47.3105 | 48.9366 | 48.1236 | 48.4184
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4574 | 24.4574 | 12.197 | 12.7778 | 19.1092 | 18.6531 | 23.3359 | 24.4477 | 23.8919 | 24.1819
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0063915 | 0.0065838 | 0.0064876 | 0.0064876
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.9291 | 850.9291 | 815.8737 | 817.5342 | 835.6372 | 834.3332 | 848.6347 | 852.0779 | 850.3563 | 851.1864
[17 empty] | Enthalpy (J/gda) | 36.4347 | 39.1307 | 39.1307 | 26.6807 | 27.2704 | 33.6997 | 33.2366 | 39.7108 | 41.3309 | 40.5209 | 40.8157
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7268 | 23.7268 | 12.2 | 12.7778 | 31.7512 | 30.2192 | 23.341 | 24.4542 | 23.8977 | 24.1862
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.011707 | 0.011707 | 0.008523 | 0.008523 | 0.008523 | 0.008523 | 0.0091986 | 0.0093909 | 0.0092948 | 0.0092948
[17 empty] | Specific volume (L/kgda) | 860.0491 | 856.9412 | 856.9412 | 819.5309 | 821.1903 | 875.6824 | 871.2824 | 852.4404 | 855.9018 | 854.1711 | 855.0007
[17 empty] | Enthalpy (J/gda) | 62.7052 | 53.6354 | 53.6354 | 33.7678 | 34.3576 | 53.7235 | 52.1597 | 46.8582 | 48.4856 | 47.6719 | 47.9668
[17 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2005 | 12.7779 | 31.7464 | 30.2159 | 23.341 | 24.4542 | 23.8977 | 24.186
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.015566 | 0.0088403 | 0.0088403 | 0.0088403 | 0.0088403 | 0.0095159 | 0.0097082 | 0.0096121 | 0.0096121
[17 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 860.0491 | 819.9447 | 821.604 | 876.1092 | 871.7113 | 852.869 | 856.3319 | 854.6005 | 855.43
[17 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 62.7052 | 34.5691 | 35.1588 | 54.5308 | 52.9677 | 47.6655 | 49.2936 | 48.4796 | 48.7744
[17 empty] | Mass flow rate (kgda/s) | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[16 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.1957 | 12.7778 | 19.0996 | 18.64 | 23.3359 | 24.4477 | 23.8919 | 24.1825
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051566 | 0.005349 | 0.0052528 | 0.0052528
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 850.518 | 814.2649 | 815.9259 | 833.966 | 832.6545 | 846.967 | 850.4039 | 848.6855 | 849.5159
[17 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 36.4347 | 23.5631 | 24.1529 | 30.558 | 30.0923 | 36.569 | 38.1866 | 37.3778 | 37.6726
[17 empty] | Mass flow rate (kgda/s) | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.3476 | 0 | 0 | 0 | 4.1447 | 4.4305 | 4.7919 |  | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.9085 | 46.6816 | 35.8656 | 21.1298 | 22.2379 | 22.2379 | 23.0366
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.6278 | -3.4106e-16 | 1.6278 | 37.0875 | 0 | 0 |  |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022891 | 0.0022874 | 0.0022874 | 0.0022874
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.5351 | 6.5718 | 14.1069 | 97.7306 | 0 | 0 |  |  | Specific volume (L/kgda) | 692.013 | 692.013 | 794.6804 | 794.6804 | 796.6257 | 906.5233 | 875.8665 | 836.821 | 839.9698 | 839.9698 | 842.241
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.5821 | -1.0611e-15 | 4.5821 | 44.8992 | 0 | 0 |  |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.9084 | 7.9084 | 8.5984 | 47.5778 | 36.7042 | 27.0468 | 28.1608 | 28.1608 | 28.9668
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.7745 | 5.1232 | 8.8977 | 99.4817 | 0 | 0 |  |  | Mass flow rate (kgda/s) | 0.28416 | 0.28416 | 0.28416 | 0.28416 | 0.28416 | 0.11366 | 0.17049 | n/a* | n/a* | 1.9429e-16 | 1.9429e-16
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6773 | 5.7022 | 9.3795 | 99.8848 | 0 | 0 |  | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9432 | 16.9432 | 12.1342 | 12.7778 | 12.7778 | 12.7778 | 23.3304 | 24.4403 | 23.9339 | 25.0078
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.8528 | 4.5475e-16 | 4.8528 | 34.6029 | 0 | 0 |  |  | Humidity ratio (g/gda) | 0.0029334 | 0.0032391 | 0.0032391 | 0.0032391 | 0.0032391 | 0.0032391 | 0.0032391 | 0.0049214 | 0.0049809 | 0.0049537 | 0.0049537
[17 empty] | Specific volume (L/kgda) | 821.6592 | 826.1715 | 826.1715 | 812.4756 | 814.3084 | 814.3084 | 814.3084 | 846.6338 | 849.8837 | 848.4008 | 851.4676
[17 empty] | Enthalpy (J/gda) | 22.9959 | 25.2281 | 25.2281 | 20.3669 | 21.0174 | 21.0174 | 21.0174 | 35.9648 | 37.2417 | 36.6591 | 37.748
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.33486 | 0.33486 | 0.33486 | 0.33486 | 0.13695 | 0.19824 | n/a* | n/a* | 0.051029 | 0.050702
[16 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.8767 | 25.8767 | 12.1904 | 12.7778 | 12.7775 | 12.7775 | 23.8864 | 24.9961 | 24.3685 | 24.722
[17 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013422 | 0.013422 | 0.0086412 | 0.0086412 | 0.0086521 | 0.0086521 | 0.0095447 | 0.0098791 | 0.0096899 | 0.0096899
[17 empty] | Specific volume (L/kgda) | 873.0237 | 865.4833 | 865.4833 | 819.6569 | 821.3443 | 821.3576 | 821.3576 | 854.477 | 858.1233 | 856.0607 | 857.0775
[17 empty] | Enthalpy (J/gda) | 69.814 | 60.2147 | 60.2147 | 34.0562 | 34.6559 | 34.6832 | 34.6832 | 48.2966 | 50.2831 | 49.1593 | 49.5208
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.53929 | 0.53929 | 0.53929 | 0.53929 | 0.25799 | 0.2813 | n/a* | n/a* | 0.25513 | 0.25513
[16 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.5256 | 24.5256 | 17.6975 | 18.2843 | 18.2937 | 18.2937 | 23.3323 | 24.4427 | 23.9348 | 24.2443
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0056341 | 0.0056341 | 0.0056341 | 0.0056341 | 0.0056357 | 0.0056357 | 0.0064411 | 0.0065567 | 0.0065038 | 0.0065038
[17 empty] | Specific volume (L/kgda) | 850.518 | 851.0132 | 851.0132 | 831.4924 | 833.1699 | 833.1991 | 833.1991 | 848.6914 | 852.0267 | 850.501 | 851.3871
[17 empty] | Enthalpy (J/gda) | 36.4347 | 38.9917 | 38.9917 | 32.0589 | 32.6547 | 32.6685 | 32.6685 | 39.8335 | 41.2567 | 40.6056 | 40.9204
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.66093 | 0.66093 | 0.66093 | 0.66093 | 0.28602 | 0.37491 | n/a* | n/a* | 0.37677 | 0.37677
[16 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.291 | 23.291 | 12.1386 | 12.7778 | 12.7778 | 12.7778 | 23.3304 | 24.4403 | 23.9302 | 25.0569
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.014843 | 0.014843 | 0.0087679 | 0.0087679 | 0.0087679 | 0.0087679 | 0.010467 | 0.010527 | 0.0105 | 0.0105
[17 empty] | Specific volume (L/kgda) | 860.0491 | 859.9188 | 859.9188 | 819.6729 | 821.5093 | 821.5093 | 821.5093 | 854.1234 | 857.4022 | 855.8951 | 859.1413
[17 empty] | Enthalpy (J/gda) | 62.7052 | 61.1685 | 61.1685 | 34.3231 | 34.9758 | 34.9758 | 34.9758 | 50.0751 | 51.365 | 50.7721 | 51.9263
[17 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.13557 | 0.19624 | n/a* | n/a* | 0.047655 | 0.047286
[16 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.1394 | 12.7784 | 12.7784 | 12.7784 | 23.3304 | 24.4403 | 23.9302 | 25.0546
[17 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.015566 | 0.0088043 | 0.0088043 | 0.0088043 | 0.0088043 | 0.010504 | 0.010564 | 0.010536 | 0.010536
[17 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 860.0491 | 819.7225 | 821.5586 | 821.5586 | 821.5586 | 854.1727 | 857.4517 | 855.9445 | 859.1843
[17 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 62.7052 | 34.416 | 35.0686 | 35.0686 | 35.0686 | 50.168 | 51.4579 | 50.865 | 52.0169
[17 empty] | Mass flow rate (kgda/s) | 0.33156 | 0.33156 | 0.33156 | 0.33156 | 0.33156 | 0.13557 | 0.19624 | n/a* | n/a* | 0.047653 | 0.0474
[16 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.2273 | 18.8119 | 18.8186 | 18.8186 | 23.3324 | 24.6263 | 24.0107 | 24.3124
[17 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.005201 | 0.0053489 | 0.0052785 | 0.0052785
[17 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 850.518 | 831.4768 | 833.1449 | 833.164 | 833.164 | 847.017 | 850.914 | 849.0598 | 849.9219
[17 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 36.4347 | 29.6742 | 30.2664 | 30.2732 | 30.2732 | 36.6782 | 38.3675 | 37.5637 | 37.8699
[17 empty] | Mass flow rate (kgda/s) | 0.71781 | 0.71781 | 0.71781 | 0.71781 | 0.71781 | 0.31999 | 0.39782 | n/a* | n/a* | 0.43366 | 0.43366
* n/a = not applicable

## Title Page
ASHRAE Standard 140-2017 | To print example results:
Informative Annex B16, Section B16.7.1 | 1. Select results type in cell B21:
"Example" for Airside HVAC BESTEST Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 5.5, Airside HVAC Equipment Performance Tests AE101 through AE245 | "Title Page" thru "Figure List"
"Tables 1" thru "Delta Tables 1"
"Fig B16.7.1-1 HeatCoil" through "Fig B16.7.1-22 Delta Econo"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.1
Scratch area for Table subtitle 1
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE101 through AE245
Scratch area for Table subtitle 2
Scratch area for chart subtitles 1
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.1
Scratch area for chart subtitles 2
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE101 through AE245

## Program List
ASHRAE Standard 140-2017
Computer Programs, Program Authors, and Producers of Example Results for
Section 5.5, Airside HVAC Equipment Performance Tests AE101 through AE245
The quasi-analytical solution and programs used to generate the example results are described in Table B17-13. The first
column of the table ("Model") indicates the program name and version number, or indicates a quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry organization
with expertise in building science that wrote the simulation software.
The third column ("Implemented By") indicates the national research facility, university, or industry organization with
expertise in building science that performed the simulations or did the quasi-analytical solutions. The organizations that
performed simulations either ran software written by their organization or otherwise maintained contact with the program
authors during the project.
The fourth column ("Abbreviation") indicates the identifying abbreviation used in the results tables and figures.
See Standard 140, Informative Annex B17 for further details.
Table B17-13 Airside HVAC Cases
Participating Organizations and Models
Model | Authoring Organization | Implemented by | Abbreviation
Quasi-Analytical Solution (QAS) | PSUa/UNOb/TAMUc/NRELd/JNAe/MDKf, United States | NRELd/JNAe/MDKf, United States | QAS/PSU-TAMU-NREL
DEEAPg 1.1.2 | AAON, Inc., United States | AAON, Inc., United States | DEEAP/AAON
DeSTh 2 | Tsinghua University, China | Tsinghua University, China / LBNLi, United States | DeST/TsinghuaU-LBNL
DOE-2.2 V48L | JJHj/LBNLi/UCk, United States | NRELd/JNAe/MDKf, United States | DOE-2.2/NREL
EnergyPlus 8.2.0 | DOE-BTl, United States | GARD Analytics, Inc., United States | EnergyPlus/GARD
IES-VEm 2014.2 | IESn, United Kingdom | IESn, United Kingdom | IES-VE/IES
LCEMo 3.10 | MLITp, Japan | TTEq, Japan | LCEM/MLIT-TTE
TRNSYS 17.01.0028 | TESSr/UWMs, United States | TESSr, United States | TRNSYS/TESS
a PSU: The Pennsylvania State University, United States
b UNO: University of Nebraska - Omaha, United States
c TAMU: Texas A&M University, United States
d NREL: National Renewable Energy Laboratory, United States
e JNA: J. Neymark & Associates, United States
f MDK: Mike D. Kennedy, Inc., United States
g DEEAP: Detailed Energy and Economic Analysis Program
h DeST: Designer's Simulation Toolkit
i LBNL: Lawrence Berkeley National Laboratory, United States
J JJH: James J. Hirsch & Associates, United States
k UC: University of California, United States
l DOE-BT: U.S. Department of Energy, Office of Building Technologies, Energy Efficiency and Renewable Energy, United States
m IES-VE: Integrated Environmental Solutions - Virtual Environment
n IES: Integrated Environmental Solutions, United Kingdom
o LCEM: Life Cycle Energy Management tool
p MLIT: Ministry of Land, Infrastructure, Transportation and Tourism, Japan
q TTE: Takasago Thermal Engineering, Japan
r TESS: Thermal Energy System Specialists, United States
s UWM: University of Wisconsin - Madison, United States

## Table List
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.1
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE101 through AE245
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.7.1-1 | FC/SZ Heating Coil Load [QH] (kWh/h) | Tables 1 | A5–K17
| B16.7.1-2 | FC/SZ Total Cooling Coil Load [QCtotal] (kWh) |  | A20–K32
| B16.7.1-3 | FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) |  | A35–K47
| B16.7.1-4 | FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) |  | A50–K62
| B16.7.1-5 | FC/SZ Outdoor Air Temp (°C) |  | A65–K77
| B16.7.1-6 | FC/SZ Outdoor Air Humidity Ratio (%) |  | A80–K82
| B16.7.1-7 | FC/SZ Outdoor Air Mass Flow Rate (kgda/s) |  | A95–K107
| B16.7.1-8 | FC/SZ Cooling Coil Outlet Air Temperature (°C) |  | A110–K122
| B16.7.1-9 | FC/SZ Relative Humidity at Cooling Coil Outlet [RHcco] (%) |  | A125–K137
| B16.7.1-10 | FC/SZ Supply Fan Air Temperature Rise (°C) |  | A140–K152
| B16.7.1-11 | FC/SZ Supply Air Temperature (°C) |  | A155–K167
| B16.7.1-12 | FC/SZ Supply Air Humidity Ratio (g/gda) |  | A170–K182
| B16.7.1-13 | FC/SZ Supply Air Specific Volume (L/kgda) |  | A185–K197
| B16.7.1-14 | FC/SZ Supply Air Enthalpy (J/gda) |  | A200–K212
| B16.7.1-15 | FC/SZ Supply Air Mass Flow Rate (kgda/s) |  | A215–K227
| B16.7.1-16 | FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) |  | A230–K242
| B16.7.1-17 | FC/SZ Zone Air Temperature (°C) |  | A245–K257
| B16.7.1-18 | FC/SZ Zone Humidity Ratio (g/gda) |  | A260–K272
| B16.7.1-19 | FC/SZ Moisture Added to Zone by Latent Gains (g/s) |  | A275–K288
| B16.7.1-20 | FC/SZ Return Fan Air Temperature Rise (°C) |  | A290–K299
| B16.7.1-21 | FC/SZ Delta Coil Load: SZ - FC (kWh/h) | Delta Tables 1 | A5–K12
| B16.7.1-22 | SZ Delta Coil Load: Economizer Operation (kWh/h) |  | A15–L23

## Figure List
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.1
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE101 through AE245
List of Figures
| Figure | Description | Sheet Tab
| B16.7.1-1 | FC/SZ Heating Coil Load [QH] | Fig B16.7.1-1 HeatCoil
| B16.7.1-2 | FC/SZ Cooling Coil Load, Total [QCtotal] | Fig B16.7.1-2 CoolCoilTot
| B16.7.1-3 | FC/SZ Cooling Coil Load, Sensible [QCsensible] | Fig B16.7.1-3 CoolCoilSens
| B16.7.1-4 | FC/SZ Cooling Coil Load, Latent [QClatent] | Fig B16.7.1-4 CoolCoilLat
| B16.7.1-5 | FC/SZ Outdoor Air Temperature | Fig B16.7.1-5 OAT
| B16.7.1-6 | FC/SZ Outdoor Air Humidity Ratio | Fig B16.7.1-6 OAW
| B16.7.1-7 | FC/SZ Outdoor Air Mass Flow Rate | Fig B16.7.1-7 OAmassflow
| B16.7.1-8 | FC/SZ Cooling Coil Outlet Air Temperature | Fig B16.7.1-8 CCOT
| B16.7.1-9 | FC/SZ Cooling Coil Outlet Relative Humidity [RHcco] | Fig B16.7.1-9 RHcco
| B16.7.1-10 | FC/SZ Supply Fan Air Temperature Rise | Fig B16.7.1-10 Supply Fan dT
| B16.7.1-11 | FC/SZ Supply Air Temperature | Fig B16.7.1-11 SAT
| B16.7.1-12 | FC/SZ Supply Air Humidity Ratio | Fig B16.7.1-12 SAW
| B16.7.1-13 | FC/SZ Supply Air Specific Volume | Fig B16.7.1-13 SAVs
| B16.7.1-14 | FC/SZ Supply Air Enthalpy | Fig B16.7.1-14 SAenth
| B16.7.1-15 | FC/SZ Supply Air Mass Flow Rate | Fig B16.7.1-15 SAmassflow
| B16.7.1-16 | FC/SZ Outdoor Air to Supply Air Mass Flow Ratio | Fig B16.7.1-16 OAFrac
| B16.7.1-17 | FC/SZ Zone Air Temperature | Fig B16.7.1-17 ZoneAirT
| B16.7.1-18 | FC/SZ Zone Humidity Ratio | Fig B16.7.1-18 ZoneAirW
| B16.7.1-19 | FC/SZ Moisture Added to Zone by Latent Gains | Fig B16.7.1-19 Zone Lat Gain
| B16.7.1-20 | FC/SZ Return Fan Air Temperature Rise | Fig B16.7.1-20 Return Fan dT
| B16.7.1-21 | FC/SZ Delta Coil Load, SZ - FC | Fig B16.7.1-21 Delta SZ-FC
| B16.7.1-22 | FC/SZ Delta Coil Load, Economizer Operation | Fig B16.7.1-22 Delta Econo

## scrape titles new (hidden)
Org Tab Name | Org Chart Title | Org Yaxis Title | Proposed Num | New Tab Name | New Chart Title | New Axis Title
Fig 4.1-1 HeatCoil | Figure 4.1-1. FC/SZ Heating Coil Load [QH] | Coil Load (kWh/h) | 1 | Fig 4.1-1 HeatCoil | Figure 4.1-1. FC/SZ Heating Coil Load [QH] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-1 | FC/SZ Heating Coil Load [QH]
Fig 4.1-2 CoolCoilTot | Figure 4.1-2. FC/SZ Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | 2 | Fig 4.1-2 CoolCoilTot | Figure 4.1-2. FC/SZ Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-2 | FC/SZ Cooling Coil Load, Total [QCtotal]
Fig 4.1-3 CoolCoilSens | Figure 4.1-3. FC/SZ Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | 3 | Fig 4.1-3 CoolCoilSens | Figure 4.1-3. FC/SZ Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-3 | FC/SZ Cooling Coil Load, Sensible [QCsensible]
Fig 4.1-4 CoolCoilLat | Figure 4.1-4. FC/SZ Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | 4 | Fig 4.1-4 CoolCoilLat | Figure 4.1-4. FC/SZ Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-4 | FC/SZ Cooling Coil Load, Latent [QClatent]
Fig 4.1-5 OAT | Figure 4.1-5. FC/SZ Outdoor Air Temperature | Temperature (°C) | 5 | Fig 4.1-5 OAT | Figure 4.1-5. FC/SZ Outdoor Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-5 | FC/SZ Outdoor Air Temperature
Fig 4.1-6 OAW | Figure 4.1-6. FC/SZ Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | 6 | Fig 4.1-6 OAW | Figure 4.1-6. FC/SZ Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.1-6 | FC/SZ Outdoor Air Humidity Ratio
Fig 4.1-7 OAmassflow | Figure 4.1-7. FC/SZ Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 7 | Fig 4.1-7 OAmassflow | Figure 4.1-7. FC/SZ Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.1-7 | FC/SZ Outdoor Air Mass Flow Rate
Fig 4.1-8 CCOT | Figure 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature | Temperature (°C) | 8 | Fig 4.1-8 CCOT | Figure 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-8 | FC/SZ Cooling Coil Outlet Air Temperature
Fig 4.1-9 RHcco | Figure 4.1-9. FC/SZ Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | 9 | Fig 4.1-9 RHcco | Figure 4.1-9. FC/SZ Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | TRUE | TRUE | TRUE | 4.1-9 | FC/SZ Cooling Coil Outlet Relative Humidity [RHcco]
Fig 4.1-10 Supply Fan dT | Figure 4.1-10. FC/SZ Supply Fan Air Temperature Rise | Temperature Rise (°C) | 10 | Fig 4.1-10 Supply Fan dT | Figure 4.1-10. FC/SZ Supply Fan Air Temperature Rise | Temperature Rise (°C) | TRUE | TRUE | TRUE | 4.1-10 | FC/SZ Supply Fan Air Temperature Rise
Fig 4.1-11 SAT | Figure 4.1-11. FC/SZ Supply Air Temperature | Temperature (°C) | 11 | Fig 4.1-11 SAT | Figure 4.1-11. FC/SZ Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-11 | FC/SZ Supply Air Temperature
Fig 4.1-12 SAW | Figure 4.1-12. FC/SZ Supply Air Humidity Ratio | Humidity Ratio (g/gda) | 12 | Fig 4.1-12 SAW | Figure 4.1-12. FC/SZ Supply Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.1-12 | FC/SZ Supply Air Humidity Ratio
Fig 4.1-13 SAVs | Figure 4.1-13. FC/SZ Supply Air Specific Volume | Specific Volume (L/kgda) | 13 | Fig 4.1-13 SAVs | Figure 4.1-13. FC/SZ Supply Air Specific Volume | Specific Volume (L/kgda) | TRUE | TRUE | TRUE | 4.1-13 | FC/SZ Supply Air Specific Volume
Fig 4.1-14 SAenth | Figure 4.1-14. FC/SZ Supply Air Enthalpy | Enthalpy (J/gda) | 14 | Fig 4.1-14 SAenth | Figure 4.1-14. FC/SZ Supply Air Enthalpy | Enthalpy (J/gda) | TRUE | TRUE | TRUE | 4.1-14 | FC/SZ Supply Air Enthalpy
Fig 4.1-15 SAmassflow | Figure 4.1-15. FC/SZ Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 15 | Fig 4.1-15 SAmassflow | Figure 4.1-15. FC/SZ Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.1-15 | FC/SZ Supply Air Mass Flow Rate
Fig 4.1-16 OAFrac | Figure 4.1-16. FC/SZ Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0-1) | 16 | Fig 4.1-16 OAFrac | Figure 4.1-16. FC/SZ Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0-1) | TRUE | TRUE | TRUE | 4.1-16 | FC/SZ Outdoor Air to Supply Air Mass Flow Ratio
Fig 4.1-17 ZoneAirT | Figure 4.1-17. FC/SZ Zone Air Temperature | Temperature (°C) | 17 | Fig 4.1-17 ZoneAirT | Figure 4.1-17. FC/SZ Zone Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-17 | FC/SZ Zone Air Temperature
Fig 4.1-18 ZoneAirW | Figure 4.1-18. FC/SZ Zone Humidity Ratio | Humidity Ratio (g/gda) | 18 | Fig 4.1-18 ZoneAirW | Figure 4.1-18. FC/SZ Zone Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.1-18 | FC/SZ Zone Humidity Ratio
Fig 4.1-19 Zone Lat Gain | Figure 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains | Water Vapor (g/s) | 19 | Fig 4.1-19 Zone Lat Gain | Figure 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains | Water Vapor (g/s) | TRUE | TRUE | TRUE | 4.1-19 | FC/SZ Moisture Added to Zone by Latent Gains
Fig 4.1-20 Return Fan dT | Figure 4.1-20. FC/SZ Return Fan Air Temperature Rise | Temperature Rise (°C) | 20 | Fig 4.1-20 Return Fan dT | Figure 4.1-20. FC/SZ Return Fan Air Temperature Rise | Temperature Rise (°C) | TRUE | TRUE | TRUE | 4.1-20 | FC/SZ Return Fan Air Temperature Rise
Fig 4.1-21 Delta SZ-FC | Figure 4.1-21. FC/SZ Delta Coil Load, SZ - FC | Delta Coil Load (kWh/h) | 21 | Fig 4.1-21 Delta SZ-FC | Figure 4.1-21. FC/SZ Delta Coil Load, SZ - FC | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-21 | FC/SZ Delta Coil Load, SZ - FC
Fig 4.1-22 Delta Econo | Figure 4.1-22. FC/SZ Delta Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | 22 | Fig 4.1-22 Delta Econo | Figure 4.1-22. FC/SZ Delta Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-22 | FC/SZ Delta Coil Load, Economizer Operation

## scrape titles (hidden)
Org Name | Yaxis Title | Proposed Num | New root | New Name | New Title | New Axis Title
HeatCoilkWh (2) | Heating Coil Load (Qh) (kWh/h) | 1 | HeatCoilkWh | Fig 4-1 HeatCoilkWh | Figure 4-1. Airside HVAC - FC/SZ: Heating Coil Load | Heating Coil Load (Qh) (kWh/h)
CoolCoilTot (2) | Cooling Coil Loads, Total (QCtotal) (kWh/h) | 2 | CoolCoilTot | Fig 4-2 CoolCoilTot | Figure 4-2. Airside HVAC - FC/SZ: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h)
CoolCoilSens (2) | Cooling Coil Loads, Sensible (QCsensible) (kWh/h) | 3 | CoolCoilSens | Fig 4-3 CoolCoilSens | Figure 4-3. Airside HVAC - FC/SZ: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
CoolCoilLat (2) | Cooling Coil Loads, Latent (QClatent) (kWh/h) | 4 | CoolCoilLat | Fig 4-4 CoolCoilLat | Figure 4-4. Airside HVAC - FC/SZ: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h)
RHcco (2) | Cooling Coil Outlet Relative Humidity (RHcco) (%) | 5 | RHcco | Fig 4-5 RHcco | Figure 4-5. Airside HVAC - FC/SZ: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%)
OAW (2) | Outdoor Air Humidity Ratio (g/gda) | 6 | OAW | Fig 4-6 OAW | Figure 4-6. Airside HVAC - FC/SZ: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda)
OAmassflow (2) | Outdoor Air Mass Flow Rate (kgda/s) | 7 | OAmassflow | Fig 4-7 OAmassflow | Figure 4-7. Airside HVAC - FC/SZ: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s)
SAT (2) | Supply Air Temperature (°C) | 8 | SAT | Fig 4-8 SAT | Figure 4-8. Airside HVAC - FC/SZ: Supply Air Temperature | Supply Air Temperature (°C)
SAW (2) | Supply Air Humidity Ratio (g/gda) | 9 | SAW | Fig 4-9 SAW | Figure 4-9. Airside HVAC - FC/SZ: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda)
SAVs (2) | Supply Air Specific Volume (L/kgda) | 10 | SAVs | Fig 4-10 SAVs | Figure 4-10. Airside HVAC - FC/SZ: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda)
SAenth (2) | Supply Air Enthalpy (j/gda) | 11 | SAenth | Fig 4-11 SAenth | Figure 4-11. Airside HVAC - FC/SZ: Supply Air Enthalpy | Supply Air Enthalpy (j/gda)
SAmassflow (2) | Supply Air Mass Flow Rate (kgda/s) | 12 | SAmassflow | Fig 4-12 SAmassflow | Figure 4-12. Airside HVAC - FC/SZ: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s)
Supply Fan dT (2) | Supply Fan Temperature Rise (°C) | 13 | Supply Fan dT | Fig 4-13 Supply Fan dT | Figure 4-13. Airside HVAC - FC/SZ: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C)
ZoneAirT (2) | Zone Air Temperature (°C) | 14 | ZoneAirT | Fig 4-14 ZoneAirT | Figure 4-14. Airside HVAC - FC/SZ: Zone Air Temperature | Zone Air Temperature (°C)
Return Fan dT (2) | Return Fan Temperature Rise (°C) | 15 | Return Fan dT | Fig 4-15 Return Fan dT | Figure 4-15. Airside HVAC - FC/SZ: Return Fan Temperature Rise | Return Fan Temperature Rise (°C)
Delta SZ-FC (2) | Delta Coil Loads, SZ - FC ( | 16 | Delta SZ-FC | Fig 4-16 Delta SZ-FC | Figure 4-16. Airside HVAC - FC/SZ: Delta Coil Loads, SZ - FC | Delta Coil Loads (kWh/h), SZ - FC
Delta Econo (2) | Delta Coil Loads, SZ Econo - No Econo ( | 17 | Delta Econo | Fig 4-17 Delta Econo | Figure 4-17. Airside HVAC - FC/SZ: Delta Coil Loads, SZ Econo - No Econo | Delta Coil Loads (kWh/h), SZ Econo - No Econo

## scrape Table names (hidden)
worksheet | Table Name | sequence | Table Name Root | New Table Name | number
Tables 1 | Table 4.1-1. FC/SZ Heating Coil Load [QH] (kWh/h) | 1 | FC/SZ Heating Coil Load [QH] (kWh/h) | Table 4.1-1. FC/SZ Heating Coil Load [QH] (kWh/h) | 4.1-1 | TRUE
Tables 1 | Table 4.1-2. FC/SZ Total Cooling Coil Load [QCtotal] (kWh) | 2 | FC/SZ Total Cooling Coil Load [QCtotal] (kWh) | Table 4.1-2. FC/SZ Total Cooling Coil Load [QCtotal] (kWh) | 4.1-2 | TRUE
Tables 1 | Table 4.1-3. FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) | 3 | FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) | Table 4.1-3. FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) | 4.1-3 | TRUE
Tables 1 | Table 4.1-4. FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) | 4 | FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) | Table 4.1-4. FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) | 4.1-4 | TRUE
Tables 1 | Table 4.1-5. FC/SZ Outdoor Air Temp (°C) | 5 | FC/SZ Outdoor Air Temp (°C) | Table 4.1-5. FC/SZ Outdoor Air Temp (°C) | 4.1-5 | TRUE
Tables 1 | Table 4.1-6. FC/SZ Outdoor Air Humidity Ratio (%) | 6 | FC/SZ Outdoor Air Humidity Ratio (%) | Table 4.1-6. FC/SZ Outdoor Air Humidity Ratio (%) | 4.1-6 | TRUE
Tables 1 | Table 4.1-7. FC/SZ Outdoor Air Mass Flow Rate (kgda/s) | 7 | FC/SZ Outdoor Air Mass Flow Rate (kgda/s) | Table 4.1-7. FC/SZ Outdoor Air Mass Flow Rate (kgda/s) | 4.1-7 | TRUE
Tables 1 | Table 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature (°C) | 8 | FC/SZ Cooling Coil Outlet Air Temperature (°C) | Table 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature (°C) | 4.1-8 | TRUE
Tables 1 | Table 4.1-9. FC/SZ Relative Humidity at Cooling Coil Outlet [Rhcco] (%) | 9 | FC/SZ Relative Humidity at Cooling Coil Outlet [Rhcco] (%) | Table 4.1-9. FC/SZ Relative Humidity at Cooling Coil Outlet [Rhcco] (%) | 4.1-9 | TRUE
Tables 1 | Table 4.1-10. FC/SZ Supply Fan Air Temperature Rise (°C) | 10 | FC/SZ Supply Fan Air Temperature Rise (°C) | Table 4.1-10. FC/SZ Supply Fan Air Temperature Rise (°C) | 4.1-10 | TRUE
Tables 1 | Table 4.1-11. FC/SZ Supply Air Temperature (°C) | 11 | FC/SZ Supply Air Temperature (°C) | Table 4.1-11. FC/SZ Supply Air Temperature (°C) | 4.1-11 | TRUE
Tables 1 | Table 4.1-12. FC/SZ Supply Air Humidity Ratio (g/gda) | 12 | FC/SZ Supply Air Humidity Ratio (g/gda) | Table 4.1-12. FC/SZ Supply Air Humidity Ratio (g/gda) | 4.1-12 | TRUE
Tables 1 | Table 4.1-13. FC/SZ Supply Air Specific Volume (L/kgda) | 13 | FC/SZ Supply Air Specific Volume (L/kgda) | Table 4.1-13. FC/SZ Supply Air Specific Volume (L/kgda) | 4.1-13 | TRUE
Tables 1 | Table 4.1-14. FC/SZ Supply Air Enthalpy (j/gda) | 14 | FC/SZ Supply Air Enthalpy (j/gda) | Table 4.1-14. FC/SZ Supply Air Enthalpy (j/gda) | 4.1-14 | TRUE
Tables 1 | Table 4.1-15. FC/SZ Supply Air Mass Flow Rate (kgda/s) | 15 | FC/SZ Supply Air Mass Flow Rate (kgda/s) | Table 4.1-15. FC/SZ Supply Air Mass Flow Rate (kgda/s) | 4.1-15 | TRUE
Tables 1 | Table 4.1-16. FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) | 16 | FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) | Table 4.1-16. FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) | 4.1-16 | TRUE
Tables 1 | Table 4.1-17. FC/SZ Zone Air Temperature (°C) | 17 | FC/SZ Zone Air Temperature (°C) | Table 4.1-17. FC/SZ Zone Air Temperature (°C) | 4.1-17 | TRUE
Tables 1 | Table 4.1-18. FC/SZ Zone Humidity Ratio (g/gda) | 18 | FC/SZ Zone Humidity Ratio (g/gda) | Table 4.1-18. FC/SZ Zone Humidity Ratio (g/gda) | 4.1-18 | TRUE
Tables 1 | Table 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains (g/s) | 19 | FC/SZ Moisture Added to Zone by Latent Gains (g/s) | Table 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains (g/s) | 4.1-19 | TRUE
Tables 1 | Table 4.1-20. FC/SZ Return Fan Air Temperature Rise (°C) | 20 | FC/SZ Return Fan Air Temperature Rise (°C) | Table 4.1-20. FC/SZ Return Fan Air Temperature Rise (°C) | 4.1-20 | TRUE
Delta Tables 1 | Table 4.1-21. FC/SZ Delta Coil Load: SZ - FC (kWh/h) | 21 | FC/SZ Delta Coil Load: SZ - FC (kWh/h) | Table 4.1-21. FC/SZ Delta Coil Load: SZ - FC (kWh/h) | 4.1-21 | TRUE
Delta Tables 1 | Table 4.1-22. SZ Delta Coil Load: Economizer Operation (kWh/h) | 22 | SZ Delta Coil Load: Economizer Operation (kWh/h) | Table 4.1-22. SZ Delta Coil Load: Economizer Operation (kWh/h) | 4.1-22 | TRUE

## Tables 1
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.1
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE101 through AE245
Table B16.7.1-1. FC/SZ Heating Coil Load [QH] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 8.4195 | 8.4133 | 8.4521 | 8.7675 | 8.4534 | 8.513 | 8.3722 | 8.4159 | 8.452
AE103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE201 | 8.3599 | 8.3488 | 8.3847 | 8.7092 | 8.387 | 8.446 | 8.3021 | 8.3563 | 8.3852
AE203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.1-2. FC/SZ Total Cooling Coil Load [QCtotal] (kWh)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE103 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.76262 | 0.78002 | 0.76511
AE104 | 5.5508 | 5.553 | 5.8358 | 5.5329 | 5.6728 | 5.607 | 5.6456 | 5.5475 | 5.7177
AE201 | 0 | 0 | 0 | 0 | 1.8464e-05 | 0 | 0 | 0 | 0
AE203 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.83037 | 0.85249 | 0.83367
AE204 | 5.6282 | 5.6234 | 5.8966 | 5.7114 | 5.7392 | 5.675 | 5.7133 | 5.6249 | 5.8212
AE205 | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.911 | 1.9128 | 1.9136
AE206 | 2.6768 | 2.6637 | 2.8181 | 2.7314 | 2.7383 | 2.696 | 2.6988 | 2.6709 | 3.2477
AE226 | 3.3617 | 3.335 | 3.6428 | 3.4049 | 3.4182 | 3.377 | 3.3911 | 3.3553 | 3.902
AE245 | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.2021 | 2.209 | 2.2059
Table B16.7.1-3. FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE103 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.75229 | 0.78002 | 0.76511
AE104 | 3.4965 | 3.4882 | 3.5428 | 3.521 | 3.4986 | 3.48 | 3.3892 | 3.4932 | 3.48
AE201 | 0 | 0 | 0 | 0 | 8.048e-08 | 0 | 0 | 0 | 0
AE203 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.81912 | 0.85249 | 0.83367
AE204 | 3.5739 | 3.5587 | 3.6078 | 3.5901 | 3.5657 | 3.547 | 3.4558 | 3.5705 | 3.5482
AE205 | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.8799 | 1.9128 | 1.9136
AE206 | 1.7064 | 1.7005 | 1.7314 | 1.7233 | 1.6967 | 1.695 | 1.6456 | 1.7033 | 1.6939
AE226 | 1.5618 | 1.5568 | 1.593 | 1.5972 | 1.5548 | 1.552 | 1.5033 | 1.5603 | 1.5476
AE245 | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.1715 | 2.209 | 2.2059
Table B16.7.1-4. FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE103 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010332 | 0 | 1.8758e-15
AE104 | 2.0543 | 2.0648 | 2.293 | 2.0119 | 2.1742 | 2.127 | 2.2564 | 2.0544 | 2.2377
AE201 | 0 | 0 | 0 | 0 | 1.8383e-05 | 0 | 0 | 0 | 0
AE203 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01125 | 0 | 3.4106e-16
AE204 | 2.0543 | 2.0648 | 2.2888 | 2.1212 | 2.1735 | 2.128 | 2.2575 | 2.0544 | 2.273
AE205 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031088 | 0 | 6.8212e-16
AE206 | 0.97038 | 0.9632 | 1.0866 | 1.0082 | 1.0417 | 1 | 1.0532 | 0.96766 | 1.5538
AE226 | 1.7999 | 1.7782 | 2.0498 | 1.8077 | 1.8634 | 1.825 | 1.8877 | 1.7951 | 2.3544
AE245 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030615 | 0 | 6.0633e-16
Table B16.7.1-5. FC/SZ Outdoor Air Temp (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE103 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE104 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
AE201 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE203 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE204 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
AE205 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9
AE206 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE226 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE245 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9
Table B16.7.1-6. FC/SZ Outdoor Air Humidity Ratio (%)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025901
AE103 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029334
AE104 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016772
AE201 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025901
AE203 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029334
AE204 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016772
AE205 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481
AE206 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | 0.015566
AE226 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | 0.015566
AE245 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481
Table B16.7.1-7. FC/SZ Outdoor Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.11281 | 0.11283 | 0.11327 | 0.11954 | 0.11367 | 0.11327 | 0.11333 | 0.11281 | 0.11366
AE103 | 0.11149 | 0.11151 | 0.11327 | 0.11241 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | 0.11366
AE104 | 0.11017 | 0.11019 | 0.11327 | 0.10928 | 0.11367 | 0.11327 | 0.11333 | 0.11017 | 0.11366
AE201 | 0.11281 | 0.11283 | 0.11327 | 0.1197 | 0.11367 | 0.11327 | 0.11327 | 0.11281 | 0.11366
AE203 | 0.11149 | 0.11151 | 0.11327 | 0.11256 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | 0.11366
AE204 | 0.11017 | 0.11019 | 0.11327 | 0.10948 | 0.11367 | 0.11327 | 0.11327 | 0.11017 | 0.11366
AE205 | 0.11121 | 0.11123 | 0.11327 | 0.11109 | 0.11367 | 0.11327 | 0.11327 | 0.11121 | 0.11366
AE206 | 0.1099 | 0.10991 | 0.11327 | 0.10983 | 0.11367 | 0.11327 | 0.11327 | 0.1099 | 0.11366
AE226 | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355 | 0.34099
AE245 | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028 | 0.34099
Table B16.7.1-8. FC/SZ Cooling Coil Outlet Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 29.3163 | 29.3262 | 29.0892 | 29.2222 | 29.0494 | 28.994 | 29.0359 | 29.309 | 5.0343
AE103 | 18.5042 | 18.5 | 18.4621 | 19 | 18.5095 | 18.5195 | 18.5081 | 18.5094 | 19.0955
AE104 | 14.9386 | 14.9302 | 14.7013 | 15.2222 | 14.9265 | 14.8437 | 14.9194 | 14.9489 | 15.5085
AE201 | 29.3163 | 29.3262 | 29.0892 | 28.6667 | 29.0498 | 28.9937 | 29.0359 | 29.309 | 4.6484
AE203 | 18.5042 | 18.5 | 18.4622 | 18.4444 | 18.5093 | 18.5187 | 18.5081 | 18.5127 | 18.5133
AE204 | 14.9386 | 14.9302 | 14.7219 | 14.6111 | 14.9264 | 14.8418 | 14.9194 | 14.949 | 14.9397
AE205 | 18.506 | 18.5041 | 18.4632 | 18.4444 | 18.5236 | 18.5187 | 18.5198 | 18.5089 | 18.5269
AE206 | 18.5142 | 18.5118 | 18.4552 | 18.4444 | 18.5888 | 18.5187 | 18.5759 | 18.5234 | 18.5766
AE226 | 18.5142 | 18.5118 | 18.4446 | 18.4444 | 18.5897 | 18.5187 | 18.5759 | 18.52 | 18.5882
AE245 | 18.5044 | 18.5025 | 18.4632 | 18.4444 | 18.5115 | 18.5187 | 18.5096 | 18.5 | 18.515
Table B16.7.1-9. FC/SZ Relative Humidity at Cooling Coil Outlet [RHcco] (%)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 6.3854 | 6.3813 |  | 6.4033 | 6.5151 | 6.75 | 6.8667 | 6.3531 | 29.9492
AE103 | 32.8432 | 32.5417 | 33.03 | 31.6536 | 32.5142 | 32.91 | 32.5498 | 32.8657 | 31.3461
AE104 | 100 | 99.9992 | 98.66 | 99.9615 | 99.6158 | 100 | 100 | 100 | 94.5132
AE201 | 6.3854 | 6.3813 |  | 6.6125 | 6.5149 | 6.75 | 6.8714 | 6.3531 | 30.7672
AE203 | 32.8432 | 32.5417 | 33.03 | 32.7731 | 32.5148 | 32.91 | 32.5498 | 32.8591 | 32.5083
AE204 | 100 | 99.9992 | 98.62 | 100 | 99.6397 | 100 | 100 | 100 | 96.8838
AE205 | 44.5612 | 44.3101 | 44.81 | 44.8531 | 44.111 | 44.59 | 44.2027 | 44.5861 | 44.1036
AE206 | 100 | 99.9992 | 99.36 | 99.9317 | 99.0255 | 100 | 100 | 100 | 86.2414
AE226 | 100 | 99.9992 | 99.65 | 99.9317 | 99.8073 | 100 | 100 | 100 | 95.7376
AE245 | 34.0915 | 33.8389 | 34.33 | 34.2864 | 33.9915 | 34.06 | 34.0684 | 34.1009 | 33.9841
Table B16.7.1-10. FC/SZ Supply Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.60585 | 0.60658 | 0.5899 | 0 | 0.58614 | 0.5818 | 0.589 | 0.60572 | 24.5942
AE103 | 0.58381 | 0.58449 | 0.5899 | 0 | 0.58327 | 0.5818 | 0.589 | 0.58371 | 0
AE104 | 0.57583 | 0.57646 | 0.5899 | 0 | 0.57663 | 0.5818 | 0.589 | 0.57574 | 0
AE201 | 0.60585 | 0.60658 | 0.5899 |  | 0.58614 | 0.5818 | 0.589 | 0.60572 | 24.9797
AE203 | 0.58381 | 0.58449 | 0.5899 |  | 0.58327 | 0.5818 | 0.589 | 0.58372 | 0.58228
AE204 | 0.57583 | 0.57646 | 0.5899 |  | 0.57663 | 0.5818 | 0.589 | 0.57574 | 0.57577
AE205 | 0.5836 | 0.58428 | 0.5899 |  | 0.58162 | 0.5818 | 0.589 | 0.5835 | 0.58063
AE206 | 0.58261 | 0.58329 | 0.5899 |  | 0.57377 | 0.5818 | 0.589 | 0.5825 | 0.57462
AE226 | 0.58261 | 0.58329 | 0.5899 |  | 0.57366 | 0.5818 | 0.589 | 0.5825 | 0.57327
AE245 | 0.58379 | 0.58632 | 0.5899 |  | 0.58306 | 0.5818 | 0.589 | 0.58367 | 0.58207
Table B16.7.1-11. FC/SZ Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 29.9222 | 29.9328 | 29.6791 | 29.2222 | 29.6355 | 29.5758 | 29.6249 | 29.9147 | 29.6284
AE103 | 19.088 | 19.0845 | 19.052 | 19 | 19.0928 | 19.1013 | 19.0971 | 19.0931 | 19.0955
AE104 | 15.5144 | 15.5066 | 15.2912 | 15.2222 | 15.5032 | 15.4255 | 15.5084 | 15.5247 | 15.5085
AE201 | 29.9222 | 29.9328 | 29.6791 |  | 29.6359 | 29.5755 | 29.6249 | 29.9147 | 29.6281
AE203 | 19.088 | 19.0845 | 19.0521 |  | 19.0925 | 19.1005 | 19.0971 | 19.0964 | 19.0955
AE204 | 15.5144 | 15.5066 | 15.3118 |  | 15.5031 | 15.4236 | 15.5084 | 15.5247 | 15.5154
AE205 | 19.0896 | 19.0883 | 19.0531 |  | 19.1052 | 19.1005 | 19.1088 | 19.0924 | 19.1075
AE206 | 19.0968 | 19.0951 | 19.0451 |  | 19.1626 | 19.1005 | 19.1649 | 19.1059 | 19.1512
AE226 | 19.0968 | 19.0951 | 19.0345 |  | 19.1634 | 19.1005 | 19.1649 | 19.1025 | 19.1615
AE245 | 19.0882 | 19.0888 | 19.0531 |  | 19.0946 | 19.1005 | 19.0986 | 19.0837 | 19.0971
Table B16.7.1-12. FC/SZ Supply Air Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.0016041 | 0.0016042 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016965 | 0.0015953 | 0.0016124
AE103 | 0.0043252 | 0.0042844 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | 0.0042846
AE104 | 0.010605 | 0.010599 | 0.010296 | 0.0108 | 0.010558 | 0.010581 | 0.010585 | 0.010612 | 0.010397
AE201 | 0.0016041 | 0.0016041 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016977 | 0.0015953 | 0.0016124
AE203 | 0.0043252 | 0.0042845 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | 0.0042846
AE204 | 0.010605 | 0.0106 | 0.010306 | 0.0104 | 0.010561 | 0.01058 | 0.010585 | 0.010612 | 0.010273
AE205 | 0.0058837 | 0.00585 | 0.0059 | 0.0059 | 0.005832 | 0.005916 | 0.0058378 | 0.0058881 | 0.0058322
AE206 | 0.013368 | 0.013367 | 0.013227 | 0.0133 | 0.013302 | 0.013424 | 0.013413 | 0.013376 | 0.011544
AE226 | 0.013368 | 0.013367 | 0.013257 | 0.0133 | 0.01341 | 0.013424 | 0.013413 | 0.013373 | 0.012851
AE245 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481
Table B16.7.1-13. FC/SZ Supply Air Specific Volume (L/kgda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 860.7762 | 860.6945 | 833.33 |  | 830.3519 |  | 833 | 856.5396 | 860.0546
AE103 | 833.6275 | 833.4546 | 833.33 |  | 830.3519 |  | 833 | 829.5769 | 833.6929
AE104 | 831.6898 | 831.5517 | 833.33 |  | 830.3519 |  | 833 | 827.6673 | 831.4967
AE201 | 860.7762 | 860.6945 | 833.33 |  | 830.3519 |  | 833 | 856.5396 | 860.0537
AE203 | 833.6275 | 833.4546 | 833.33 |  | 830.3519 |  | 833 | 829.5862 | 833.6929
AE204 | 831.6898 | 831.5517 | 833.33 |  | 830.3519 |  | 833 | 827.6674 | 831.3537
AE205 | 835.7063 | 835.549 | 833.33 |  | 830.3519 |  | 833 | 831.6391 | 835.7874
AE206 | 845.6895 | 845.5719 | 833.33 |  | 830.3519 |  | 833 | 841.5963 | 843.5176
AE226 | 845.6895 | 845.5719 | 833.33 |  | 830.3519 |  | 833 | 841.5827 | 845.2874
AE245 | 833.8485 | 833.6965 | 833.33 |  | 830.3519 |  | 833 | 829.7636 | 833.9587
Table B16.7.1-14. FC/SZ Supply Air Enthalpy (J/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 34.2029 |  | 34.02 |  | 33.8997 |  | 34.1363 | 34.1729 | 33.8932
AE103 | 30.1736 |  | 30.14 |  | 30.0522 |  | 30.0761 | 30.1899 | 30.0557
AE104 | 42.4358 |  | 41.4 |  | 42.2878 |  | 42.3718 | 42.4646 | 41.8848
AE201 | 34.2055 |  | 34.02 |  | 33.9001 |  | 34.1393 | 34.1729 | 33.8928
AE203 | 30.1752 |  | 30.14 |  | 30.0519 |  | 30.0761 | 30.1932 | 30.0557
AE204 | 42.4371 |  | 41.44 |  | 42.2941 |  | 42.3718 | 42.4647 | 41.5784
AE205 | 34.1298 |  | 34.1 |  | 33.9902 |  | 34.0251 | 34.1421 | 33.9933
AE206 | 53.121 |  | 52.67 |  | 52.9973 |  | 53.29 | 53.1486 | 48.5263
AE226 | 53.121 |  | 52.74 |  | 53.2723 |  | 53.29 | 53.1378 | 51.8519
AE245 | 30.5955 |  | 30.58 |  | 30.5528 |  | 30.5893 | 30.5893 | 30.5554
Table B16.7.1-15. FC/SZ Supply Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.32963 | 0.32966 | 0.3398 | 0.35862 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | 0.34099
AE103 | 0.34036 | 0.34043 | 0.3398 | 0.33724 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | 0.34099
AE104 | 0.34115 | 0.34121 | 0.3398 | 0.32785 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | 0.34099
AE201 | 0.32963 | 0.32966 | 0.3398 | 0.35909 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | 0.34099
AE203 | 0.34036 | 0.34043 | 0.3398 | 0.33768 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | 0.34099
AE204 | 0.34115 | 0.34121 | 0.3398 | 0.32843 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | 0.34099
AE205 | 0.33952 | 0.33958 | 0.3398 | 0.33327 | 0.34102 | 0.3398 | 0.3398 | 0.33951 | 0.34099
AE206 | 0.33551 | 0.33555 | 0.3398 | 0.32948 | 0.34102 | 0.3398 | 0.3398 | 0.33549 | 0.34099
AE226 | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355 | 0.34099
AE245 | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028 | 0.34099
Table B16.7.1-16. FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.34223 | 0.33333
AE103 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33333
AE104 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.32295 | 0.33333
AE201 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.34223 | 0.33333
AE203 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33333
AE204 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32295 | 0.33333
AE205 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33333
AE206 | 0.32756 | 0.32756 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32757 | 0.33333
AE226 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE245 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Table B16.7.1-17. FC/SZ Zone Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 21.1111 | 21.1111 | 21.0991 | 21.1111 | 21.1183 | 21.111 | 21.111 | 21.1138 | 21.1111
AE103 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3293 | 23.3321 | 23.333 | 23.3325 | 23.3333
AE104 | 23.8889 | 23.8889 | 23.8764 | 23.8889 | 23.8823 | 23.8901 | 23.889 | 23.8905 | 23.8902
AE201 | 21.1111 | 21.1111 | 21.099 | 21.1111 | 21.1187 | 21.1107 | 21.111 | 21.1138 | 21.1108
AE203 | 23.3333 | 23.3333 | 23.3481 | 23.3333 | 23.3288 | 23.3313 | 23.333 | 23.3358 | 23.3333
AE204 | 23.8889 | 23.8889 | 23.897 | 23.8889 | 23.8822 | 23.8882 | 23.889 | 23.8905 | 23.899
AE205 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3296 | 23.3313 | 23.333 | 23.3302 | 23.3333
AE206 | 23.3333 | 23.3333 | 23.3378 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3365 | 23.3334
AE226 | 23.3333 | 23.3333 | 23.3272 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3331 | 23.3338
AE245 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3294 | 23.3313 | 23.333 | 23.3227 | 23.3333
Table B16.7.1-18. FC/SZ Zone Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.00237 | 0.0023731 | 0.0022906 | 0.0022891
AE103 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | 0.0049602
AE104 | 0.01128 | 0.011274 | 0.010986 | 0.0115 | 0.011233 | 0.011285 | 0.011261 | 0.011291 | 0.011072
AE201 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.002374 | 0.0023743 | 0.0022906 | 0.0022891
AE203 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | 0.0049602
AE204 | 0.01128 | 0.011274 | 0.010995 | 0.0111 | 0.011236 | 0.011284 | 0.011261 | 0.011291 | 0.010948
AE205 | 0.0065621 | 0.0065284 | 0.0065931 | 0.0066 | 0.0065075 | 0.00662 | 0.0065133 | 0.0065687 | 0.0065079
AE206 | 0.014054 | 0.014053 | 0.013921 | 0.014 | 0.013978 | 0.014128 | 0.014089 | 0.014065 | 0.01222
AE226 | 0.014054 | 0.014053 | 0.013951 | 0.0141 | 0.014086 | 0.014128 | 0.014089 | 0.014062 | 0.013527
AE245 | 0.0051678 | 0.005134 | 0.0052044 | 0.0052 | 0.0051565 | 0.005212 | 0.0051623 | 0.00517 | 0.0051566
Table B16.7.1-19. FC/SZ Moisture Added to Zone by Latent Gains (g/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE101 | 0.23072 | 0.23072 | 0.23474 | 0.21517 | 0.23073 | 0.23786 | 0.22991 | 0.22921 | 0.23075
AE103 | 0.23034 | 0.23034 | 0.23595 | 0.23607 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037
AE104 | 0.23025 | 0.23026 | 0.23437 | 0.2295 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | 0.23028
AE201 | 0.23072 | 0.23075 | 0.23474 | 0.21546 | 0.23073 | 0.23922 | 0.22991 | 0.22921 | 0.23075
AE203 | 0.23034 | 0.23032 | 0.23595 | 0.23638 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037
AE204 | 0.23025 | 0.23025 | 0.23437 | 0.2299 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | 0.23028
AE205 | 0.23034 | 0.23035 | 0.23551 | 0.23329 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037
AE206 | 0.23034 | 0.23035 | 0.23595 | 0.23064 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037
AE226 | 0.23034 | 0.23035 | 0.23595 | 0.26353 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037
AE245 | 0.23034 | 0.23035 | 0.23595 | 0.23316 | 0.23036 | 0.23922 | 0.22954 | 0.23108 | 0.23037
[(Zone Supply Air Mass Flow) × {(Zone Humidity Ratio) – (Zone Supply Air Humidity Ratio )} × 1000 g/kg]
Table B16.7.1-20. FC/SZ Return Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE201 | 0.27209 | 0.295 | 0.29495 | 0.27778 | 0.28973 | 0.2909 | 0.295 | 0.27201 | 0.29885
AE203 | 0.31262 | 0.29704 | 0.29495 | 0.27778 | 0.29127 | 0.2909 | 0.295 | 0.31247 | 0.29739
AE204 | 0.32615 | 0.29715 | 0.29495 | 0.27778 | 0.28796 | 0.2909 | 0.295 | 0.326 | 0.29466
AE205 | 0.3125 | 0.29693 | 0.29495 | 0.33333 | 0.29045 | 0.2909 | 0.295 | 0.31234 | 0.29655
AE206 | 0.31193 | 0.29641 | 0.29495 | 0.27778 | 0.28654 | 0.2909 | 0.295 | 0.31178 | 0.29348
AE226 | 0.31193 | 0.29641 | 0.29495 | 0.33333 | 0.28648 | 0.2909 | 0.295 | 0.31179 | 0.29279
AE245 | 0.3126 | 0.29703 | 0.29495 | 0.33333 | 0.29117 | 0.2909 | 0.295 | 0.31245 | 0.29728

## Delta Tables 1
ASHRAE Standard 140-2017, Informative Annex B16, Section B16.7.1
Example Results for Section 5.5, Airside HVAC BESTEST Cases AE101 through AE245
Table B16.7.1-21. FC/SZ Delta Coil Load: SZ - FC (kWh/h)
|  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE201-AE101 | Heating | -0.059605 | -0.064549 | -0.067382 | -0.058321 | -0.066421 | -0.067 | -0.070108 | -0.059584 | -0.06686
AE203-AE103 | Sensible Cooling | 0.072652 | 0.068956 | 0.067631 | 0.063303 | 0.067154 | 0.068 | 0.067746 | 0.072468 | 0.068554
AE204-AE104 | Total Cooling | 0.077372 | 0.07042 | 0.06085 | 0.17848 | 0.066443 | 0.068 | 0.067691 | 0.077318 | 0.1035
| Sensible Cooling | 0.077372 | 0.07042 | 0.06503 | 0.069165 | 0.067164 | 0.067 | 0.066631 | 0.077323 | 0.06822
| Latent Cooling | 0 | -5.7732e-15 | -0.0041804 | 0.10932 | -0.00072059 | 0.001 | 0.0010596 | -5.7975e-06 | 0.035283
Table B16.7.1-22. SZ Delta Coil Load: Economizer Operation (kWh/h)
|  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | HAP
Test Case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | Carrier
AE245-AE205 | Total Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29113 | 0.29622 | 0.29227
| Sensible Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29161 | 0.29622 | 0.29227
| Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | -0.00047276 | 0 | -7.5791e-17
AE226-AE206 | Total Cooling | 0.68493 | 0.67125 | 0.82473 | 0.67348 | 0.67988 | 0.681 | 0.69228 | 0.68443 | 0.65422
| Sensible Cooling | -0.14458 | -0.14373 | -0.13841 | -0.12602 | -0.14185 | -0.143 | -0.14226 | -0.143 | -0.14636
| Latent Cooling | 0.82951 | 0.81497 | 0.96314 | 0.7995 | 0.82172 | 0.825 | 0.83454 | 0.82743 | 0.80057

## Detailed Location Results
User-definable chart to look at diagnostic results. Allows selection of test case and diagnostic variable; see Cells B4, B5 (instructions in Cells C4, C5). Displays selected case and diagnostic value for all programs by system location. For selection of viewed program results, see Cells A8-A20, A42-A54 (instructions in Cell A4).
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - Detailed Location Results
| AE101 | <== Select Case | Desc: | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C
| Dry Bulb Temperature (°C) | <== Select Variable | Title | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C Dry Bulb Temperature (°C)
InOut | Tab Name | [13 empty] | Dry Bulb Temperature (°C) | 1
1 | QAS | [11 empty] | OFFSETS |  | Humidity Ratio (g/gda) | 2
1 | DEEAP | [13 empty] | Specific Volume (L/kgda) | 3
1 | DeST | [13 empty] | Enthalpy (J/gda) | 4
1 | DOE22 | [11 empty] | Summary Outputs | Detailed Outputs | Mass Flow Rate (kgda/s) | 5
1 | EPlus | [10 empty] | AE101 | 1 | 1
1 | IES-VE | [10 empty] | AE103 | 2 | 6
1 | LCEM | [10 empty] | AE104 | 3 | 11
1 | TRNSYS | [10 empty] | AE201 | 29 | 29
0 | YourData | [10 empty] | AE203 | 30 | 34
0 | Blank | [10 empty] | AE204 | 31 | 39
0 | Blank | [10 empty] | AE205 | 32 | 44
0 | Blank | [10 empty] | AE206 | 33 | 49
0 | Blank | [10 empty] | AE226 | 34 | 54
[12 empty] | AE245 | 35 | 59
Table Below
*
*
*
*
\/
|  |  | Results Offset ==> | 1 | Results Row ==> | 1 |  | Result Sets ==> | #N/A | Ret Fan Exists | FALSE
| Result Col Offset==> | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Air Loop Location==> | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone
| Air Loop Location==> | Air | Air | Outlet | Outlet | Air | Air
InOut | Tab Name | Outdoor Air | Mixed Air | Heat Coil Outlet | Cool Coil Outlet | Supply Air | Zone Air | Return Air
1 | QAS | -29 | 4.0034 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111 | #N/A
1 | DEEAP | -29 | 4.0029 | 29.3262 | 29.3262 | 29.9328 | 21.1111 | #N/A | #N/A
1 | DeST | -29 | 4.4073 | 29.0892 | 29.0892 | 29.6791 | 21.0991 | 21.0991 | #N/A
1 | DOE22 | -29 | 4.3889 | 29.2222 | 29.2222 | 29.2222 | 21.1111 | 21.1111 | #N/A
1 | EPlus | -29 | 4.4539 | 29.0494 | 29.0494 | 29.6355 | 21.1183 | 21.1183 | #N/A
1 | IES-VE | -29 | 4.4073 | 28.994 | 28.994 | 29.5758 | 21.111 | 21.111 | #N/A
1 | LCEM | -29 | 4.3977 | 29.0359 | 29.0359 | 29.6249 | 21.111 | 21.111 | #N/A
1 | TRNSYS | -29 | 4.0054 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138 | #N/A
0 | YourData | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on A5: Set to 0 to turn off result set.

## Aggregate Results
Output spreadsheet for Airside HVAC BESTEST
0
Aggregator Sheet - Collects data from Plots
Cooling Coil Outlet Relative Humidity (RHcco) (%) |  | Results Column ==> | 8
OFFSETS
Cells B9:N9 contain the tab name of the results set. By changing the tab name all results for that column are changed and plot data updated. It is possible to change the order or plot multiple new results sets by changing the tab names. Plots currently only address through column J. To plot more than 9 results sets the plot ranges must be adjusted.
Tab Name==> | QAS | DEEAP | DeST | DOE22 | EPlus | IES-VE | LCEM | TRNSYS | YourData | Blank | Blank | Blank | Blank |  | Summary Outputs | Detailed Outputs |  |  | Summary Output Columns | Detailed Output Columns
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 6.3854 | 6.3813 | #N/A | 6.4033 | 6.5151 | 6.75 | 6.8667 | 6.3531 | 29.9492 | #N/A | #N/A | #N/A | #N/A | AE101 | 1 | 1 | FC Heat | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C | Zone Sensible Heating Load (QZHsensible) (kWh) | Outdoor Air (oa)
AE103 FC Dry Coil 15.5/-3.0 | 32.8432 | 32.5417 | 33.03 | 31.6536 | 32.5142 | 32.91 | 32.5498 | 32.8657 | 31.3461 | #N/A | #N/A | #N/A | #N/A | AE103 | 2 | 6 | FC Dry Coil | AE103: FC, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Zone Sensible Cooling Load (QZCsensible) (kWh) | Mixed Air (ma)
AE104 FC Wet Coil 26.9/22.1 | 100 | 99.9992 | 98.66 | 99.9615 | 99.6158 | 100 | 100 | 100 | 94.5132 | #N/A | #N/A | #N/A | #N/A | AE104 | 3 | 11 | FC Wet Coil | AE104: FC, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Zone Latent Load (QZlatent) (kWh) | Heat Coil Outlet (hco)
AE201 SZ Heat -29.0/-29.0 | 6.3854 | 6.3813 | #N/A | 6.6125 | 6.5149 | 6.75 | 6.8714 | 6.3531 | 30.7672 | #N/A | #N/A | #N/A | #N/A | AE201 | 29 | 29 | SZ Heat | AE201: FC, Heating, -OD/OWB = 29.00/-29.00 °C | Heating Coil Load (Qh) (kWh) | Cool Coil Outlet (cco)
AE203 SZ Dry Coil 15.5/-3.0 | 32.8432 | 32.5417 | 33.03 | 32.7731 | 32.5148 | 32.91 | 32.5498 | 32.8591 | 32.5083 | #N/A | #N/A | #N/A | #N/A | AE203 | 30 | 34 | SZ Dry Coil | AE203: SZ, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Cooling Coil Loads - Sensible (Qcsensible) (kWh) | Supply Air (sa)
AE204 SZ Wet Coil 26.9/22.1 | 100 | 99.9992 | 98.62 | 100 | 99.6397 | 100 | 100 | 100 | 96.8838 | #N/A | #N/A | #N/A | #N/A | AE204 | 31 | 39 | SZ Wet Coil | AE204: SZ, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Cooling Coil Loads - Latent (Qclatent) (kWh) | Zone Ar (z1)
AE205 SZ Dry Coil 24.9/2.4 No Econo | 44.5612 | 44.3101 | 44.81 | 44.8531 | 44.111 | 44.59 | 44.2027 | 44.5861 | 44.1036 | #N/A | #N/A | #N/A | #N/A | AE205 | 32 | 44 | SZ Dry Coil 2, No Econo | AE205: SZ, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | Cooling Coil Loads - Total (Qctotal) (kWh)
AE206 SZ Wet Coil 23.0/20.9 No Econo | 100 | 99.9992 | 99.36 | 99.9317 | 99.0255 | 100 | 100 | 100 | 86.2414 | #N/A | #N/A | #N/A | #N/A | AE206 | 33 | 49 | SZ Wet Coil 2, No Econo | AE206: SZ, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | Cooling Coil Outlet Relative Humidity (RHcco) (%)
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 100 | 99.9992 | 99.65 | 99.9317 | 99.8073 | 100 | 100 | 100 | 95.7376 | #N/A | #N/A | #N/A | #N/A | AE226 | 34 | 54 | SZ Dry Coil 2, Dry Bulb Econo | AE226: SZ, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo.
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 34.0915 | 33.8389 | 34.33 | 34.2864 | 33.9915 | 34.06 | 34.0684 | 34.1009 | 33.9841 | #N/A | #N/A | #N/A | #N/A | AE245 | 35 | 59 | SZ Wet Coil 2, Enthalpy Econo | AE245: SZ, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo
Heating Coil Load (Qh) (kWh) |  | Results Column ==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 8.4195 | 8.4133 | 8.4521 | 8.7675 | 8.4534 | 8.513 | 8.3722 | 8.4159 | 8.452 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 8.3599 | 8.3488 | 8.3847 | 8.7092 | 8.387 | 8.446 | 8.3021 | 8.3563 | 8.3852 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads - Sensible (Qcsensible) (kWh) |  | Results Column ==> | 5
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.75229 | 0.78002 | 0.76511 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 3.4965 | 3.4882 | 3.5428 | 3.521 | 3.4986 | 3.48 | 3.3892 | 3.4932 | 3.48 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 8.048e-08 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.81912 | 0.85249 | 0.83367 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 3.5739 | 3.5587 | 3.6078 | 3.5901 | 3.5657 | 3.547 | 3.4558 | 3.5705 | 3.5482 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.8799 | 1.9128 | 1.9136 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 1.7064 | 1.7005 | 1.7314 | 1.7233 | 1.6967 | 1.695 | 1.6456 | 1.7033 | 1.6939 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 1.5618 | 1.5568 | 1.593 | 1.5972 | 1.5548 | 1.552 | 1.5033 | 1.5603 | 1.5476 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.1715 | 2.209 | 2.2059 | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads - Latent (Qclatent) (kWh) |  | Results Column ==> | 6
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010332 | 0 | 1.8758e-15 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 2.0543 | 2.0648 | 2.293 | 2.0119 | 2.1742 | 2.127 | 2.2564 | 2.0544 | 2.2377 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 1.8383e-05 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01125 | 0 | 3.4106e-16 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 2.0543 | 2.0648 | 2.2888 | 2.1212 | 2.1735 | 2.128 | 2.2575 | 2.0544 | 2.273 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0.031088 | 0 | 6.8212e-16 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.97038 | 0.9632 | 1.0866 | 1.0082 | 1.0417 | 1 | 1.0532 | 0.96766 | 1.5538 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 1.7999 | 1.7782 | 2.0498 | 1.8077 | 1.8634 | 1.825 | 1.8877 | 1.7951 | 2.3544 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0.030615 | 0 | 6.0633e-16 | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads - Total (Qctotal) (kWh) |  | Results Column ==> | 7
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.76262 | 0.78002 | 0.76511 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 5.5508 | 5.553 | 5.8358 | 5.5329 | 5.6728 | 5.607 | 5.6456 | 5.5475 | 5.7177 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 1.8464e-05 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.83037 | 0.85249 | 0.83367 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 5.6282 | 5.6234 | 5.8966 | 5.7114 | 5.7392 | 5.675 | 5.7133 | 5.6249 | 5.8212 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.911 | 1.9128 | 1.9136 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 2.6768 | 2.6637 | 2.8181 | 2.7314 | 2.7383 | 2.696 | 2.6988 | 2.6709 | 3.2477 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 3.3617 | 3.335 | 3.6428 | 3.4049 | 3.4182 | 3.377 | 3.3911 | 3.3553 | 3.902 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.2021 | 2.209 | 2.2059 | #N/A | #N/A | #N/A | #N/A
Detailed Outputs
Outdoor Air Temp |  | Results Column ==> | 1 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A
Outdoor Air Temperature (just for 5 cases)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE201 SZ Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio |  | Results Column ==> | 1 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029334 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016772 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029334 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016772 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio (just for 5 cases)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE201 SZ Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025901 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029334 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016772 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | 0.015566 | #N/A | #N/A | #N/A | #N/A
Outdoor Air Mass Flow Rat |  | Results Column ==> | 1 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.11281 | 0.11283 | 0.11327 | 0.11954 | 0.11367 | 0.11327 | 0.11333 | 0.11281 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.11149 | 0.11151 | 0.11327 | 0.11241 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.11017 | 0.11019 | 0.11327 | 0.10928 | 0.11367 | 0.11327 | 0.11333 | 0.11017 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.11281 | 0.11283 | 0.11327 | 0.1197 | 0.11367 | 0.11327 | 0.11327 | 0.11281 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.11149 | 0.11151 | 0.11327 | 0.11256 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.11017 | 0.11019 | 0.11327 | 0.10948 | 0.11367 | 0.11327 | 0.11327 | 0.11017 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.11121 | 0.11123 | 0.11327 | 0.11109 | 0.11367 | 0.11327 | 0.11327 | 0.11121 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.1099 | 0.10991 | 0.11327 | 0.10983 | 0.11367 | 0.11327 | 0.11327 | 0.1099 | 0.11366 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028 | 0.34099 | #N/A | #N/A | #N/A | #N/A
Cooling Coil Outlet Air Temperature |  | Results Column ==> | 4 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 29.3163 | 29.3262 | 29.0892 | 29.2222 | 29.0494 | 28.994 | 29.0359 | 29.309 | 5.0343 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 18.5042 | 18.5 | 18.4621 | 19 | 18.5095 | 18.5195 | 18.5081 | 18.5094 | 19.0955 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 14.9386 | 14.9302 | 14.7013 | 15.2222 | 14.9265 | 14.8437 | 14.9194 | 14.9489 | 15.5085 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 29.3163 | 29.3262 | 29.0892 | 28.6667 | 29.0498 | 28.9937 | 29.0359 | 29.309 | 4.6484 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 18.5042 | 18.5 | 18.4622 | 18.4444 | 18.5093 | 18.5187 | 18.5081 | 18.5127 | 18.5133 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 14.9386 | 14.9302 | 14.7219 | 14.6111 | 14.9264 | 14.8418 | 14.9194 | 14.949 | 14.9397 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 18.506 | 18.5041 | 18.4632 | 18.4444 | 18.5236 | 18.5187 | 18.5198 | 18.5089 | 18.5269 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 18.5142 | 18.5118 | 18.4552 | 18.4444 | 18.5888 | 18.5187 | 18.5759 | 18.5234 | 18.5766 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 18.5142 | 18.5118 | 18.4446 | 18.4444 | 18.5897 | 18.5187 | 18.5759 | 18.52 | 18.5882 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 18.5044 | 18.5025 | 18.4632 | 18.4444 | 18.5115 | 18.5187 | 18.5096 | 18.5 | 18.515 | #N/A | #N/A | #N/A | #N/A
Supply Air Temperature |  | Results Column ==> | 5 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 29.9222 | 29.9328 | 29.6791 | 29.2222 | 29.6355 | 29.5758 | 29.6249 | 29.9147 | 29.6284 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 19.088 | 19.0845 | 19.052 | 19 | 19.0928 | 19.1013 | 19.0971 | 19.0931 | 19.0955 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 15.5144 | 15.5066 | 15.2912 | 15.2222 | 15.5032 | 15.4255 | 15.5084 | 15.5247 | 15.5085 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 29.9222 | 29.9328 | 29.6791 | #N/A | 29.6359 | 29.5755 | 29.6249 | 29.9147 | 29.6281 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 19.088 | 19.0845 | 19.0521 | #N/A | 19.0925 | 19.1005 | 19.0971 | 19.0964 | 19.0955 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 15.5144 | 15.5066 | 15.3118 | #N/A | 15.5031 | 15.4236 | 15.5084 | 15.5247 | 15.5154 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 19.0896 | 19.0883 | 19.0531 | #N/A | 19.1052 | 19.1005 | 19.1088 | 19.0924 | 19.1075 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 19.0968 | 19.0951 | 19.0451 | #N/A | 19.1626 | 19.1005 | 19.1649 | 19.1059 | 19.1512 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 19.0968 | 19.0951 | 19.0345 | #N/A | 19.1634 | 19.1005 | 19.1649 | 19.1025 | 19.1615 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 19.0882 | 19.0888 | 19.0531 | #N/A | 19.0946 | 19.1005 | 19.0986 | 19.0837 | 19.0971 | #N/A | #N/A | #N/A | #N/A
Supply Air Humidity Ratio |  | Results Column ==> | 5 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.0016041 | 0.0016042 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016965 | 0.0015953 | 0.0016124 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.0043252 | 0.0042844 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | 0.0042846 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.010605 | 0.010599 | 0.010296 | 0.0108 | 0.010558 | 0.010581 | 0.010585 | 0.010612 | 0.010397 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.0016041 | 0.0016041 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016977 | 0.0015953 | 0.0016124 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.0043252 | 0.0042845 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | 0.0042846 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.010605 | 0.0106 | 0.010306 | 0.0104 | 0.010561 | 0.01058 | 0.010585 | 0.010612 | 0.010273 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0058837 | 0.00585 | 0.0059 | 0.0059 | 0.005832 | 0.005916 | 0.0058378 | 0.0058881 | 0.0058322 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.013368 | 0.013367 | 0.013227 | 0.0133 | 0.013302 | 0.013424 | 0.013413 | 0.013376 | 0.011544 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.013368 | 0.013367 | 0.013257 | 0.0133 | 0.01341 | 0.013424 | 0.013413 | 0.013373 | 0.012851 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | 0.004481 | #N/A | #N/A | #N/A | #N/A
Supply Air Specific Volume |  | Results Column ==> | 5 |  | Results Row Offset==> | 2
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 860.7762 | 860.6945 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 856.5396 | 860.0546 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 833.6275 | 833.4546 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 829.5769 | 833.6929 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 831.6898 | 831.5517 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 827.6673 | 831.4967 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 860.7762 | 860.6945 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 856.5396 | 860.0537 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 833.6275 | 833.4546 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 829.5862 | 833.6929 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 831.6898 | 831.5517 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 827.6674 | 831.3537 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 835.7063 | 835.549 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 831.6391 | 835.7874 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 845.6895 | 845.5719 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 841.5963 | 843.5176 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 845.6895 | 845.5719 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 841.5827 | 845.2874 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 833.8485 | 833.6965 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 829.7636 | 833.9587 | #N/A | #N/A | #N/A | #N/A
Supply Air Enthalpy |  | Results Column ==> | 5 |  | Results Row Offset==> | 3
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 34.2029 | #N/A | 34.02 | #N/A | 33.8997 | #N/A | 34.1363 | 34.1729 | 33.8932 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 30.1736 | #N/A | 30.14 | #N/A | 30.0522 | #N/A | 30.0761 | 30.1899 | 30.0557 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 42.4358 | #N/A | 41.4 | #N/A | 42.2878 | #N/A | 42.3718 | 42.4646 | 41.8848 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 34.2055 | #N/A | 34.02 | #N/A | 33.9001 | #N/A | 34.1393 | 34.1729 | 33.8928 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 30.1752 | #N/A | 30.14 | #N/A | 30.0519 | #N/A | 30.0761 | 30.1932 | 30.0557 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 42.4371 | #N/A | 41.44 | #N/A | 42.2941 | #N/A | 42.3718 | 42.4647 | 41.5784 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 34.1298 | #N/A | 34.1 | #N/A | 33.9902 | #N/A | 34.0251 | 34.1421 | 33.9933 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 53.121 | #N/A | 52.67 | #N/A | 52.9973 | #N/A | 53.29 | 53.1486 | 48.5263 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 53.121 | #N/A | 52.74 | #N/A | 53.2723 | #N/A | 53.29 | 53.1378 | 51.8519 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 30.5955 | #N/A | 30.58 | #N/A | 30.5528 | #N/A | 30.5893 | 30.5893 | 30.5554 | #N/A | #N/A | #N/A | #N/A
Supply Air Mass Flow Rate |  | Results Column ==> | 5 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.32963 | 0.32966 | 0.3398 | 0.35862 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.34036 | 0.34043 | 0.3398 | 0.33724 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.34115 | 0.34121 | 0.3398 | 0.32785 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.32963 | 0.32966 | 0.3398 | 0.35909 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.34036 | 0.34043 | 0.3398 | 0.33768 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.34115 | 0.34121 | 0.3398 | 0.32843 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.33952 | 0.33958 | 0.3398 | 0.33327 | 0.34102 | 0.3398 | 0.3398 | 0.33951 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.33551 | 0.33555 | 0.3398 | 0.32948 | 0.34102 | 0.3398 | 0.3398 | 0.33549 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355 | 0.34099 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028 | 0.34099 | #N/A | #N/A | #N/A | #N/A
Zone Air Temperature |  | Results Column ==> | 6 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.0991 | 21.1111 | 21.1183 | 21.111 | 21.111 | 21.1138 | 21.1111 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3293 | 23.3321 | 23.333 | 23.3325 | 23.3333 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.8764 | 23.8889 | 23.8823 | 23.8901 | 23.889 | 23.8905 | 23.8902 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.099 | 21.1111 | 21.1187 | 21.1107 | 21.111 | 21.1138 | 21.1108 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.3481 | 23.3333 | 23.3288 | 23.3313 | 23.333 | 23.3358 | 23.3333 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.897 | 23.8889 | 23.8822 | 23.8882 | 23.889 | 23.8905 | 23.899 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3296 | 23.3313 | 23.333 | 23.3302 | 23.3333 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 23.3333 | 23.3333 | 23.3378 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3365 | 23.3334 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 23.3333 | 23.3333 | 23.3272 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3331 | 23.3338 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3294 | 23.3313 | 23.333 | 23.3227 | 23.3333 | #N/A | #N/A | #N/A | #N/A
Supply Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.60585 | 0.60658 | 0.5899 | 0 | 0.58614 | 0.5818 | 0.589 | 0.60572 | 24.5942 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.58381 | 0.58449 | 0.5899 | 0 | 0.58327 | 0.5818 | 0.589 | 0.58371 | 0 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.57583 | 0.57646 | 0.5899 | 0 | 0.57663 | 0.5818 | 0.589 | 0.57574 | 0 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.60585 | 0.60658 | 0.5899 | #N/A | 0.58614 | 0.5818 | 0.589 | 0.60572 | 24.9797 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.58381 | 0.58449 | 0.5899 | #N/A | 0.58327 | 0.5818 | 0.589 | 0.58372 | 0.58228 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.57583 | 0.57646 | 0.5899 | #N/A | 0.57663 | 0.5818 | 0.589 | 0.57574 | 0.57577 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.5836 | 0.58428 | 0.5899 | #N/A | 0.58162 | 0.5818 | 0.589 | 0.5835 | 0.58063 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.58261 | 0.58329 | 0.5899 | #N/A | 0.57377 | 0.5818 | 0.589 | 0.5825 | 0.57462 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.58261 | 0.58329 | 0.5899 | #N/A | 0.57366 | 0.5818 | 0.589 | 0.5825 | 0.57327 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.58379 | 0.58632 | 0.5899 | #N/A | 0.58306 | 0.5818 | 0.589 | 0.58367 | 0.58207 | #N/A | #N/A | #N/A | #N/A
Return Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.27209 | 0.295 | 0.29495 | 0.27778 | 0.28973 | 0.2909 | 0.295 | 0.27201 | 0.29885 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.31262 | 0.29704 | 0.29495 | 0.27778 | 0.29127 | 0.2909 | 0.295 | 0.31247 | 0.29739 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.32615 | 0.29715 | 0.29495 | 0.27778 | 0.28796 | 0.2909 | 0.295 | 0.326 | 0.29466 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.3125 | 0.29693 | 0.29495 | 0.33333 | 0.29045 | 0.2909 | 0.295 | 0.31234 | 0.29655 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.31193 | 0.29641 | 0.29495 | 0.27778 | 0.28654 | 0.2909 | 0.295 | 0.31178 | 0.29348 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.31193 | 0.29641 | 0.29495 | 0.33333 | 0.28648 | 0.2909 | 0.295 | 0.31179 | 0.29279 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.3126 | 0.29703 | 0.29495 | 0.33333 | 0.29117 | 0.2909 | 0.295 | 0.31245 | 0.29728 | #N/A | #N/A | #N/A | #N/A
Zone Humidity Ratio Rise (gw/gda) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.00069993 | 0.00069989 | 0.00069081 | 0.0006 | 0.00067658 | 0.0007 | 0.00067658 | 0.00069532 | 0.0006767 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.00067676 | 0.00067661 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00067892 | 0.00067561 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.00067491 | 0.00067482 | 0.00068973 | 0.0007 | 0.00067521 | 0.000704 | 0.00067525 | 0.00067917 | 0.00067533 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.00069993 | 0.00069996 | 0.00069081 | 0.0006 | 0.00067658 | 0.000704 | 0.00067658 | 0.00069532 | 0.0006767 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.00067676 | 0.00067654 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00067893 | 0.00067561 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.00067491 | 0.00067481 | 0.00068973 | 0.0007 | 0.00067521 | 0.000704 | 0.00067525 | 0.00067917 | 0.00067533 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.00067844 | 0.00067834 | 0.00069308 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00068061 | 0.00067561 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.00068655 | 0.00068648 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00068876 | 0.00067561 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.00068655 | 0.00068648 | 0.00069436 | 0.0008 | 0.00067549 | 0.000704 | 0.00067552 | 0.00068875 | 0.0006756 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.00067694 | 0.00067683 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00067908 | 0.00067561 | #N/A | #N/A | #N/A | #N/A
Zone Humidity Ratio (gw/gda) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.00237 | 0.0023731 | 0.0022906 | 0.0022891 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | 0.0049602 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.01128 | 0.011274 | 0.010986 | 0.0115 | 0.011233 | 0.011285 | 0.011261 | 0.011291 | 0.011072 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.002374 | 0.0023743 | 0.0022906 | 0.0022891 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | 0.0049602 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.01128 | 0.011274 | 0.010995 | 0.0111 | 0.011236 | 0.011284 | 0.011261 | 0.011291 | 0.010948 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0065621 | 0.0065284 | 0.0065931 | 0.0066 | 0.0065075 | 0.00662 | 0.0065133 | 0.0065687 | 0.0065079 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.014054 | 0.014053 | 0.013921 | 0.014 | 0.013978 | 0.014128 | 0.014089 | 0.014065 | 0.01222 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.014054 | 0.014053 | 0.013951 | 0.0141 | 0.014086 | 0.014128 | 0.014089 | 0.014062 | 0.013527 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.0051678 | 0.005134 | 0.0052044 | 0.0052 | 0.0051565 | 0.005212 | 0.0051623 | 0.00517 | 0.0051566 | #N/A | #N/A | #N/A | #N/A
Zone Latent Gain (gw/s) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.23072 | 0.23072 | 0.23474 | 0.21517 | 0.23073 | 0.23786 | 0.22991 | 0.22921 | 0.23075 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.23034 | 0.23034 | 0.23595 | 0.23607 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.23025 | 0.23026 | 0.23437 | 0.2295 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | 0.23028 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.23072 | 0.23075 | 0.23474 | 0.21546 | 0.23073 | 0.23922 | 0.22991 | 0.22921 | 0.23075 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.23034 | 0.23032 | 0.23595 | 0.23638 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.23025 | 0.23025 | 0.23437 | 0.2299 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | 0.23028 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.23034 | 0.23035 | 0.23551 | 0.23329 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.23034 | 0.23035 | 0.23595 | 0.23064 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.23034 | 0.23035 | 0.23595 | 0.26353 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23037 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.23034 | 0.23035 | 0.23595 | 0.23316 | 0.23036 | 0.23922 | 0.22954 | 0.23108 | 0.23037 | #N/A | #N/A | #N/A | #N/A

## Delta Results
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - DELTA RESULTS for Delta Plots
Total Heating and Cooling Loads
Tab Name==>
Cases | QAS | DEEAP | DeST | DOE22 | EPlus | IES-VE | LCEM | TRNSYS | YourData | Blank | Blank | Blank | Blank
| QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE201-AE101 Heating -29.0/-29.0 | -0.059605 | -0.064549 | -0.067382 | -0.058321 | -0.066421 | -0.067 | -0.070108 | -0.059584 | -0.06686 | #N/A | #N/A | #N/A | #N/A
AE203-AE103 Dry Coil Cooling 15.5/-3.0 | 0.072652 | 0.068956 | 0.067631 | 0.063303 | 0.067154 | 0.068 | 0.067746 | 0.072468 | 0.068554 | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Total Coil Load 26.9/22.1 | 0.077372 | 0.07042 | 0.06085 | 0.17848 | 0.066443 | 0.068 | 0.067691 | 0.077318 | 0.1035 | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Sensible Coil Load 26.9/22.1 | 0.077372 | 0.07042 | 0.06503 | 0.069165 | 0.067164 | 0.067 | 0.066631 | 0.077323 | 0.06822 | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Latent Coil Load 26.9/22.1 | 0 | -5.7732e-15 | -0.0041804 | 0.10932 | -0.00072059 | 0.001 | 0.0010596 | -5.7975e-06 | 0.035283 | #N/A | #N/A | #N/A | #N/A
Economizer
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
Total Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29113 | 0.29622 | 0.29227 | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29161 | 0.29622 | 0.29227 | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | -0.00047276 | 0 | -7.5791e-17 | #N/A | #N/A | #N/A | #N/A
Total Cooling | 0.68493 | 0.67125 | 0.82473 | 0.67348 | 0.67988 | 0.681 | 0.69228 | 0.68443 | 0.65422 | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.14458 | -0.14373 | -0.13841 | -0.12602 | -0.14185 | -0.143 | -0.14226 | -0.143 | -0.14636 | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0.82951 | 0.81497 | 0.96314 | 0.7995 | 0.82172 | 0.825 | 0.83454 | 0.82743 | 0.80057 | #N/A | #N/A | #N/A | #N/A
Temperature
DB | AE101 | AE102 | AE103 | AE104 | AE105 | AE106
Original DB | -20 | 30 | 60 | 80 | 77 | 74
New DB | -20.2 | 30.02 | 59.9 | 80.42 | 76.82 | 73.4
Original WB | -20 | 20 | 45 | 75 | 55 | 70
New WB | -20.2 | 19.756 | 44.972 | 74.191 | 55.452 | 70.744
Outdoor Air Fraction
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | HAP/Carrier | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.34223 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.32295 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.34223 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32295 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.32756 | 0.32756 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32757 | 0.33333 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | [6 empty] | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | bar: AE101 to AE106
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | [6 empty] | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | bar: AE101 to AE106
|  | Original Case Conditions |  | New Case Conditions |  | June 13th 2012 case conditions
| Case | DB (°F) | WB (°F) | DB (°F) | WB (°F) | DB (°C) | WB (°C)
| AE101 | -20 | -20 | -20.2 | -20.2 | -29 | -29
| AE102 | 30 | 20 | 30.02 | 19.756
| AE103 | 60 | 45 | 59.9 | 44.972 | 15.5 | 7.2
| AE104 | 80 | 75 | 80.42 | 74.191 | 26.9 | 23.4
| AE105 | 77 | 55 | 76.82 | 55.452 | 24.9 | 13.03
| AE106 | 74 | 70 | 73.4 | 70.744 | 23 | 21.5

## QAS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Quasi-Analytical Solution V2 | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: |  |  |  | 2014-10-10 |  | Modeler Organization for Tables and Charts (short): |  |  |  | PSU-TAMU-NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | QAS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | QAS/PSU-TAMU-NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | Quasi-analytic Solution
| Version: | V2
| Date: | 2014-11-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.4195 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0034 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.78348 | 0 | 0.78348 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.4965 | 2.0543 | 5.5508 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.1625 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0513 | 33.5916 | 33.5916 | 34.2029 | 27.0907 | 27.0907
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5042 | 19.088 | 23.3333 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 838.437 | 838.437 | 831.9622 | 833.6275 | 846.6514 | 846.6514
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8833 | 31.8833 | 29.5815 | 30.1736 | 36.2004 | 36.2004
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8678 | 24.8678 | 14.9386 | 15.5144 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 861.9632 | 861.9632 | 830.0307 | 831.6898 | 856.7312 | 856.7312
[16 empty] | Enthalpy (J/gda) | 69.8513 | 58.2685 | 58.2685 | 41.8451 | 42.4358 | 52.7436 | 52.7436
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3599 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1826 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111 | 21.3832
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.85614 | 0 | 0.85614 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304 | 0.002304
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5739 | 2.0543 | 5.6282 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.6715 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895 | 837.4631
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9163 | 0 | 1.9163 | 44.5612 | [6 empty] | Enthalpy (J/gda) | -28.5429 | 8.2324 | 33.5942 | 33.5942 | 34.2055 | 27.0925 | 27.0925 | 27.3675
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7064 | 0.97038 | 2.6768 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681 | 0.21681
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5618 | 1.7999 | 3.3617 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9845 | 20.9845 | 18.5042 | 19.088 | 23.3333 | 23.3333 | 23.6459
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2077 | 0 | 2.2077 | 34.0915 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0374 | 839.0374 | 831.9622 | 833.6275 | 846.6514 | 846.6514 | 847.5441
[16 empty] | Enthalpy (J/gda) | 23.0217 | 32.0985 | 32.0985 | 29.5832 | 30.1752 | 36.2025 | 36.2025 | 36.5199
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888 | 0.22888
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.088 | 25.088 | 14.9386 | 15.5144 | 23.8889 | 23.8889 | 24.215
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.5998 | 862.5998 | 830.0307 | 831.6898 | 856.7312 | 856.7312 | 857.6719
[16 empty] | Enthalpy (J/gda) | 69.8537 | 58.4974 | 58.4974 | 41.8464 | 42.4371 | 52.7457 | 52.7457 | 53.0807
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098 | 0.23098
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0556 | 24.0556 | 18.506 | 19.0896 | 23.3333 | 23.3333 | 23.6458
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0065621 | 0.0065621 | 0.0065621
[16 empty] | Specific volume (L/kgda) | 850.4314 | 849.9075 | 849.9075 | 834.0374 | 835.7063 | 848.7583 | 848.7583 | 849.6529
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.1804 | 39.1804 | 33.5362 | 34.1298 | 40.172 | 40.172 | 40.4903
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33952 | #N/A | 0.22831 | 0.22831
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4335 | 23.4335 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014546 | 0.014546 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.8306 | 859.8306 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.5901 | 60.5901 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5044 | 19.0882 | 23.3333 | 23.3333 | 23.6459
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051678 | 0.0051678 | 0.0051678
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 832.1827 | 833.8485 | 846.8753 | 846.8753 | 847.7683
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 30.0033 | 30.5955 | 36.6243 | 36.6243 | 36.9419
[16 empty] | Mass flow rate (kgda/s) | 0.34027 | 0.34027 | 0.34027 | 0.34027 | 0.34027 | #N/A | 0.22882 | 0.22882
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load | Load | Load | Load | Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 2.947 | 0 | 0 | 0 | 24.7331 | 7.7129 | 8.3889 | AE301 | Dry bulb temperature (°C) | -29 | 3.4316 | 7.2222 | 7.2222 | 7.7838 | 29.2787 | 27.8228 | 21.1111 | 22.2222 | 21.6708 | 22.019
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.7354 | 0 | 6.7354 | 48.1495 | 2.2584 | 2.4572 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0021971 | 0.0023817 | 0.0022901 | 0.0022901
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.3202 | 6.2583 | 16.5785 | 100 | 0.99332 | 1.519 |  | Specific volume (L/kgda) | 691.9314 | 785.4683 | 796.2333 | 796.2333 | 797.8282 | 858.8717 | 854.7372 | 836.5461 | 839.9533 | 838.262 | 839.252
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.3829 | 0 | 9.3829 | 65.719 | 2.2598 | 2.4589 |  | Enthalpy (J/gda) | -28.5429 | 7.3347 | 11.1593 | 11.1593 | 11.726 | 33.4136 | 31.9447 | 26.8208 | 28.4127 | 27.6225 | 27.9743
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9211 | 5.4432 | 14.3643 | 100 | 2.2625 | 2.4624 |  | Mass flow rate (kgda/s) | 0.28139 | 0.77054 | 0.77054 | 0.77054 | 0.77054 | 0.35564 | 0.41491 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.4609 | 12.3018 | 20.7626 | 100 | 2.2625 | 2.4624 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.0184 | 21.0184 | 12.2066 | 12.7778 | 19.1796 | 18.7479 | 23.3333 | 24.4444 | 23.8924 | 24.232
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.7029 | 0 | 9.7029 | 51.0891 | 2.2587 | 2.4575 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0048927 | 0.0050812 | 0.0049876 | 0.0049876
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0074 | 839.0074 | 813.8748 | 815.504 | 833.7629 | 832.5316 | 846.5039 | 849.9317 | 848.2283 | 849.198
[16 empty] | Enthalpy (J/gda) | 23.0217 | 31.8928 | 31.8928 | 22.9579 | 23.5371 | 30.0283 | 29.5906 | 35.9245 | 37.5324 | 36.7334 | 37.0782
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.75384 | 0.75384 | 0.75384 | 0.75384 | 0.34793 | 0.40591 | #N/A | #N/A | 0.47575 | 0.47575
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5732 | 25.5732 | 12.2072 | 12.7778 | 15.5904 | 16.4644 | 23.8889 | 25 | 24.4481 | 24.7899
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.01225 | 0.01225 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095185 | 0.0097082 | 0.0096139 | 0.0096139
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.9099 | 862.9099 | 819.8829 | 821.5223 | 829.6035 | 832.1147 | 854.3485 | 857.802 | 856.0862 | 857.0696
[16 empty] | Enthalpy (J/gda) | 69.8537 | 56.9493 | 56.9493 | 34.6208 | 35.2043 | 38.0804 | 38.9741 | 48.2629 | 49.8839 | 49.0785 | 49.4286
[16 empty] | Mass flow rate (kgda/s) | 0.27554 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47278 | 0.47278
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4777 | 24.4777 | 12.2068 | 12.7778 | 19.1811 | 18.75 | 23.3333 | 24.4444 | 23.8924 | 24.2318
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0064526 | 0.0066415 | 0.0065476 | 0.0065476
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.9862 | 850.9862 | 815.9007 | 817.5333 | 835.842 | 834.6093 | 848.6104 | 852.0467 | 850.3391 | 851.3109
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.3684 | 39.3684 | 26.8906 | 27.4712 | 33.9825 | 33.5441 | 39.8934 | 41.5057 | 40.7045 | 41.0501
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.75197 | 0.75197 | 0.75197 | 0.75197 | 0.34706 | 0.40491 | #N/A | #N/A | 0.47457 | 0.47457
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7742 | 23.7742 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.011806 | 0.011806 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 857.1123 | 857.1123 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 53.9677 | 53.9677 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.27605 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2066 | 12.7778 | 19.1799 | 18.7483 | 23.3333 | 24.4444 | 23.8924 | 24.2319
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051532 | 0.0053417 | 0.005248 | 0.005248
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 814.213 | 815.8428 | 834.11 | 832.8785 | 846.8556 | 850.2849 | 848.5808 | 849.5508
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 23.6145 | 24.194 | 30.6885 | 30.2507 | 36.5871 | 38.1958 | 37.3964 | 37.7413
[16 empty] | Mass flow rate (kgda/s) | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.34778 | 0.40575 | #N/A | #N/A | 0.47555 | 0.47555
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 |  | Zone 1 | Zone 2 |  | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible |  | Latent | Sensible |  | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load |  | Load | Load |  | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZC1sensible) |  | (QZ1latent) | (QZC2sensible) |  | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) |  | (kWh/h) | (kWh/h) |  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.2597 | 0 | 0 | 0 | 4.1447 | 4.4994 | 4.8772 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.2968 | 46.92 | 36.0391 | 21.1111 | 22.2222 | #N/A | #N/A
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.458 | 0 | 1.458 | 36.3949 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.002304 | 0.0023101 | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.399 | 5.9242 | 13.3232 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9314 | 691.9314 | 794.5867 | 794.5867 | 794.7981 | 907.0919 | 876.2548 | 836.6895 | 839.8569 | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1023 | 0 | 4.1023 | 53.4629 | 0 | 0 |  | Enthalpy (J/gda) | -28.5429 | -28.5429 | 7.9172 | 7.9172 | 7.9923 | 47.8758 | 36.9234 | 27.0925 | 28.2306 | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6354 | 4.5879 | 8.2233 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.11281 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.5938 | 5.2366 | 8.8305 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9553 | 16.9553 | 12.6643 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9545
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1575 | 0 | 4.1575 | 49.575 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0049701 | 0.0050294 | 0.005003 | 0.005003
[16 empty] | Specific volume (L/kgda) | 821.5658 | 826.1765 | 826.1765 | 813.9564 | 814.2796 | 814.2796 | 814.2796 | 846.6083 | 849.8616 | 848.4124 | 848.4267
[16 empty] | Enthalpy (J/gda) | 23.0217 | 25.392 | 25.392 | 21.0486 | 21.1635 | 21.1635 | 21.1635 | 36.1213 | 37.4006 | 36.8307 | 36.8358
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.13715 | 0.19854 | #N/A | #N/A | 0.057601 | 0.057601
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7259 | 25.7259 | 12.4805 | 12.7778 | 12.7778 | 12.7778 | 23.8889 | 25 | 24.3792 | 24.4858
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013486 | 0.013486 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0099076 | 0.010241 | 0.010055 | 0.010055
[16 empty] | Specific volume (L/kgda) | 872.9245 | 865.0327 | 865.0327 | 820.8802 | 821.7345 | 821.7345 | 821.7345 | 854.875 | 858.5261 | 856.4857 | 856.7924
[16 empty] | Enthalpy (J/gda) | 69.8537 | 60.2554 | 60.2554 | 35.3116 | 35.6156 | 35.6156 | 35.6156 | 49.2534 | 51.2422 | 50.1307 | 50.2399
[16 empty] | Mass flow rate (kgda/s) | 0.27533 | 0.53919 | 0.53919 | 0.53919 | 0.53919 | 0.25787 | 0.28132 | #N/A | #N/A | 0.26386 | 0.26386
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7375 | 24.7375 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0065301 | 0.0065896 | 0.0065631 | 0.0065631
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4494 | 850.4494 | 815.9814 | 816.3051 | 816.3051 | 816.3051 | 848.715 | 851.9764 | 850.5234 | 850.5376
[16 empty] | Enthalpy (J/gda) | 36.4912 | 37.2305 | 37.2305 | 24.975 | 25.0901 | 25.0901 | 25.0901 | 40.0906 | 41.3736 | 40.802 | 40.807
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.33473 | 0.33473 | 0.33473 | 0.33473 | 0.13676 | 0.19797 | #N/A | #N/A | 0.057335 | 0.057335
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1615 | 23.1615 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014755 | 0.014755 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.3233 | 859.3233 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.8393 | 60.8393 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061741 | 0.0062336 | 0.0062071 | 0.0062071
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 815.5192 | 815.8428 | 815.8428 | 815.8428 | 848.2342 | 851.4937 | 850.0416 | 850.0558
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 24.0789 | 24.194 | 24.194 | 24.194 | 39.1847 | 40.4668 | 39.8956 | 39.9007
[16 empty] | Mass flow rate (kgda/s) | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13685 | 0.1981 | #N/A | #N/A | 0.057395 | 0.057395
* n/a = not applicable

## DEEAP
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | AAON Detailed Energy and Economic Analysis Program 1.1.2 | [5 empty] | AAON Inc.
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | AAON
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DEEAP
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2012-12-10 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DEEAP/AAON
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | AAON Detailed Energy and Economics Analysis Program
| Version: | 1.1.2
| Date: | 2012-12-10
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9309 |  | 0.58608 | 8.4133 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0029 | 29.3262 | 29.3262 | 29.9328 | 21.1111
| AE103 |  | 1.4649 | 0.586 | 0 | 0.78407 | 0 | 0.78407 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016042 | 0.0023041
| AE104 |  | 2.9303 | 0.58608 | 0 | 3.4882 | 2.0648 | 5.553 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.0586 | 858.9719 | 858.9719 | 860.6945 | 836.5805
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5 | 19.0845 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.2732 | 838.2732 | 831.7876 | 833.4546 | 846.4857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.8642 | 24.8642 | 14.9302 | 15.5066 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.010599 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 861.8387 | 861.8387 | 829.891 | 831.5517 | 856.6119
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9309 |  | 0.58608 | 8.3488 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1972 | 29.3262 | 29.3262 | 29.9328 | 21.1111 | 21.1111 | 21.4061
| AE203 |  | 1.4649 | 0.586 | 0 | 0.85303 | 0 | 0.85303 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0023041 | 0.0023041 | 0.0023041
| AE204 |  | 2.9303 | 0.58608 | 0 | 3.5587 | 2.0648 | 5.6234 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.6103 | 858.9719 | 858.9719 | 860.6945 | 836.5805 | 836.5805 | 837.4192
| AE205 |  | 1.4642 | 0.58608 | 0 | 1.9099 | 0 | 1.9099 | 44.3101 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 |  | 1.4644 | 0.58608 | 0 | 1.7005 | 0.9632 | 2.6637 | 99.9992 | [6 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A | 0.21683 | 0.21683
| AE226 |  | 1.4644 | 0.58608 | 0 | 1.5568 | 1.7782 | 3.335 | 99.9992 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9741 | 20.9741 | 18.5 | 19.0845 | 23.3333 | 23.3333 | 23.6304
| AE245 |  | 1.4642 | 0.58608 | 0 | 2.202 | 0 | 2.202 | 33.8389 | [6 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042845 | 0.0049611 | 0.0049611 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.8436 | 838.8436 | 831.7876 | 833.4546 | 846.4857 | 846.4857 | 847.3338
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A | 0.22893 | 0.22893
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.0648 | 25.0648 | 14.9302 | 15.5066 | 23.8889 | 23.8889 | 24.186
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.0106 | 0.011274 | 0.011274 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.4186 | 862.4186 | 829.891 | 831.5517 | 856.6119 | 856.6119 | 857.4688
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A | 0.23102 | 0.23102
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0415 | 24.0415 | 18.5041 | 19.0883 | 23.3333 | 23.3333 | 23.6303
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0058499 | 0.0058499 | 0.0058499 | 0.00585 | 0.0065284 | 0.0065284 | 0.0065284
[16 empty] | Specific volume (L/kgda) | 850.243 | 849.7105 | 849.7105 | 833.8783 | 835.549 | 848.6018 | 848.6018 | 849.4517
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11123 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | #N/A | 0.22835 | 0.22835
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4231 | 23.4231 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014534 | 0.014534 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.6718 | 859.6718 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10991 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33555 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.5025 | 19.0888 | 23.3333 | 23.3333 | 23.6304
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.005134 | 0.005134 | 0.005134
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 832.0238 | 833.6965 | 846.7192 | 846.7192 | 847.5674
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.34033 | 0.34033 | 0.34033 | 0.34033 | 0.34033 | #N/A | 0.22886 | 0.22886
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9309 |  | 0.58608 | 2.3449 |  | 0.87918 | 2.9697 | 0 | 0 | 0 | 24.7328 | 7.7075 | 8.3822 | AE301 | Dry bulb temperature (°C) | -29 | 3.3982 | 7.2222 | 7.2222 | 7.7845 | 29.2883 | 27.8298 | 21.1111 | 22.2222 | 21.6708 | 21.9663
| AE303 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 6.7082 | 0 | 6.7082 | 47.6873 | 2.2547 | 2.4515 |  | Humidity ratio (g/gda) | 0.00025894 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0021972 | 0.0023819 | 0.0022902 | 0.0022902
| AE304 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 10.2556 | 6.2947 | 16.5503 | 99.9992 | 0.98884 | 1.5135 |  | Specific volume (L/kgda) | 691.8414 | 785.2713 | 796.1298 | 796.1298 | 797.7263 | 858.7874 | 854.646 | 836.4373 | 839.8441 | 838.1531 | 838.9934
| AE305 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.3496 | 0 | 9.3496 | 65.3364 | 2.2561 | 2.4532 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.8688 | 5.4441 | 14.3129 | 99.9992 | 2.2588 | 2.4568 |  | Mass flow rate (kgda/s) | 0.28143 | 0.77064 | 0.77064 | 0.77064 | 0.77064 | 0.35568 | 0.41496 | #N/A | #N/A | 0.48921 | 0.48921
| AE326 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.3501 | 12.3442 | 20.6943 | 99.9992 | 2.2588 | 2.4568 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.9919 | 20.9919 | 12.2059 | 12.7778 | 19.1761 | 18.7408 | 23.3333 | 24.4444 | 23.8924 | 24.19
| AE345 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.6843 | 0 | 9.6843 | 50.7067 | 2.255 | 2.4518 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0048518 | 0.0050403 | 0.0049466 | 0.0049466
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.7678 | 838.7678 | 813.7138 | 815.3446 | 833.59 | 832.3485 | 846.3382 | 849.7654 | 848.0623 | 848.912
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.75399 | 0.75399 | 0.75399 | 0.75399 | 0.348 | 0.40599 | #N/A | #N/A | 0.47585 | 0.47585
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5414 | 25.5414 | 12.2065 | 12.7778 | 15.5808 | 16.4551 | 23.8889 | 25 | 24.4481 | 24.7459
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.012254 | 0.012254 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095186 | 0.0097084 | 0.0096141 | 0.0096141
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.7095 | 862.7095 | 819.774 | 821.4151 | 829.4677 | 831.9792 | 854.2369 | 857.69 | 855.9744 | 856.831
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27557 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47284 | 0.47284
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4471 | 24.4471 | 12.2061 | 12.7778 | 19.1778 | 18.7428 | 23.3333 | 24.4444 | 23.8924 | 24.1899
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0064187 | 0.0066076 | 0.0065137 | 0.0065137
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.7417 | 850.7417 | 815.7483 | 817.3825 | 835.6783 | 834.4349 | 848.4538 | 851.8894 | 850.1822 | 851.0336
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.34713 | 0.40498 | #N/A | #N/A | 0.47466 | 0.47466
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7478 | 23.7478 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.011794 | 0.011794 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 856.9076 | 856.9076 | 819.774 | 821.4151 | 839.8095 | 839.8095 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27609 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 819.774 | 821.4151 | 839.8095 | 838.5636 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2059 | 12.7778 | 19.1765 | 18.7411 | 23.3333 | 24.4444 | 23.8924 | 24.19
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0051194 | 0.0053078 | 0.0052142 | 0.0052142
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 814.0611 | 815.6925 | 833.9468 | 832.7047 | 846.6994 | 850.1279 | 848.4242 | 849.2742
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.34785 | 0.40582 | #N/A | #N/A | 0.47566 | 0.47566
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9309 |  | 0.58608 | 2.3448 |  | 0.87918 | 10.2479 | 0 | 0 | 0 | 4.1474 | 4.4963 | 4.8725 | AE401 | Dry bulb temperature (°C) | -29 | -28.9957 | 7.2222 | 7.2222 | 7.3083 | 46.9483 | 36.0548 | 21.1111 | 22.2222
| AE403 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 1.4663 | 0 | 1.4663 | 36.0086 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025894 | 0.00025911 | 0.00025911 | 0.00025911 | 0.00025861 | 0.00025861 | 0.00025861 | 0.0023034 | 0.0023096
| AE404 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 7.3735 | 5.9745 | 13.348 | 99.9992 | 0 | 0 |  | Specific volume (L/kgda) | 691.8414 | 691.8536 | 794.4835 | 794.4835 | 794.7275 | 907.0536 | 876.1849 | 836.5796 | 839.7468
| AE405 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1049 | 0 | 4.1049 | 53.1717 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.6094 | 4.6068 | 8.2162 | 99.9992 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.11283 | 0.1686 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.5586 | 5.2655 | 8.8241 | 99.9992 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9621 | 16.9621 | 12.6466 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.981
| AE445 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1596 | 0 | 4.1596 | 49.2421 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.00493 | 0.0049886 | 0.0049625 | 0.0049625
[16 empty] | Specific volume (L/kgda) | 821.4055 | 826.0373 | 826.0373 | 813.7497 | 814.1232 | 814.1236 | 814.1236 | 846.4437 | 849.6953 | 848.2496 | 848.3367
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.33612 | 0.33612 | 0.33612 | 0.33612 | 0.13729 | 0.19883 | #N/A | #N/A | 0.057974 | 0.057974
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.91 | 25.91 | 12.4612 | 12.7778 | 12.7777 | 12.7777 | 23.8889 | 25 | 24.3794 | 24.4935
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.01348 | 0.01348 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0098953 | 0.010229 | 0.010042 | 0.010042
[16 empty] | Specific volume (L/kgda) | 872.7897 | 864.9025 | 864.9025 | 820.7028 | 821.6126 | 821.6122 | 821.6122 | 854.7464 | 858.3966 | 856.3573 | 856.6857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27537 | 0.53988 | 0.53988 | 0.53988 | 0.53988 | 0.25821 | 0.28167 | #N/A | #N/A | 0.2645 | 0.2645
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.728 | 24.728 | 12.6468 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.004814 | 0.004814 | 0.004814 | 0.004814 | 0.0048143 | 0.0048143 | 0.006497 | 0.0065555 | 0.0065295 | 0.0065295
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.268 | 850.268 | 815.7831 | 816.1571 | 816.1574 | 816.1574 | 848.5594 | 851.8189 | 850.3696 | 850.3892
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.13689 | 0.19826 | #N/A | #N/A | 0.057705 | 0.057705
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1628 | 23.1628 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014721 | 0.014721 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.169 | 859.169 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27556 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6519 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0061387 | 0.0061973 | 0.0061712 | 0.0061712
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 815.3186 | 815.6925 | 815.6925 | 815.6925 | 848.0757 | 851.3333 | 849.8849 | 849.9045
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.13698 | 0.19839 | #N/A | #N/A | 0.057768 | 0.057768
* n/a = not applicable

## DeST
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Designer's Simulation Toolkit 2 | [5 empty] | Tsinghua University / Lawarence Berkeley National Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TsinghuaU-LBNL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DeST
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2013-11-21 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DeST/TsinghuaU-LBNL
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | DeST
| Version: | 2
| Date: | 2013-11-21
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.93 |  | 0.5867 | 8.4521 | 0 | 0 | 0 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4073 | 29.0892 | 29.0892 | 29.6791 | 21.0991 | 21.0991
| AE103 |  | 1.4666 | 0.58971 | 0 | 0.7777 | 0 | 0.7777 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324
| AE104 |  | 2.9311 | 0.58578 | 0 | 3.5428 | 2.293 | 5.8358 | 98.66 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | -28.5113 | 8.55 | 33.4266 | 33.4266 | 34.02 | 27.1262 | 27.1262
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.722 | 20.722 | 18.4621 | 19.052 | 23.3479 | 23.3479
[16 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.83 | 31.83 | 29.54 | 30.14 | 36.26 | 36.26
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8861 | 24.8861 | 14.7013 | 15.2912 | 23.8764 | 23.8764
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012947 | 0.012947 | 0.010296 | 0.010296 | 0.010986 | 0.010986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 57.97 | 57.97 | 40.79 | 41.4 | 51.94 | 51.94
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 |  | 0.59 | 8.3847 | 0 | 0 | 0 | [6 empty] | AET201a | Dry bulb temperature (°C) | -29 | 4.604 | 29.0892 | 29.0892 | 29.6791 | 21.099 | 21.099 | 21.3939
| AE203 |  | 1.4666 | 0.58971 | 0 | 0.84533 | 0 | 0.84533 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324 | 0.0023324
| AE204 |  | 2.9311 | 0.58578 | 0 | 3.6078 | 2.2888 | 5.8966 | 98.62 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE205 |  | 1.47 | 0.59 | 0 | 1.9287 | 0 | 1.9287 | 44.81 | [6 empty] | Enthalpy (J/gda) | -28.5113 | 8.75 | 33.43 | 33.43 | 34.02 | 27.13 | 27.13 | 27.42
| AE206 |  | 1.47 | 0.59 | 0 | 1.7314 | 1.0866 | 2.8181 | 99.36 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 |  | 1.4655 | 0.58971 | 0 | 1.593 | 2.0498 | 3.6428 | 99.65 | [5 empty] | AET203a | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.4622 | 19.0521 | 23.3481 | 23.3481 | 23.643
| AE245 |  | 1.4663 | 0.58971 | 0 | 2.2158 | 0 | 2.2158 | 34.33 | [6 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 32.02 | 32.02 | 29.54 | 30.14 | 36.26 | 36.26 | 36.56
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET204a | Dry bulb temperature (°C) | 26.9 | 25.0935 | 25.0935 | 14.7219 | 15.3118 | 23.897 | 23.897 | 24.192
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012952 | 0.012952 | 0.010306 | 0.010306 | 0.010995 | 0.010995 | 0.011319
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 58.2 | 58.2 | 40.84 | 41.44 | 51.99 | 51.99 | 52.29
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET205a | Dry bulb temperature (°C) | 24.9 | 24.052 | 24.052 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6428
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0058987 | 0.0058987 | 0.0058987 | 0.0059 | 0.0065931 | 0.0065931 | 0.00659
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5 | 39.18 | 39.18 | 33.5 | 34.1 | 40.23 | 40.23 | 40.53
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET206a | Dry bulb temperature (°C) | 23 | 23.4067 | 23.4067 | 18.4552 | 19.0451 | 23.3378 | 23.3378 | 23.6328
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014484 | 0.014484 | 0.013227 | 0.013227 | 0.013921 | 0.013921 | 0.013921
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 60.36 | 60.36 | 52.06 | 52.67 | 58.85 | 58.85 | 59.16
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET226a | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4446 | 19.0345 | 23.3272 | 23.3272 | 23.6221
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.013257 | 0.013257 | 0.013951 | 0.013951 | 0.013951
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 52.13 | 52.74 | 58.92 | 58.92 | 58.92
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET245a | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6429
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0052044 | 0.0052044
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.51 | 36.51 | 36.51 | 29.98 | 30.58 | 36.7 | 36.7 | 36.7
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 3.58 | 0 | 0 | 0 |  | 7.4721 | 8.0774 | AET301 | Dry bulb temperature (°C) | -29 | 2.3874 | 7.22 | 7.22 | 7.8099 | 29.6699 | 28.084 | 21.111 | 22.222 | 21.7092 | 22.0042
| AE303 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 6.4595 | 0 | 6.4595 | 48.22 | 2.1363 | 2.3 |  | Humidity ratio (g/gda) | 0.00026 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0022251 | 0.0024213 | 0.0023308 | 0.0023308
| AE304 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 10.0587 | 7.0108 | 17.0695 | 95.49 | 0.85904 | 1.3509 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE305 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.1806 | 0 | 9.1806 | 65.84 | 2.1367 | 2.3017 |  | Enthalpy (J/gda) | -28.5113 | 6.24 | 11.11 | 11.11 | 11.71 | 33.74 | 32.14 | 26.8658 | 28.4854 | 27.74 | 28.04
| AE306 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.6987 | 6.1035 | 14.8022 | 96.21 | 2.1374 | 2.3004 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
| AE326 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.1141 | 12.8792 | 20.9933 | 98.89 | 2.1374 | 2.3005 | AET303 | Dry bulb temperature (°C) | 15.5 | 20.87 | 20.87 | 12.2049 | 12.7948 | 19.05 | 18.57 | 23.333 | 24.444 | 23.9462 | 24.2412
| AE345 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.4684 | 0 | 9.4684 | 51.33 | 2.1374 | 2.3005 |  | Humidity ratio (g/gda) | 0.002948 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0049298 | 0.0051345 | 0.00504 | 0.0049864
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.73 | 31.73 | 22.95 | 23.55 | 29.88 | 29.4 | 35.99 | 37.63 | 36.89 | 37.19
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET304 | Dry bulb temperature (°C) | 26.9 | 25.5957 | 25.5957 | 12.2047 | 12.7946 | 15.3101 | 16.1852 | 23.889 | 25 | 24.502 | 24.7969
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012182 | 0.012182 | 0.0084426 | 0.0084426 | 0.0084426 | 0.0084426 | 0.00914 | 0.00934 | 0.0092505 | 0.0092505
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 56.75 | 56.75 | 33.56 | 34.16 | 36.73 | 37.62 | 47.2602 | 48.9046 | 48.17 | 48.47
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET305 | Dry bulb temperature (°C) | 24.9 | 24.4854 | 24.4854 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0064918 | 0.0066965 | 0.006602 | 0.006602
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 39.36 | 39.36 | 26.89 | 27.49 | 33.84 | 33.36 | 39.96 | 41.61 | 40.86 | 41.16
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET306 | Dry bulb temperature (°C) | 23 | 23.7552 | 23.7552 | 12.1759 | 12.7658 | 19.0246 | 18.5398 | 23.333 | 24.444 | 23.9171 | 24.2121
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.011752 | 0.011752 | 0.0084916 | 0.0084916 | 0.0084916 | 0.0084916 | 0.00919 | 0.00939 | 0.0092962 | 0.009673
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 53.77 | 53.77 | 33.66 | 34.26 | 40.65 | 40.15 | 46.81 | 48.47 | 47.69 | 47.99
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2038 | 12.7937 | 19.0525 | 18.5677 | 23.333 | 24.444 | 23.9451 | 24.24
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0094417 | 0.00965 | 0.009552 | 0.009552
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 34.33 | 34.93 | 41.32 | 40.8278 | 47.45 | 49.14 | 48.37 | 48.37
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0054091 | 0.0053146 | 0.0053146
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 23.64 | 24.24 | 30.55 | 30.07 | 36.68 | 38.33 | 37.59 | 37.59
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 10.31 | 0 | 0 | 0 |  | 4.5019 | 4.891 | AET401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3073 | 46.8548 | 35.9521 | 21.111 | 22.222 | 21.7776 | 21.7776
| AE403 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 1.4433 | 0 | 1.4433 | 36.39 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.0023324 | 0.0023296 | 0.0023308 | 0.0023308
| AE404 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 7.4502 | 6.5805 | 14.0307 | 97.24 | 0 | 0 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE405 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1432 | 0 | 4.1432 | 53.52 | 0 | 0 |  | Enthalpy (J/gda) | -28.5113 | -28.5113 | 7.91 | 7.91 | 8 | 47.76 | 36.8 | 27.1382 | 28.2525 | 27.8068 | 27.8068
| AE406 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.6269 | 4.9686 | 8.5955 | 99.38 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.5745 | 5.6327 | 9.2072 | 99.58 | 0 | 0 | AET403 | Dry bulb temperature (°C) | 15.5 | 16.888 | 16.888 | 12.6699 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.005 | 24.0094
| AE445 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1914 | 0 | 4.1914 | 49.78 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002948 | 0.00329 | 0.00329 | 0.00329 | 0.0032876 | 0.0032876 | 0.0032876 | 0.0049958 | 0.0050706 | 0.00504 | 0.00504
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 25.3 | 25.3 | 21.03 | 21.16 | 21.16 | 21.16 | 36.1476 | 37.47 | 36.95 | 36.95
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.13832 | 0.20018 | #N/A | #N/A | 0.055336 | 0.055336
[15 empty] | AET404 | Dry bulb temperature (°C) | 26.9 | 25.7508 | 25.7508 | 12.4633 | 12.7916 | 12.7916 | 12.7916 | 23.889 | 25 | 24.48 | 24.5817
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.013454 | 0.013454 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0096515 | 0.0099979 | 0.0098321 | 0.0098321
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 60.15 | 60.15 | 34.6 | 34.93 | 34.93 | 34.93 | 48.56 | 50.58 | 49.63 | 49.73
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54925 | 0.54925 | 0.54925 | 0.54925 | 0.26284 | 0.28641 | #N/A | #N/A | 0.26609 | 0.26609
[15 empty] | AET405 | Dry bulb temperature (°C) | 24.9 | 24.7517 | 24.7517 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 23.9959 | 24.0003
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.0065572 | 0.006633 | 0.0065986 | 0.0065986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 37.2162 | 37.2162 | 24.97 | 25.1 | 25.1 | 25.1 | 40.1156 | 41.45 | 40.92 | 40.92
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13829 | 0.20003 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET406 | Dry bulb temperature (°C) | 23 | 23.1638 | 23.1638 | 12.6693 | 12.7939 | 12.7939 | 12.7939 | 23.333 | 24.444 | 24.0041 | 24.0085
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014845 | 0.014845 | 0.0090684 | 0.0090684 | 0.0090684 | 0.0090684 | 0.010775 | 0.010849 | 0.010819 | 0.010819
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 61.03 | 61.03 | 35.62 | 35.74 | 35.74 | 35.74 | 50.85 | 52.18 | 51.65 | 51.65
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055191 | 0.055191
[15 empty] | AET426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6574 | 12.782 | 12.782 | 12.782 | 23.333 | 24.444 | 23.9922 | 23.9966
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0090802 | 0.0090802 | 0.0090802 | 0.0090802 | 0.010787 | 0.010861 | 0.010831 | 0.010831
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 35.63 | 35.76 | 35.76 | 35.76 | 50.88 | 52.2078 | 51.67 | 51.67
[16 empty] | Mass flow rate (kgda/s) | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.0049 | 24.0093
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0062162 | 0.006292 | 0.006261 | 0.006261
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 24.11 | 24.24 | 24.24 | 24.24 | 39.26 | 40.58 | 40.05 | 40.06
[16 empty] | Mass flow rate (kgda/s) | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
* n/a = not applicable

## DOE22
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | DOE-2.2 V48L | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DOE-2.2
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-03-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DOE-2.2/NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | DOE2.2 Design Day
| Version: | 2.2-48L
| Date: | 2015-03-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone |  | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible |  | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Load |  | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) |  | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh) |  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.7675 | 0 | 0 | 0 | 6.4033 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3889 | 29.2222 | 29.2222 | 29.2222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.77693 | 0 | 0.77693 | 31.6536 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.521 | 2.0119 | 5.5329 | 99.9615 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11954 | 0.35862 | 0.35862 | 0.35862 | 0.35862 | #N/A | 0.23908 |  |  | Aug 7, 2015: Zone air mass flows set to "NA" by JN
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.6889 | 21.2778 | 19 | 19 | 23.3333 | 23.3333 |  |  | Matches most recent output template.
[16 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11241 | 0.33724 | 0.33724 | 0.33724 | 0.33724 | #N/A | 0.22483
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.9056 | 25.5 | 15.2222 | 15.2222 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0132 | 0.0132 | 0.0108 | 0.0108 | 0.0115 | 0.0115
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10928 | 0.32785 | 0.32785 | 0.32785 | 0.32785 | #N/A | 0.21857
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.7092 | 0 | 0 | 0 | 6.6125 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6111 | 28.6667 | 28.6667 | #N/A | 21.1111 | 21.1111 | 21.3889
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.84024 | 0 | 0.84024 | 32.7731 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022 | 0.0022
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5901 | 2.1212 | 5.7114 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9085 | 0 | 1.9085 | 44.8531 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7233 | 1.0082 | 2.7314 | 99.9317 | [6 empty] | Mass flow rate (kgda/s) | 0.1197 | 0.35909 | 0.35909 | 0.35909 | 0.35909 | #N/A | 0.2394 | 0.2394
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5972 | 1.8077 | 3.4049 | 99.9317 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.8889 | 20.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.1878 | 0 | 2.1878 | 34.2864 | [6 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11256 | 0.33768 | 0.33768 | 0.33768 | 0.33768 | #N/A | 0.22512 | 0.22512
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.1111 | 25.1111 | 14.6111 | #N/A | 23.8889 | 23.8889 | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.013 | 0.013 | 0.0104 | 0.0104 | 0.0111 | 0.0111 | 0.0111
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10948 | 0.32843 | 0.32843 | 0.32843 | 0.32843 | #N/A | 0.21895 | 0.21895
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0556 | 24.0556 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0059 | 0.0059 | 0.0059 | 0.0059 | 0.0066 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11109 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | #N/A | 0.22218 | 0.22218
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4444 | 23.4444 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0145 | 0.0145 | 0.0133 | 0.0133 | 0.014 | 0.014 | 0.014
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10983 | 0.32948 | 0.32948 | 0.32948 | 0.32948 | #N/A | 0.21965 | 0.21965
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0133 | 0.0133 | 0.0141 | 0.0141 | 0.0141
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | #N/A | 0.21961 | 0.21961
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0052 | 0.0052 | 0.0052
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.33309 | #N/A | 0.22206 | 0.22206
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 3.7882 | 0 | 0 | 0 | 23.9613 | 7.706 | 8.3763 | AE301 | Dry bulb temperature (°C) | -29 | #N/A | 7.2222 | 7.2222 | 7.7778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | 21.9444
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.4197 | 0 | 6.4197 | 47.9247 | 2.15 | 2.3194 |  | Humidity ratio (g/gda) | 0.0003 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | #N/A | #N/A | 0.0022 | 0.0022
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 9.8897 | 6.214 | 16.1037 | 100 | 0.79774 | 1.2681 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9287 | 0 | 8.9287 | 65.5319 | 2.0723 | 2.2232 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.5975 | 5.4338 | 14.0314 | 100 | 2.1107 | 2.2695 |  | Mass flow rate (kgda/s) | 0.29649 | 0.77088 | 0.77088 | 0.77088 | 0.77088 | 0.35579 | 0.41509 | #N/A | #N/A | 0.47438 | 0.47438
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.2315 | 11.7123 | 19.9438 | 100 | 2.1256 | 2.2886 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8333 | 20.8333 | 12.1667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.2222
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.2851 | 0 | 9.2851 | 51.1359 | 2.0887 | 2.2414 |  | Humidity ratio (g/gda) | 0.0029 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | #N/A | #N/A | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28151 | 0.73193 | 0.73193 | 0.73193 | 0.73193 | 0.33781 | 0.39412 | #N/A | #N/A | 0.45042 | 0.45042
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5556 | 25.5556 | 12.2222 | 12.8333 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.7222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0124 | 0.0124 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.2735 | 0.71109 | 0.71109 | 0.71109 | 0.71109 | 0.32819 | 0.38289 | #N/A | #N/A | 0.43759 | 0.43759
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4444 | 24.4444 | 12.2778 | 12.8889 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | #N/A | #N/A | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27741 | 0.72126 | 0.72126 | 0.72126 | 0.72126 | 0.33289 | 0.38837 | #N/A | #N/A | 0.44385 | 0.44385
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7222 | 23.7222 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.012 | 0.012 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27538 | 0.716 | 0.716 | 0.716 | 0.716 | 0.33046 | 0.38554 | n/a* | n/a* | 0.44061 | 0.44061
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.32941 | 0.38431 | #N/A | #N/A | 0.43921 | 0.43921
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0053 | 0.0053
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.33309 | 0.3886 | #N/A | #N/A | 0.44412 | 0.44412
* =na()
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 10.8176 | 0 | 0 | 0 | 4.8015 | 4.5839 | 5.0147 | AE401 | Dry bulb temperature (°C) | -29 | -17.7778 | 7.2222 | 7.2222 | 7.2778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | #N/A | 40
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.4021 | 0 | 1.4021 | 34.2896 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | #N/A | #N/A | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.4587 | 5.9168 | 13.3755 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1138 | 0 | 4.1138 | 51.8548 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6801 | 4.4948 | 8.1749 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.11883 | 0.17824 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6423 | 5.1885 | 8.8308 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7778 | 16.7778 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 7.6667
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1701 | 0 | 4.1701 | 49.664 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | #N/A | #N/A | 0.0041 | 0.0041
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28597 | 0.33688 | 0.33688 | 0.33688 | 0.33688 | 0.13784 | 0.19904 | #N/A | #N/A | 0.050903 | 0.050903
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.7222 | 25.7222 | 12.4444 | 12.7778 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.5 | -0.72222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0135 | 0.0135 | 0.009 | 0.009 | 0.009 | 0.009 | #N/A | #N/A | 0.0101 | 0.0101
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27289 | 0.53541 | 0.53541 | 0.53541 | 0.53541 | 0.25542 | 0.27998 | #N/A | #N/A | 0.26252 | 0.26252
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.7222 | 24.7222 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.27778
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | #N/A | #N/A | 0.0059 | 0.0059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27761 | 0.33591 | 0.33591 | 0.33591 | 0.33591 | 0.13714 | 0.19877 | #N/A | #N/A | 0.058299 | 0.058299
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1667 | 23.1667 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.2778
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0147 | 0.0147 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0103 | 0.0103
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27474 | 0.32968 | 0.32968 | 0.32968 | 0.32968 | 0.13462 | 0.19506 | #N/A | #N/A | 0.054947 | 0.054947
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.4444
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0104 | 0.0104
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.13451 | 0.1949 | #N/A | #N/A | 0.054902 | 0.054902
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.44444
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0057 | 0.0057
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.13712 | 0.19874 | #N/A | #N/A | 0.05829 | 0.05829
* =na()

## Eplus
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | EnergyPlus 8.2.0 | [5 empty] | GARD Analytics
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | GARD
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | EnergyPlus
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-01-14 |  | Model / Organization Indentifier for Charts (short): |  |  |  | EnergyPlus/GARD
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | EnergyPlus
| Version: | 8.2.0
| Date: | 2015-01-14
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 |  | 0.5861 | 8.4534 | 0 | 0 | 0 | 6.5151 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4539 | 29.0494 | 29.0494 | 29.6355 | 21.1183 | 21.1183
| AE103 |  | 1.465 | 0.5861 | 0 | 0.76554 | 0 | 0.76554 | 32.5142 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887
| AE104 |  | 2.931 | 0.5861 | 0 | 3.4986 | 2.1742 | 5.6728 | 99.6158 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5207 | 33.309 | 33.309 | 33.8997 | 27.0344 | 27.0344
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.726 | 20.726 | 18.5095 | 19.0928 | 23.3293 | 23.3293
[16 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7063 | 31.7063 | 29.4615 | 30.0522 | 36.0616 | 36.0616
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8949 | 24.8949 | 14.9265 | 15.5032 | 23.8823 | 23.8823
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013079 | 0.013079 | 0.010558 | 0.010558 | 0.011233 | 0.011233
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.3316 | 58.3316 | 41.6971 | 42.2878 | 52.5907 | 52.5907
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | -2.931 |  | 0.5861 | 8.387 | 8.048e-08 | 1.8383e-05 | 1.8464e-05 | 6.5149 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6476 | 29.0498 | 29.0498 | 29.6359 | 21.1187 | 21.1187 | 21.4084
| AE203 |  | 1.465 | 0.5861 | 0 | 0.83269 | 0 | 0.83269 | 32.5148 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887 | 0.0022887
| AE204 |  | 2.931 | 0.5861 | 0 | 3.5657 | 2.1735 | 5.7392 | 99.6397 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE205 |  | 1.465 | 0.5861 | 0 | 1.9127 | 0 | 1.9127 | 44.111 | [6 empty] | Enthalpy (J/gda) | -28.5066 | 8.7159 | 33.3094 | 33.3094 | 33.9001 | 27.0348 | 27.0348 | 27.3272
| AE206 |  | 1.465 | 0.5861 | 0 | 1.6967 | 1.0417 | 2.7383 | 99.0255 | [6 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
| AE226 |  | 1.465 | 0.5861 | 0 | 1.5548 | 1.8634 | 3.4182 | 99.8073 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9201 | 20.9201 | 18.5093 | 19.0925 | 23.3288 | 23.3288 | 23.6201
| AE245 |  | 1.465 | 0.5861 | 0 | 2.2073 | 0 | 2.2073 | 33.9915 | [6 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.9029 | 31.9029 | 29.4612 | 30.0519 | 36.0611 | 36.0611 | 36.3565
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0862 | 25.0862 | 14.9264 | 15.5031 | 23.8822 | 23.8822 | 24.1702
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013081 | 0.013081 | 0.010561 | 0.010561 | 0.011236 | 0.011236 | 0.011236
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.5327 | 58.5327 | 41.7033 | 42.2941 | 52.5969 | 52.5969 | 52.8923
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0456 | 24.0456 | 18.5236 | 19.1052 | 23.3296 | 23.3296 | 23.62
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.005832 | 0.005832 | 0.005832 | 0.005832 | 0.0065075 | 0.0065075 | 0.0065075
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.0081 | 39.0081 | 33.3995 | 33.9902 | 39.9994 | 39.9994 | 40.2948
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4106 | 23.4106 | 18.5888 | 19.1626 | 23.33 | 23.33 | 23.6165
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014507 | 0.014507 | 0.013302 | 0.013302 | 0.013978 | 0.013978 | 0.013978
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 60.4363 | 60.4363 | 52.4066 | 52.9973 | 59.0066 | 59.0066 | 59.302
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5897 | 19.1634 | 23.33 | 23.33 | 23.6164
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.01341 | 0.01341 | 0.014086 | 0.014086 | 0.014086
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 52.6815 | 53.2723 | 59.2816 | 59.2816 | 59.5769
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5115 | 19.0946 | 23.3294 | 23.3294 | 23.6205
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0051565 | 0.0051565
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 29.962 | 30.5528 | 36.562 | 36.562 | 36.8573
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 3.5747 | 0 | 0 | 0 | 23.8906 | 7.5057 | 8.1309 | AE301 | Dry bulb temperature (°C) | -29 | 2.4185 | 7.22 | 7.22 | 7.8063 | 29.649 | 28.0886 | 21.1299 | 22.2485 | 21.6893 | 21.982
| AE303 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 6.4764 | 0 | 6.4764 | 47.4569 | 2.1827 | 2.3607 |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0021723 | 0.0023649 | 0.0022686 | 0.0022686
| AE304 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 10.1563 | 6.6217 | 16.778 | 99.1258 | 0.94208 | 1.4552 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE305 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.1994 | 0 | 9.1994 | 64.909 | 2.193 | 2.3739 |  | Enthalpy (J/gda) | -28.5066 | 6.1776 | 11.0156 | 11.0156 | 11.6064 | 33.6155 | 32.0433 | 26.7502 | 28.3684 | 27.5593 | 27.8547
| AE306 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.7437 | 5.7489 | 14.4926 | 99.2475 | 2.2136 | 2.4005 |  | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
| AE326 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.2481 | 12.5316 | 20.7797 | 99.9275 | 2.2141 | 2.4012 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8531 | 20.8531 | 12.197 | 12.7804 | 19.1013 | 18.6401 | 23.3385 | 24.4517 | 23.8952 | 24.1865
| AE345 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.5096 | 0 | 9.5096 | 50.9944 | 2.1849 | 2.3635 |  | Humidity ratio (g/gda) | 0.0029334 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0048436 | 0.0050359 | 0.0049397 | 0.0049397
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.5397 | 31.5397 | 22.7746 | 23.3653 | 29.7658 | 29.2989 | 35.775 | 37.3934 | 36.5842 | 36.8796
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5756 | 7.22 | 12.2012 | 12.7797 | 15.485 | 16.3615 | 23.8914 | 25.0047 | 24.4481 | 24.737
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012324 | 0.012324 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0094477 | 0.00964 | 0.0095439 | 0.0095439
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 57.1062 | 57.1062 | 34.3988 | 34.9895 | 37.752 | 38.6471 | 48.0548 | 49.6829 | 48.8688 | 49.1642
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4598 | 7.22 | 12.1989 | 12.7806 | 19.1133 | 18.6566 | 23.3385 | 24.4517 | 23.8952 | 24.1857
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0063912 | 0.0065835 | 0.0064873 | 0.0064873
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.1326 | 39.1326 | 26.6821 | 27.2729 | 33.7034 | 33.2397 | 39.7127 | 41.3343 | 40.5235 | 40.8188
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7256 | 7.22 | 12.2019 | 12.7804 | 19.1369 | 18.6889 | 23.3385 | 24.4517 | 23.8952 | 24.1841
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.011867 | 0.011867 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0094593 | 0.0096517 | 0.0095555 | 0.0095555
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 54.0424 | 54.0424 | 34.4281 | 35.0189 | 41.5099 | 41.0525 | 47.5192 | 49.1471 | 48.3331 | 48.6285
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 7.22 | 12.2017 | 12.7801 | 19.1373 | 18.6896 | 23.3385 | 24.4517 | 23.8952 | 24.184
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0095202 | 0.0097126 | 0.0096164 | 0.0096164
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 34.5816 | 35.1723 | 41.6648 | 41.2075 | 47.6741 | 49.3022 | 48.4881 | 48.7835
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 7.22 | 12.197 | 12.78 | 19.1037 | 18.6434 | 23.3385 | 24.4517 | 23.8952 | 24.1863
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0053488 | 0.0052527 | 0.0052527
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 23.5643 | 24.155 | 30.562 | 30.0957 | 36.5712 | 38.1903 | 37.3807 | 37.6761
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 10.343 | 0 | 0 | 0 | 4.1501 | 4.5034 | 4.9022 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.2031 | 7.2901 | 46.6969 | 35.8886 | 21.1452 | 22.2593 | 21.1452 | 21.1452
| AE403 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 1.3987 | 0 | 1.3987 | 35.8492 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022887 | 0.0022872 | 0.0022887 | 0.0022887
| AE404 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 7.3706 | 6.3173 | 13.6879 | 98.7059 | 0 | 0 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| AE405 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.0977 | 0 | 4.0977 | 52.7786 | 0 | 0 |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.8892 | 7.8892 | 7.9766 | 47.5931 | 36.7273 | 27.0614 | 28.1819 | 27.0614 | 27.0614
| AE406 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5834 | 4.84 | 8.4235 | 99.7649 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.11367 | 0.17051 | n/a* | n/a* | 0 | 0
| AE426 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5416 | 5.3897 | 8.9313 | 99.9528 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7888 | 7.22 | 12.6598 | 12.78 | 12.78 | 12.78 | 23.3441 | 24.4608 | 23.9508 | 23.9546
| AE445 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.1451 | 0 | 4.1451 | 49.4632 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029334 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.0049254 | 0.0049851 | 0.0049578 | 0.0049578
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 25.0767 | 25.0767 | 20.9029 | 21.0244 | 21.0244 | 21.0244 | 35.9889 | 37.2733 | 36.6866 | 36.6905
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.13676 | 0.19796 | n/a* | n/a* | 0.050546 | 0.050919
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7623 | 7.22 | 12.4725 | 12.7797 | 12.7808 | 12.7808 | 23.9001 | 25.0168 | 24.3846 | 24.4749
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013543 | 0.013543 | 0.0088944 | 0.0088944 | 0.0088944 | 0.0088944 | 0.009788 | 0.010124 | 0.0099335 | 0.0099335
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 60.4045 | 60.4045 | 34.9834 | 35.2972 | 35.2982 | 35.2982 | 48.93 | 50.9269 | 49.7961 | 49.8885
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.53845 | 0.53845 | 0.53845 | 0.53845 | 0.25766 | 0.28079 | n/a* | n/a* | 0.25427 | 0.25427
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.758 | 7.22 | 12.661 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9497 | 23.9534
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0064728 | 0.0065327 | 0.0065053 | 0.0065053
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 37.0618 | 37.0618 | 24.7987 | 24.9195 | 24.9195 | 24.9195 | 39.9261 | 41.2141 | 40.6246 | 40.6284
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.13638 | 0.19741 | n/a* | n/a* | 0.049606 | 0.049969
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1345 | 7.22 | 12.6637 | 12.78 | 12.7899 | 12.7899 | 23.3441 | 24.4607 | 23.9468 | 23.95
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014891 | 0.014891 | 0.0091064 | 0.0091064 | 0.0091018 | 0.0091018 | 0.010803 | 0.010863 | 0.010835 | 0.010835
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 61.1277 | 61.1277 | 35.7139 | 35.8327 | 35.8312 | 35.8312 | 50.9427 | 52.2412 | 51.6436 | 51.6468
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.13543 | 0.19602 | n/a* | n/a* | 0.047271 | 0.047271
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 7.22 | 12.6638 | 12.7801 | 12.79 | 12.79 | 23.3441 | 24.4607 | 23.9468 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0091238 | 0.0091238 | 0.009124 | 0.009124 | 0.010825 | 0.010885 | 0.010858 | 0.010858
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 35.758 | 35.8769 | 35.8875 | 35.8875 | 50.9995 | 52.2981 | 51.7004 | 51.7036
[16 empty] | Mass flow rate (kgda/s) | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.13543 | 0.19601 | n/a* | n/a* | 0.047261 | 0.047261
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 7.22 | 12.6608 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9499 | 23.9536
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0061691 | 0.006229 | 0.0062016 | 0.0062016
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 24.0343 | 24.1552 | 24.1552 | 24.1552 | 39.1535 | 40.4408 | 39.8519 | 39.8557
[16 empty] | Mass flow rate (kgda/s) | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.13645 | 0.19752 | n/a* | n/a* | 0.049791 | 0.050091
* n/a = not applicable
EnergyPlus 4-Pipe Fan Coil
| Last Hour of Simulation - Summary Outputs - Fan Coil Air System | [13 empty] | EnergyPlus 4-Pipe Fan Coil
|  | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AET101a | -2.931 | 0.5861 | 8.4527 | 0 | 0 | 0 | 29.9418 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4496 | 29.6291 | 5.0358 | 29.6291 | 21.1119 | 21.1119
| AET103a | 1.465 | 0.5861 | 0 | 0.76509 | 0 | 0.76509 | 31.3427 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022888 | 0.0022888
| AET104a | 2.931 | 0.5861 | 0 | 3.4965 | 2.1082 | 5.6047 | 98.0115 | [7 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5164 | 33.8933 | 9.1072 | 33.8933 | 27.0279 | 27.0279
| Notes: | [14 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
| 1) EnergyPlus 4-Pipe Fan Coil model only allows a blow-through configuration with the heating coil placed after the cooling coil | [13 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.7283 | 19.0965 | 19.0965 | 19.0965 | 23.3328 | 23.3328
| 2) Outdoor air and exhaust air interchange takes place automatically within the fan coil unit without the aid of an exhaust fan | [14 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049598 | 0.0049598
| and therefore the fan coil return air flow rate is always equal to the supply air flow rate | [14 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7087 | 30.0559 | 30.0559 | 30.0559 | 36.0651 | 36.0651
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8985 | 15.5126 | 15.5126 | 15.5126 | 23.8882 | 23.8882
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013235 | 0.010791 | 0.010791 | 0.010791 | 0.011466 | 0.011466
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.7307 | 42.8864 | 42.8864 | 42.8864 | 53.1892 | 53.1892
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
* n/a = not applicable

## IES-VE
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Integrated Environmental Solutions Virtual Environment IES-VE 2014.2 | [5 empty] | Integrated Environmental Solutions
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | IES
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | IES-VE
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-02-20 |  | Model / Organization Indentifier for Charts (short): |  |  |  | IES-VE/IES
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | IES-VE
| Version: | <VE>2014.2
| Date: | 2015-02-20
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.513 | 0 | 0 | 0 | 6.75 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4073 | 28.994 | 28.994 | 29.5758 | 21.111 | 21.111
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.762 | 0 | 0.762 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.00237 | 0.002374
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.48 | 2.127 | 5.607 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 |  | Aug 7, 2015: Zone air mass flows set to "NA" by JN
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7214 | 20.7214 | 18.5195 | 19.1013 | 23.3321 | 23.3321 |  | Matches most recent output template.
[16 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8934 | 24.8934 | 14.8437 | 15.4255 | 23.8901 | 23.8901
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013136 | 0.013136 | 0.010581 | 0.010581 | 0.011285 | 0.011285
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.446 | 0 | 0 | 0 | 6.75 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6011 | 28.9937 | 28.9937 | 29.5755 | 21.1107 | 21.1107 | 21.4016
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.83 | 0 | 0.83 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.002374 | 0.002374 | 0.002374
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.547 | 2.128 | 5.675 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.915 | 0 | 1.915 | 44.59 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.695 | 1 | 2.696 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.552 | 1.825 | 3.377 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9148 | 20.9148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
| AE245 | 0 | 1.564 | 0.5861 | 0 | 2.21 | 0 | 2.21 | 34.06 | [6 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0861 | 25.0861 | 14.8418 | 15.4236 | 23.8882 | 23.8882 | 24.1791
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013135 | 0.013135 | 0.01058 | 0.01058 | 0.011284 | 0.011284 | 0.011284
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0481 | 24.0481 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005916 | 0.005916 | 0.005916 | 0.005916 | 0.00662 | 0.00662 | 0.00662
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4148 | 23.4148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014624 | 0.014624 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005212 | 0.005212
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 3.647 | 0 | 0 | 0 | 24.65 | 7.539 | 8.17 | AE301 | Dry bulb temperature (°C) | -29 | 2.3582 | 7.22 | 7.22 | 7.8018 | 29.5754 | 28.026 | 21.1106 | 22.221 | 21.6658 | 21.9567
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.483 | 0 | 6.483 | 48.02 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.000262 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.002253 | 0.002454 | 0.002354 | 0.002354
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.034 | 6.629 | 16.662 | 100 | 0.915 | 1.419 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.195 | 0 | 9.195 | 65.57 | 2.188 | 2.366 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.652 | 5.75 | 14.403 | 100 | 2.188 | 2.366 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.096 | 12.558 | 20.654 | 100 | 2.188 | 2.366 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8401 | 20.8401 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.529 | 0 | 9.529 | 51.1 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.002947 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004938 | 0.005139 | 0.005039 | 0.005039
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5681 | 25.5681 | 12.199 | 12.7808 | 15.4247 | 16.2939 | 23.8893 | 25.001 | 24.4447 | 24.7356
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.012443 | 0.012443 | 0.008891 | 0.008891 | 0.008891 | 0.008891 | 0.009595 | 0.009796 | 0.009695 | 0.009695
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4554 | 24.4554 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.006499 | 0.0067 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7247 | 23.7247 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.011971 | 0.011971 | 0.008888 | 0.008888 | 0.008888 | 0.008888 | 0.009592 | 0.009793 | 0.009693 | 0.009693
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.008909 | 0.008909 | 0.008909 | 0.008909 | 0.009613 | 0.009814 | 0.009713 | 0.009713
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005413 | 0.005312 | 0.005312
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.451 | 0 | 0 | 0 | 4.17 | 4.524 | 4.926 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3103 | 46.5047 | 35.7662 | 21.1103 | 22.2208 | #N/A | #N/A
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.399 | 0 | 1.399 | 35.98 | 0 | 0 |  | Humidity ratio (g/gda) | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.002374 | 0.002374 | #N/A | #N/A
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.333 | 6.313 | 13.645 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.111 | 0 | 4.111 | 53.05 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.567 | 4.868 | 8.435 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | 0.11327 | 0.1699 | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.516 | 5.456 | 8.972 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7759 | 16.7759 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.16 | 0 | 4.16 | 49.58 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002947 | 0.003265 | 0.003265 | 0.00326 | 0.003265 | 0.003265 | 0.003265 | 0.005021 | 0.005084 | 0.005037 | 0.005055
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05055 | 0.05037
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.744 | 25.744 | 12.47 | 12.7846 | 12.7846 | 12.7846 | 23.8934 | 25.0043 | 24.3776 | 24.4762
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013639 | 0.013639 | 0.009056 | 0.009056 | 0.009056 | 0.009056 | 0.00998 | 0.010327 | 0.010131 | 0.010131
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54137 | 0.54137 | 0.54137 | 0.54137 | 0.25892 | 0.28245 | 0.25892 | 0.28245 | 0.25821 | 0.25821
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7562 | 24.7562 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004826 | 0.004826 | 0.00482 | 0.004826 | 0.004826 | 0.004826 | 0.006582 | 0.006645 | 0.006616 | 0.006616
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1432 | 23.1432 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4432 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014914 | 0.014914 | 0.009175 | 0.009175 | 0.009175 | 0.009175 | 0.010931 | 0.010994 | 0.010966 | 0.010966
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9481
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.009184 | 0.009184 | 0.009184 | 0.009184 | 0.01094 | 0.011003 | 0.010974 | 0.010974
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.006264 | 0.006327 | 0.006298 | 0.006298
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
* n/a = not applicable

## LCEM
Sec5-5out.XLS
Output spreadsheet for Airside Mechanical Equipment Diagnostic Tests: AE101-AE445
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | Life Cycle Energy Management Tool V3.10 | [5 empty] | Takasago Thermal Engineering, CO, JAPAN
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | MLIT-TTE
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | LCEM
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2015-04-16 |  | Model / Organization Indentifier for Charts (short): |  |  |  | LCEM/MLIT-TTE | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | LCEM
| Version: | 3.10
| Date: | 2015-04-16
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 | 0 | 0.5861 | 8.3722 | 0 | 0 | 0 | 6.8667 | [6 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3977 | 29.0359 | 29.0359 | 29.6249 | 21.111 | 21.111
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.75229 | 0.010332 | 0.76262 | 32.5498 | [7 empty] | Humidity ratio (g/gda) | 0.00034449 | 0.0016965 | 0.0016965 | 0.0016965 | 0.0016965 | 0.0023731 | 0.0023731
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.3892 | 2.2564 | 5.6456 | 100 | [7 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | -28.3305 | 8.6805 | 33.542 | 33.542 | 34.1363 | 27.2632 | 27.2631
[17 empty] | Mass flow rate (kgda/s) | 0.11333 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 |  | Aug 7, 2015: Zone air mass flows set to "NA" by JN
[16 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.722 | 20.722 | 18.5081 | 19.0971 | 23.333 | 23.333 |  | Matches most recent output template.
[17 empty] | Humidity ratio (g/gda) | 0.0029339 | 0.004285 | 0.004285 | 0.004285 | 0.004285 | 0.0049605 | 0.0049605
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 23.0129 | 31.7233 | 31.7233 | 29.479 | 30.0761 | 36.0881 | 36.0881
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[16 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8932 | 24.8932 | 14.9194 | 15.5084 | 23.889 | 23.889
[17 empty] | Humidity ratio (g/gda) | 0.016761 | 0.013095 | 0.013095 | 0.010585 | 0.010585 | 0.011261 | 0.011261
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 69.7952 | 58.3823 | 58.3823 | 41.768 | 42.3718 | 52.6808 | 52.6808
[17 empty] | Mass flow rate (kgda/s) | 0.11333 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3021 | 0 | 0 | 0 | 6.8714 | [6 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.604 | 29.0359 | 29.0359 | 29.6249 | 21.111 | 21.111 | 21.406
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.81912 | 0.01125 | 0.83037 | 32.5498 | [7 empty] | Humidity ratio (g/gda) | 0.00034449 | 0.0016977 | 0.0016977 | 0.0016977 | 0.0016977 | 0.0023743 | 0.0023743 | 0.0023743
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.4558 | 2.2575 | 5.7133 | 100 | [7 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.8799 | 0.031088 | 1.911 | 44.2027 | [7 empty] | Enthalpy (J/gda) | -28.3305 | 8.8916 | 33.5449 | 33.5449 | 34.1393 | 27.2661 | 27.2661 | 27.5642
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.6456 | 1.0532 | 2.6988 | 100 | [7 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5033 | 1.8877 | 3.3911 | 100 | [6 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.5081 | 19.0971 | 23.333 | 23.333 | 23.628
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.1715 | 0.030615 | 2.2021 | 34.0684 | [7 empty] | Humidity ratio (g/gda) | 0.0029339 | 0.004285 | 0.004285 | 0.004285 | 0.004285 | 0.0049605 | 0.0049605 | 0.0049605
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 23.0129 | 31.9227 | 31.9227 | 29.479 | 30.0761 | 36.0881 | 36.0881 | 36.3875
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0893 | 25.0893 | 14.9194 | 15.5084 | 23.889 | 23.889 | 24.184
[17 empty] | Humidity ratio (g/gda) | 0.016761 | 0.013094 | 0.013094 | 0.010585 | 0.010585 | 0.011261 | 0.011261 | 0.011261
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 69.7952 | 58.5815 | 58.5815 | 41.768 | 42.3718 | 52.6808 | 52.6808 | 52.9836
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.052 | 24.052 | 18.5198 | 19.1088 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.0044868 | 0.0058378 | 0.0058378 | 0.0058378 | 0.0058378 | 0.0065133 | 0.0065133 | 0.0065133
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 36.4725 | 39.05 | 39.05 | 33.4263 | 34.0251 | 40.0371 | 40.0371 | 40.3373
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4187 | 23.4187 | 18.5759 | 19.1649 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.015546 | 0.014574 | 0.014574 | 0.013413 | 0.013413 | 0.014089 | 0.014089 | 0.014089
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 62.6628 | 60.6255 | 60.6255 | 52.6832 | 53.29 | 59.302 | 59.302 | 59.6063
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5759 | 19.1649 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.015546 | 0.015546 | 0.015546 | 0.013413 | 0.013413 | 0.014089 | 0.014089 | 0.014089
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 62.6628 | 62.6628 | 62.6628 | 52.6832 | 53.29 | 59.302 | 59.302 | 59.6063
[17 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5096 | 19.0986 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.0044868 | 0.0044868 | 0.0044868 | 0.0044868 | 0.0044868 | 0.0051623 | 0.0051623 | 0.0051623
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 36.4725 | 36.4725 | 36.4725 | 29.992 | 30.5893 | 36.6013 | 36.6013 | 36.9008
[17 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | [14 empty] | AE301 | Dry bulb temperature (°C)
| AE303 | [15 empty] | Humidity ratio (g/gda)
| AE304 | [15 empty] | Specific volume (L/kgda)
| AE305 | [15 empty] | Enthalpy (J/gda)
| AE306 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE326 | [14 empty] | AE303 | Dry bulb temperature (°C)
| AE345 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE304 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE305 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE306 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE326 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE345 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | [14 empty] | AE401 | Dry bulb temperature (°C)
| AE403 | [15 empty] | Humidity ratio (g/gda)
| AE404 | [15 empty] | Specific volume (L/kgda)
| AE405 | [15 empty] | Enthalpy (J/gda)
| AE406 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE426 | [14 empty] | AE403 | Dry bulb temperature (°C)
| AE445 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE404 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE405 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE406 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE426 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE445 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable

## TRNSYS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | TRNSYS 17.01.0028 with TESS Libraries (and custom types) | [5 empty] | Thermal Energy System Specialists
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TESS
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | TRNSYS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-18 |  | Model / Organization Indentifier for Charts (short): |  |  |  | TRNSYS/TESS
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | TRNSYS with TESS Libraries
| Version: | 17.01.0028
| Date: | 2014-11-18
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.4159 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0054 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.78002 | 0 | 0.78002 | 32.8657 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.4932 | 2.0544 | 5.5475 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.163 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0312 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7694 | 20.7694 | 18.5094 | 19.0931 | 23.3325 | 23.3325
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 838.436 | 838.436 | 831.9891 | 829.5769 | 846.6643 | 846.6643
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8897 | 31.8897 | 29.598 | 30.1899 | 36.2163 | 36.2163
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8689 | 24.8689 | 14.9489 | 15.5247 | 23.8905 | 23.8905
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 861.9835 | 861.9835 | 830.0764 | 827.6673 | 856.7579 | 856.7579
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.2895 | 58.2895 | 41.874 | 42.4646 | 52.7745 | 52.7745
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3563 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1845 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138 | 21.3858
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.85249 | 0 | 0.85249 | 32.8591 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906 | 0.0022906
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.5705 | 2.0544 | 5.6249 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.6718 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855 | 835.563
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.9128 | 0 | 1.9128 | 44.5861 | [6 empty] | Enthalpy (J/gda) | -28.5404 | 8.2119 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593 | 27.3341
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.7033 | 0.96766 | 2.6709 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683 | 0.21683
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5603 | 1.7951 | 3.3553 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9827 | 20.9827 | 18.5127 | 19.0964 | 23.3358 | 23.3358 | 23.6483
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.209 | 0 | 2.209 | 34.1009 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0444 | 839.0444 | 831.9985 | 829.5862 | 846.6738 | 846.6738 | 845.3778
[16 empty] | Enthalpy (J/gda) | 23.0203 | 32.106 | 32.106 | 29.6013 | 30.1932 | 36.2197 | 36.2197 | 36.537
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887 | 0.22887
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.089 | 25.089 | 14.949 | 15.5247 | 23.8905 | 23.8905 | 24.2165
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.62 | 862.62 | 830.0765 | 827.6674 | 856.758 | 856.758 | 855.3891
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.5163 | 58.5163 | 41.8741 | 42.4647 | 52.7746 | 52.7746 | 53.1094
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097 | 0.23097
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0489 | 24.0489 | 18.5089 | 19.0924 | 23.3302 | 23.3302 | 23.6425
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0065687 | 0.0065687 | 0.0065687
[16 empty] | Specific volume (L/kgda) | 850.4379 | 849.9007 | 849.9007 | 834.0579 | 831.6391 | 848.7645 | 848.7645 | 847.465
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.1826 | 39.1826 | 33.5487 | 34.1421 | 40.1835 | 40.1835 | 40.5015
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33951 | #N/A | 0.2283 | 0.2283
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4334 | 23.4334 | 18.5234 | 19.1059 | 23.3365 | 23.3365 | 23.6483
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014551 | 0.014551 | 0.013376 | 0.013376 | 0.014065 | 0.014065 | 0.014065
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.8435 | 859.8435 | 844.0471 | 841.5963 | 858.9055 | 858.9055 | 857.5889
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.6005 | 60.6005 | 52.5481 | 53.1486 | 59.2623 | 59.2623 | 59.5841
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.3355 | 0.3355 | 0.3355 | 0.33549 | #N/A | 0.2256 | 0.2256
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.52 | 19.1025 | 23.3331 | 23.3331 | 23.6449
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013373 | 0.013373 | 0.014062 | 0.014062 | 0.014062
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 844.0335 | 841.5827 | 858.8916 | 858.8916 | 857.5751
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 52.5373 | 53.1378 | 59.2514 | 59.2514 | 59.5732
[16 empty] | Mass flow rate (kgda/s) | 0.3355 | 0.3355 | 0.3355 | 0.3355 | 0.3355 | #N/A | 0.2256 | 0.2256
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5 | 19.0837 | 23.3227 | 23.3227 | 23.6352
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.00517 | 0.00517 | 0.00517
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 832.1765 | 829.7636 | 846.8544 | 846.8544 | 845.558
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 29.9972 | 30.5893 | 36.617 | 36.617 | 36.9343
[16 empty] | Mass flow rate (kgda/s) | 0.34028 | 0.34028 | 0.34028 | 0.34028 | 0.34028 | #N/A | 0.22882 | 0.22882
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 2.9467 | 0 | 0 | 0 | 24.6351 | 7.7093 | 8.3843 | AE301 | Dry bulb temperature (°C) | -29 | 3.4295 | 7.22 | 7.22 | 7.7815 | 29.27 | 27.81 | 21.1102 | 22.2171 | 21.6678 | 22.0159
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.7255 | 0 | 6.7255 | 48.1783 | 2.2552 | 2.4545 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0021868 | 0.0023719 | 0.00228 | 0.00228
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.315 | 6.2615 | 16.5765 | 100 | 0.99153 | 1.5236 |  | Specific volume (L/kgda) | 691.9366 | 785.4602 | 796.2249 | 796.2249 | 793.9174 | 858.8449 | 854.6986 | 836.5361 | 839.9318 | 838.2465 | 836.8112
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.3734 | 0 | 9.3734 | 65.7465 | 2.2567 | 2.4562 |  | Enthalpy (J/gda) | -28.5404 | 7.3163 | 11.1404 | 11.1404 | 11.7069 | 33.386 | 31.913 | 26.7919 | 28.3805 | 27.592 | 27.9436
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.9149 | 5.4435 | 14.3584 | 100 | 2.2618 | 2.4621 |  | Mass flow rate (kgda/s) | 0.2814 | 0.77055 | 0.77055 | 0.77055 | 0.77055 | 0.35561 | 0.41494 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.4705 | 12.3053 | 20.7757 | 100 | 2.2668 | 2.4678 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.015 | 21.015 | 12.215 | 12.7861 | 19.18 | 18.75 | 23.3285 | 24.4389 | 23.8872 | 24.2266
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.7073 | 0 | 9.7073 | 51.1113 | 2.2607 | 2.461 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0048998 | 0.0050898 | 0.0049954 | 0.0049954
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0106 | 839.0106 | 813.9115 | 811.5517 | 833.7769 | 832.5505 | 846.506 | 849.9339 | 848.2307 | 846.8233
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.9 | 31.9 | 22.9778 | 23.5569 | 30.0395 | 29.6035 | 35.9355 | 37.5464 | 36.746 | 37.0906
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.34788 | 0.40592 | #N/A | #N/A | 0.47572 | 0.47572
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5714 | 25.5714 | 12.2114 | 12.7819 | 15.59 | 16.48 | 23.8806 | 25.0027 | 24.4454 | 24.7871
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.012255 | 0.012255 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0095252 | 0.0097162 | 0.0096213 | 0.0096213
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.9176 | 862.9176 | 819.9046 | 817.5256 | 829.612 | 832.1692 | 854.3402 | 857.8271 | 856.095 | 854.6649
[16 empty] | Enthalpy (J/gda) | 69.8514 | 56.9571 | 56.9571 | 34.6305 | 35.2138 | 38.085 | 38.995 | 48.2695 | 49.9048 | 49.0924 | 49.4423
[16 empty] | Mass flow rate (kgda/s) | 0.27553 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34534 | 0.40296 | #N/A | #N/A | 0.47277 | 0.47277
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4732 | 24.4732 | 12.2132 | 12.7841 | 19.18 | 18.75 | 23.3269 | 24.4367 | 23.8854 | 24.2247
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0064597 | 0.0066501 | 0.0065555 | 0.0065555
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.9864 | 850.9864 | 815.9317 | 813.5654 | 835.8517 | 834.6222 | 848.608 | 852.0428 | 850.3362 | 848.9249
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.3742 | 39.3742 | 26.9085 | 27.489 | 33.9922 | 33.555 | 39.9028 | 41.5175 | 40.7152 | 41.0606
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.75194 | 0.75194 | 0.75194 | 0.75194 | 0.34702 | 0.40492 | #N/A | #N/A | 0.47454 | 0.47454
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7738 | 23.7738 | 12.2138 | 12.7843 | 19.19 | 18.76 | 23.3339 | 24.4427 | 23.8919 | 24.2309
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.01181 | 0.01181 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0095248 | 0.0097161 | 0.0096211 | 0.0096211
[16 empty] | Specific volume (L/kgda) | 859.942 | 857.1235 | 857.1235 | 819.9131 | 817.5341 | 839.9574 | 838.7219 | 852.7674 | 856.2158 | 854.5024 | 853.0834
[16 empty] | Enthalpy (J/gda) | 62.7079 | 53.9762 | 53.9762 | 34.6363 | 35.2197 | 41.7693 | 41.3297 | 47.7088 | 49.3311 | 48.525 | 48.8722
[16 empty] | Mass flow rate (kgda/s) | 0.27604 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34533 | 0.40295 | #N/A | #N/A | 0.47224 | 0.47224
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2 | 12.7705 | 19.19 | 18.76 | 23.3337 | 24.4424 | 23.8916 | 24.2307
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0095166 | 0.009708 | 0.0096129 | 0.0096129
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 819.863 | 817.4842 | 839.9466 | 838.7111 | 852.7558 | 856.2039 | 854.4907 | 853.0715
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 34.6018 | 35.185 | 41.7487 | 41.3091 | 47.6878 | 49.31 | 48.504 | 48.8512
[16 empty] | Mass flow rate (kgda/s) | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.34536 | 0.40298 | #N/A | #N/A | 0.47229 | 0.47229
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2 | 12.7711 | 19.18 | 18.75 | 23.328 | 24.4382 | 23.8867 | 24.2261
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051553 | 0.0053453 | 0.0052509 | 0.0052509
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 814.2005 | 811.8397 | 834.1168 | 832.8898 | 846.8497 | 850.2785 | 848.5748 | 847.1665
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 23.6068 | 24.186 | 30.687 | 30.2508 | 36.5851 | 38.1965 | 37.3958 | 37.7406
[16 empty] | Mass flow rate (kgda/s) | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.34776 | 0.40578 | #N/A | #N/A | 0.47557 | 0.47557
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.2578 | 0 | 0 | 0 | 4.1464 | 4.4895 | 4.8689 | AE401 | Dry bulb temperature (°C) | -29 | -28.9976 | 7.22 | 7.22 | 7.2949 | 46.8281 | 35.9884 | 21.1151 | 22.2211 | 21.1151 | 21.1151
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.4476 | 0 | 1.4476 | 36.3722 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025899 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00026343 | 0.00025893 | 0.0022691 | 0.0022892 | 0.0022691 | 0.0022691
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.3862 | 5.9214 | 13.3076 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9366 | 691.9435 | 794.5864 | 794.5864 | 794.2783 | 906.845 | 876.1179 | 836.6603 | 839.8318 | 836.6603 | 836.6603
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.091 | 0 | 4.091 | 53.4325 | 0 | 0 |  | Enthalpy (J/gda) | -28.5404 | -28.5378 | 7.9144 | 7.9144 | 7.9897 | 47.7909 | 36.8692 | 27.006 | 28.1742 | 27.006 | 27.006
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.6296 | 4.5892 | 8.2187 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.11282 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.5849 | 5.2196 | 8.8045 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9405 | 16.9405 | 12.6692 | 12.7822 | 12.7822 | 12.7822 | 23.3302 | 24.4386 | 23.9452 | 23.95
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.1448 | 0 | 4.1448 | 49.5567 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032912 | 0.0032912 | 0.0032904 | 0.0032889 | 0.0032889 | 0.0032889 | 0.0049882 | 0.0050489 | 0.0050219 | 0.0050219
[16 empty] | Specific volume (L/kgda) | 821.5721 | 826.1416 | 826.1416 | 813.9765 | 813.5066 | 814.2962 | 814.2962 | 846.6302 | 849.8778 | 848.4319 | 848.4118
[16 empty] | Enthalpy (J/gda) | 23.0203 | 25.3772 | 25.3772 | 21.0521 | 21.1625 | 21.1625 | 21.1625 | 36.1621 | 37.442 | 36.8722 | 36.8771
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13681 | 0.19814 | #N/A | #N/A | 0.056872 | 0.056872
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.721 | 25.721 | 12.491 | 12.7811 | 12.7878 | 12.7878 | 23.8829 | 24.9989 | 24.3678 | 24.474
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013494 | 0.013494 | 0.009021 | 0.009017 | 0.009021 | 0.009021 | 0.0099213 | 0.010261 | 0.010067 | 0.010067
[16 empty] | Specific volume (L/kgda) | 872.9312 | 865.0361 | 865.0361 | 820.9246 | 819.6593 | 821.7776 | 821.7776 | 854.883 | 858.5556 | 856.4754 | 856.0296
[16 empty] | Enthalpy (J/gda) | 69.8514 | 60.2687 | 60.2687 | 35.3369 | 35.6235 | 35.6405 | 35.6405 | 49.2802 | 51.2876 | 50.1471 | 50.256
[16 empty] | Mass flow rate (kgda/s) | 0.27532 | 0.53883 | 0.53883 | 0.53883 | 0.53882 | 0.25786 | 0.28097 | #N/A | #N/A | 0.2635 | 0.2635
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7397 | 24.7397 | 12.6697 | 12.7825 | 12.7825 | 12.7825 | 23.3319 | 24.4401 | 23.9467 | 23.9515
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.0065372 | 0.006598 | 0.0065709 | 0.0065709
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4473 | 850.4473 | 815.9886 | 815.5201 | 816.3107 | 816.3107 | 848.7271 | 851.9817 | 850.5325 | 850.5124
[16 empty] | Enthalpy (J/gda) | 36.4891 | 37.2029 | 37.2029 | 24.9519 | 25.0664 | 25.0664 | 25.0664 | 40.1052 | 41.3882 | 40.8169 | 40.8218
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.13639 | 0.19754 | #N/A | #N/A | 0.056539 | 0.056539
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1572 | 23.1606 | 12.6584 | 12.7709 | 12.7709 | 12.7709 | 23.318 | 24.431 | 23.9345 | 23.9393
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014766 | 0.014801 | 0.0091221 | 0.0091221 | 0.0091221 | 0.0091221 | 0.010838 | 0.0109 | 0.010873 | 0.010873
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.3332 | 859.3905 | 821.5375 | 821.0663 | 821.8609 | 821.8609 | 854.4955 | 857.7874 | 856.3189 | 856.2989
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.8624 | 60.9557 | 35.7636 | 35.8787 | 35.8787 | 35.8787 | 51.0348 | 52.3348 | 51.7549 | 51.7598
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.13538 | 0.19599 | #N/A | #N/A | 0.055858 | 0.055858
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.67 | 12.7822 | 12.7822 | 12.7822 | 23.3286 | 24.4416 | 23.9452 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0091292 | 0.0091292 | 0.0091292 | 0.0091292 | 0.010844 | 0.010906 | 0.010879 | 0.010879
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 821.58 | 821.1102 | 821.9025 | 821.9025 | 854.534 | 857.8259 | 856.3576 | 856.3375
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 35.7933 | 35.908 | 35.908 | 35.908 | 51.0608 | 52.3607 | 51.7809 | 51.7858
[16 empty] | Mass flow rate (kgda/s) | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.13536 | 0.19597 | #N/A | #N/A | 0.055831 | 0.055831
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.67 | 12.7825 | 12.7825 | 12.7825 | 23.3321 | 24.442 | 23.9476 | 23.9524
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061921 | 0.006253 | 0.0062259 | 0.0062259
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 815.5415 | 815.0746 | 815.8626 | 815.8626 | 848.2614 | 851.5195 | 850.0683 | 850.0482
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 24.0835 | 24.1977 | 24.1977 | 24.1977 | 39.2271 | 40.5117 | 39.9395 | 39.9444
[16 empty] | Mass flow rate (kgda/s) | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.13647 | 0.19764 | #N/A | #N/A | 0.056569 | 0.056569
* n/a = not applicable

## blank
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Blank
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short):
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | Blank
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: | [5 empty] | Model / Organization Indentifier for Charts (short): | Blank
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
Software:
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling |  |  | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet |  |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH |  |  |  |  | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) |  |  |  |  | Air | Air | Outlet | Outlet | Air | Ar
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) |  |  | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1)
| AE101 | 2.93 | [9 empty] | AE101 | Dry bulb temperature (°C)
| AE103 | [11 empty] | Humidity ratio (g/gda)
| AE104 | [11 empty] | Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE103 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE104 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling |  |  | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet |  |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH |  |  |  |  | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) |  |  |  |  | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) |  |  | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 | [9 empty] | AE201 | Dry bulb temperature (°C)
| AE203 | [11 empty] | Humidity ratio (g/gda)
| AE204 | [11 empty] | Specific volume (L/kgda)
| AE205 | [11 empty] | Enthalpy (J/gda)
| AE206 | [11 empty] | Mass flow rate (kgda/s)
| AE226 | [10 empty] | AE203 | Dry bulb temperature (°C)
| AE245 | [11 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE204 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE205 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE206 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE226 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE245 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)