## A
Sec5-3Aout.XLS
Output spreadsheet for HVAC BESTEST Cases CE100 through CE200
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1507.4667 |  | 141.5649 |  | 3770.3648 | 3770.3648 | -3.6077e-14 | 3628.7999 | 3628.7999 | 0 | 2.4072 | 22.2023 | 0.0075726 | 2.4089 | 22.2023 | 0.0075726 | 2.4037 | 22.2023 | 0.0075726
CE110 | 1049.6476 |  | 123.3037 |  | 3752.1036 | 3752.1036 | -1.819e-15 | 3628.7999 | 3628.7999 | 0 | 3.4572 | 22.2 | 0.0064893 | 3.4572 | 22.2 | 0.0064893 | 3.4572 | 22.2 | 0.0064893
CE120 | 1003.8994 |  | 115.5855 |  | 3744.3854 | 3744.3854 | -7.0031e-14 | 3628.7999 | 3628.7999 | 0 | 3.6147 | 26.6667 | 0.0081221 | 3.6172 | 26.6667 | 0.0081221 | 3.6094 | 26.6667 | 0.0081221
CE130 | 94.8215 |  | 8.8991 |  | 190.3391 | 190.3391 | 4.5475e-16 | 181.44 | 181.44 | 0 | 1.9135 | 22.2 | 0.0076199 | 1.9155 | 22.2 | 0.0076199 | 1.9097 | 22.2 | 0.0076199
CE140 | 64.0044 |  | 7.5187 |  | 189.1009 | 189.1009 | 3.5053e-16 | 181.5822 | 181.5822 | 0 | 2.837 | 22.2 | 0.0065389 | 2.837 | 22.2 | 0.0065389 | 2.837 | 22.2 | 0.0065389
CE150 | 1193.5837 |  | 138.8032 |  | 4501.3861 | 3761.8134 | 739.5727 | 4369.0008 | 3629.6739 | 739.3269 | 3.6604 | 22.2012 | 0.0085399 | 3.6643 | 22.2013 | 0.0085585 | 3.6564 | 22.2012 | 0.0084677
CE160 | 1128.7968 |  | 127.2403 |  | 4489.1363 | 3749.56 | 739.5763 | 4369.0008 | 3629.6739 | 739.3269 | 3.8705 | 26.6685 | 0.010394 | 3.8748 | 26.6685 | 0.01042 | 3.8662 | 26.6685 | 0.010306
CE165 | 1482.0808 |  | 146.8965 |  | 4509.9409 | 3770.3722 | 739.5687 | 4369.0008 | 3629.6739 | 739.3269 | 2.9479 | 23.3339 | 0.0095622 | 2.9515 | 23.334 | 0.0095826 | 2.9448 | 23.3339 | 0.00948
CE170 | 630.6815 |  | 71.981 |  | 2217.2175 | 1477.6153 | 739.6022 | 2150.6261 | 1411.2991 | 739.3269 | 3.41 | 22.2 | 0.010792 | 3.414 | 22.2 | 0.01081 | 3.4057 | 22.2 | 0.010709
CE180 | 1080.3239 |  | 118.4387 |  | 4475.474 | 1516.764 | 2958.71 | 4369.0008 | 1411.2991 | 2957.7017 | 4.0442 | 22.2 | 0.016571 | 4.0488 | 22.2 | 0.016582 | 4.0416 | 22.2 | 0.016454
CE185 | 1531.8823 |  | 138.2981 |  | 4497.4185 | 1538.7424 | 2958.6762 | 4369.0008 | 1411.2991 | 2957.7017 | 2.852 | 22.2 | 0.016501 | 2.8563 | 22.2002 | 0.016513 | 2.8493 | 22.2 | 0.016379
CE190 | 161.7076 |  | 17.7284 |  | 567.2514 | 197.5027 | 369.7488 | 551.04 | 181.44 | 369.6 | 3.4076 | 22.2 | 0.01644 | 3.4096 | 22.2 | 0.016452 | 3.4076 | 22.2 | 0.016327
CE195 | 237.0209 |  | 21.3982 |  | 571.393 | 201.5813 | 369.8117 | 551.2456 | 181.5822 | 369.6635 | 2.3257 | 22.2 | 0.016383 | 2.3274 | 22.2 | 0.016394 | 2.3254 | 22.2 | 0.016261
CE200 | 1461.1346 |  | 151.9823 |  | 5476.5805 | 4255.1364 | 1221.4441 | 5335.207 | 4114.1555 | 1221.0514 | 3.6514 | 26.6669 | 0.011596 | 3.6559 | 26.6669 | 0.011621 | 3.6479 | 26.6668 | 0.011499