## A
Sec5-5out.xlsx
Output Spreadsheet for Standard 140 Airside HVAC Equipment Performance Analytical Verification Cases AE101 through AE445
© Carrier 2023. All rights reserved.
INSTRUCTIONS
1. Use specified units.
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | Carrier HAP
| Version: | 6.0.0.888
| Date: | 2022-11-29
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 | 0 | 0.5861 | 8.452 | 0 | 0 | 0 | 29.95 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4489 | 29.6284 | 5.0343 | 29.6284 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.5861 | 0 | 0.76511 | 0 | 0.76511 | 31.346 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0022891 | 0.0022891
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.48 | 2.2377 | 5.7177 | 94.51 | [6 empty] | Specific volume (L/kgda) | 692.0128 | 788.5312 | 860.0545 | 790.194 | 860.0545 | 836.7683 | 836.7683
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5163 | 33.8932 | 9.1063 | 33.8932 | 27.028 | 27.028
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7287 | 19.0955 | 19.0955 | 19.0955 | 23.3333 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0049602 | 0.0049602
[16 empty] | Specific volume (L/kgda) | 821.6589 | 838.3516 | 833.6932 | 833.6932 | 833.6932 | 846.6945 | 846.6945
[16 empty] | Enthalpy (J/gda) | 22.9959 | 31.7097 | 30.0557 | 30.0557 | 30.0557 | 36.0667 | 36.0667
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.9003 | 15.5085 | 15.5085 | 15.5085 | 23.8902 | 23.8902
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012972 | 0.010397 | 0.010397 | 0.010397 | 0.011072 | 0.011072
[16 empty] | Specific volume (L/kgda) | 873.0237 | 862.0467 | 831.4964 | 831.4964 | 831.4964 | 856.5545 | 856.5545
[16 empty] | Enthalpy (J/gda) | 69.814 | 58.063 | 41.8848 | 41.8848 | 41.8848 | 52.188 | 52.188
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3818 | 0 | 0 | 0 | 30.7878 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.639 | 29.0288 | 4.639 | 29.614 | 21.0967 | 21.0967 | 21.3955
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.82766 | 9.0949e-16 | 0.82766 | 32.4016 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0016124 | 0.0022891 | 0.0022891 | 0.0022891
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5482 | 2.273 | 5.8212 | 96.8838 | [6 empty] | Specific volume (L/kgda) | 692.013 | 789.0711 | 858.3515 | 789.0711 | 860.0137 | 836.727 | 836.727 | 837.5768
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9122 | 2.2737e-16 | 1.9122 | 44.0703 | [6 empty] | Enthalpy (J/gda) | -28.5066 | 8.7079 | 33.2889 | 8.7079 | 33.8787 | 27.0136 | 27.0136 | 27.3151
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.6935 | 1.5535 | 3.247 | 86.2264 | [6 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5406 | 2.3442 | 3.8848 | 95.7023 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9621 | 18.5655 | 18.5655 | 19.1478 | 23.3856 | 23.3856 | 23.683
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2048 | 4.5475e-16 | 2.2048 | 33.9774 | [6 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0042846 | 0.0049602 | 0.0049602 | 0.0049602
[16 empty] | Specific volume (L/kgda) | 821.6592 | 839.0176 | 832.1808 | 832.1808 | 833.8419 | 846.8437 | 846.8437 | 847.693
[16 empty] | Enthalpy (J/gda) | 22.9959 | 31.946 | 29.5187 | 29.5187 | 30.1085 | 36.1195 | 36.1195 | 36.421
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.1021 | 14.9397 | 14.9397 | 15.5154 | 23.899 | 23.899 | 24.1937
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012889 | 0.010273 | 0.010273 | 0.010273 | 0.010948 | 0.010948 | 0.010948
[16 empty] | Specific volume (L/kgda) | 873.0237 | 862.518 | 829.6955 | 829.6955 | 831.3537 | 856.412 | 856.412 | 857.2616
[16 empty] | Enthalpy (J/gda) | 69.814 | 58.0604 | 40.9888 | 40.9888 | 41.5784 | 51.8815 | 51.8815 | 52.1836
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0602 | 18.5389 | 18.5389 | 19.1196 | 23.3454 | 23.3454 | 23.6419
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0058322 | 0.0058322 | 0.0058322 | 0.0058322 | 0.0065078 | 0.0065078 | 0.0065078
[16 empty] | Specific volume (L/kgda) | 850.518 | 849.9509 | 834.1613 | 834.1613 | 835.8218 | 848.819 | 848.819 | 849.668
[16 empty] | Enthalpy (J/gda) | 36.4347 | 39.0236 | 33.4157 | 33.4157 | 34.0055 | 40.0165 | 40.0165 | 40.3181
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4198 | 18.5807 | 18.5807 | 19.1553 | 23.3374 | 23.3374 | 23.6309
[16 empty] | Humidity ratio (g/gda) | 0.015566 | 0.013336 | 0.011545 | 0.011545 | 0.011545 | 0.012221 | 0.012221 | 0.012221
[16 empty] | Specific volume (L/kgda) | 860.0491 | 858.2558 | 841.8723 | 841.8723 | 843.5306 | 856.5118 | 856.5118 | 857.3596
[16 empty] | Enthalpy (J/gda) | 62.7052 | 57.4654 | 47.9431 | 47.9431 | 48.5328 | 54.5439 | 54.5439 | 54.8455
[16 empty] | Mass flow rate (kgda/s) | 0.11366 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 18.6083 | 18.6083 | 19.1816 | 23.3538 | 23.3538 | 23.6465
[16 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.012863 | 0.012863 | 0.012863 | 0.013538 | 0.013538 | 0.013538
[16 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 843.7033 | 843.7033 | 845.3611 | 858.3386 | 858.3386 | 859.1862
[16 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 51.3124 | 51.3124 | 51.9022 | 57.9133 | 57.9133 | 58.2148
[16 empty] | Mass flow rate (kgda/s) | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 18.5181 | 18.5181 | 19.1002 | 23.3365 | 23.3365 | 23.6338
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051566 | 0.0051566 | 0.0051566
[16 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 832.3066 | 832.3066 | 833.9676 | 846.9687 | 846.9687 | 847.818
[16 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 29.9688 | 29.9688 | 30.5586 | 36.5696 | 36.5696 | 36.8711
[16 empty] | Mass flow rate (kgda/s) | 0.34099 | 0.34099 | 0.34099 | 0.34099 | 0.34099 | n/a* | 0.22733 | 0.22733
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 3.5822 | 0 | 0 | 0 | 23.8892 | 7.501 | 8.1235 | AE301 | Dry bulb temperature (°C) | -29 | 2.4103 | 7.2222 | 7.2222 | 7.8075 | 29.6391 | 28.0732 | 21.1199 | 22.2336 | 21.6769 | 21.9691
| AE303 | 0 | 1.4654 | 0 | 0 | 2.3446 | 0 | 0 | 6.4549 | 0 | 6.4549 | 33.4715 | 2.171 | 2.3444 |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0014958 | 0.0021725 | 0.0023652 | 0.0022689 | 0.0022689
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.0831 | 6.9711 | 17.0541 | 94.7543 | 0.93938 | 1.451 |  | Specific volume (L/kgda) | 692.013 | 782.5942 | 796.2601 | 796.2601 | 797.9222 | 859.9241 | 855.477 | 836.6368 | 840.0622 | 838.3495 | 839.1805
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.1982 | 0 | 9.1982 | 64.9185 | 2.1923 | 2.3735 |  | Enthalpy (J/gda) | -28.5066 | 6.1697 | 11.0183 | 11.0183 | 11.608 | 33.6059 | 32.0281 | 26.7408 | 28.3541 | 27.5475 | 27.8423
| AE306 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 0 | 8.6909 | 6.0483 | 14.7392 | 95.3924 | 6.603 | 7.0813 |  | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
| AE326 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 0 | 8.1485 | 12.6386 | 20.7871 | 99.8848 | 6.6056 | 7.0847 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.842 | 20.842 | 12.1941 | 12.7778 | 19.0797 | 18.6109 | 23.3333 | 24.4444 | 23.8889 | 24.1808
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.5096 | -3.638e-15 | 9.5096 | 50.9986 | 2.1841 | 2.3628 |  | Humidity ratio (g/gda) | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334
[16 empty] | Specific volume (L/kgda) | 821.6592 | 836.8655 | 836.8655 | 812.2486 | 813.9103 | 831.8491 | 830.5147 | 843.9573 | 847.1201 | 845.5387 | 846.3695
[16 empty] | Enthalpy (J/gda) | 22.9959 | 28.3928 | 28.3928 | 19.6559 | 20.2456 | 26.6124 | 26.1388 | 30.9098 | 32.0324 | 31.4711 | 31.766
[16 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5745 | 25.5745 | 12.1999 | 12.7778 | 15.4775 | 16.3522 | 23.89 | 25.002 | 24.4461 | 24.7346
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012082 | 0.012082 | 0.0083798 | 0.0083798 | 0.0083798 | 0.0083798 | 0.0090551 | 0.0092474 | 0.0091512 | 0.0091512
[16 empty] | Specific volume (L/kgda) | 873.0237 | 862.786 | 862.786 | 819.3443 | 821.0038 | 828.7558 | 831.2673 | 853.8247 | 857.2823 | 855.5535 | 856.3831
[16 empty] | Enthalpy (J/gda) | 69.814 | 56.4896 | 56.4896 | 33.4063 | 33.996 | 36.7509 | 37.6434 | 47.054 | 48.6799 | 47.8669 | 48.1618
[16 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4574 | 24.4574 | 12.197 | 12.7778 | 19.1092 | 18.6531 | 23.3359 | 24.4477 | 23.8919 | 24.1819
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0057159 | 0.0063915 | 0.0065838 | 0.0064876 | 0.0064876
[16 empty] | Specific volume (L/kgda) | 850.518 | 850.9291 | 850.9291 | 815.8737 | 817.5342 | 835.6372 | 834.3332 | 848.6347 | 852.0779 | 850.3563 | 851.1864
[16 empty] | Enthalpy (J/gda) | 36.4347 | 39.1307 | 39.1307 | 26.6807 | 27.2704 | 33.6997 | 33.2366 | 39.7108 | 41.3309 | 40.5209 | 40.8157
[16 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7267 | 23.7267 | 12.1999 | 12.7778 | 31.7525 | 30.2201 | 23.341 | 24.4542 | 23.8977 | 24.1862
[16 empty] | Humidity ratio (g/gda) | 0.015566 | 0.011654 | 0.011654 | 0.008437 | 0.008437 | 0.008437 | 0.008437 | 0.0091126 | 0.0093049 | 0.0092088 | 0.0092088
[16 empty] | Specific volume (L/kgda) | 860.0491 | 856.8696 | 856.8696 | 819.4189 | 821.0783 | 875.5668 | 871.1661 | 852.3243 | 855.7852 | 854.0548 | 854.8844
[16 empty] | Enthalpy (J/gda) | 62.7052 | 53.5007 | 53.5007 | 33.5507 | 34.1405 | 53.5047 | 51.9408 | 46.6394 | 48.2666 | 47.453 | 47.7479
[16 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2005 | 12.778 | 31.7464 | 30.2159 | 23.341 | 24.4542 | 23.8977 | 24.186
[16 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.015566 | 0.0088403 | 0.0088403 | 0.0088403 | 0.0088403 | 0.0095159 | 0.0097083 | 0.0096121 | 0.0096121
[16 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 860.0491 | 819.9449 | 821.6042 | 876.1092 | 871.7114 | 852.869 | 856.3319 | 854.6005 | 855.43
[16 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 62.7052 | 34.5692 | 35.159 | 54.5309 | 52.9678 | 47.6656 | 49.2936 | 48.4796 | 48.7745
[16 empty] | Mass flow rate (kgda/s) | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.1957 | 12.7778 | 19.0996 | 18.64 | 23.3359 | 24.4477 | 23.8919 | 24.1825
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051566 | 0.005349 | 0.0052528 | 0.0052528
[16 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 850.518 | 814.2649 | 815.9259 | 833.966 | 832.6545 | 846.967 | 850.4039 | 848.6855 | 849.5159
[16 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 36.4347 | 23.5631 | 24.1529 | 30.558 | 30.0923 | 36.569 | 38.1866 | 37.3778 | 37.6726
[16 empty] | Mass flow rate (kgda/s) | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.73881 | 0.34099 | 0.39782 | n/a* | n/a* | 0.45465 | 0.45465
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.3476 | 0 | 0 | 0 | 4.1447 | 4.5018 | 4.8988 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.2849 | 46.6818 | 35.8658 | 21.1299 | 22.2381 | 22.2381 | 22.4393
| AE403 | 0 | 1.4654 | 0 | 0 | 2.3446 | 0 | 0 | 1.4098 | 7.5791e-17 | 1.4098 | 32.3951 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022891 | 0.0022874 | 0.0022874 | 0.0022874
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.2943 | 6.48 | 13.7744 | 96.7661 | 0 | 0 |  | Specific volume (L/kgda) | 692.013 | 692.013 | 794.6804 | 794.6804 | 794.858 | 906.5239 | 875.8672 | 836.8215 | 839.9704 | 839.9704 | 840.5426
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.0987 | -3.0316e-16 | 4.0987 | 52.6788 | 0 | 0 |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.9084 | 7.9084 | 7.9714 | 47.578 | 36.7044 | 27.047 | 28.1611 | 28.1611 | 28.3641
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.5461 | 4.8931 | 8.4392 | 99.3471 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28416 | 0.28416 | 0.28416 | 0.28416 | 0.28416 | 0.11366 | 0.17049 | n/a* | n/a* | 1.9429e-16 | 1.9429e-16
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.4927 | 5.4244 | 8.9171 | 99.8844 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.8403 | 16.8403 | 12.6915 | 12.7778 | 12.7781 | 12.7781 | 23.3333 | 24.4444 | 23.9387 | 24.1396
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1393 | -6.0633e-16 | 4.1393 | 49.3605 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334 | 0.0029334
[16 empty] | Specific volume (L/kgda) | 821.6592 | 825.4746 | 825.4746 | 813.6646 | 813.9103 | 813.9113 | 813.9113 | 843.9573 | 847.1201 | 845.6804 | 846.2525
[16 empty] | Enthalpy (J/gda) | 22.9959 | 24.35 | 24.35 | 20.1584 | 20.2456 | 20.246 | 20.246 | 30.9098 | 32.0324 | 31.5214 | 31.7244
[16 empty] | Mass flow rate (kgda/s) | 0.28416 | 0.33634 | 0.33634 | 0.33634 | 0.33634 | 0.13741 | 0.19892 | n/a* | n/a* | 0.052179 | 0.052179
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.8033 | 25.8033 | 12.5624 | 12.7778 | 12.7846 | 12.7846 | 23.8864 | 24.9961 | 24.3686 | 24.567
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013482 | 0.013482 | 0.0087695 | 0.0087695 | 0.0087824 | 0.0087824 | 0.0096746 | 0.010009 | 0.0098198 | 0.0098198
[16 empty] | Specific volume (L/kgda) | 873.0237 | 865.3527 | 865.3527 | 820.8926 | 821.5114 | 821.5477 | 821.5477 | 854.6527 | 858.2997 | 856.2368 | 856.8079
[16 empty] | Enthalpy (J/gda) | 69.814 | 60.2922 | 60.2922 | 34.7601 | 34.98 | 35.0193 | 35.0193 | 48.6272 | 50.6138 | 49.4901 | 49.6931
[16 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.53949 | 0.53949 | 0.53949 | 0.53949 | 0.25809 | 0.2814 | n/a* | n/a* | 0.25533 | 0.25533
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7845 | 24.7845 | 12.6927 | 12.7778 | 12.7778 | 12.7778 | 23.3304 | 24.4403 | 23.9329 | 24.1326
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0047847 | 0.0064717 | 0.0065313 | 0.0065041 | 0.0065041
[16 empty] | Specific volume (L/kgda) | 850.518 | 850.6004 | 850.6004 | 816.0786 | 816.3214 | 816.3214 | 816.3214 | 848.7275 | 851.9855 | 850.496 | 851.0677
[16 empty] | Enthalpy (J/gda) | 36.4347 | 37.091 | 37.091 | 24.8332 | 24.9194 | 24.9194 | 24.9194 | 39.9093 | 41.1898 | 40.6044 | 40.8075
[16 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.33437 | 0.33437 | 0.33437 | 0.33437 | 0.13656 | 0.19768 | n/a* | n/a* | 0.050079 | 0.050216
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1602 | 23.1602 | 12.6947 | 12.7778 | 12.7783 | 12.7783 | 23.3304 | 24.4403 | 23.9299 | 24.128
[16 empty] | Humidity ratio (g/gda) | 0.015566 | 0.014886 | 0.014886 | 0.0090865 | 0.0090865 | 0.0090851 | 0.0090851 | 0.010785 | 0.010845 | 0.010818 | 0.010818
[16 empty] | Specific volume (L/kgda) | 860.0491 | 859.5975 | 859.5975 | 821.6856 | 821.9243 | 821.9239 | 821.9239 | 854.553 | 857.8335 | 856.325 | 856.896
[16 empty] | Enthalpy (J/gda) | 62.7052 | 61.1428 | 61.1428 | 35.6955 | 35.7803 | 35.7772 | 35.7772 | 50.8845 | 52.1751 | 51.5817 | 51.7847
[16 empty] | Mass flow rate (kgda/s) | 0.28419 | 0.33164 | 0.33164 | 0.33164 | 0.33164 | 0.1355 | 0.19614 | n/a* | n/a* | 0.047479 | 0.047479
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6949 | 12.778 | 12.778 | 12.778 | 23.3304 | 24.4403 | 23.9299 | 24.1313
[16 empty] | Humidity ratio (g/gda) | 0.015566 | 0.015566 | 0.015566 | 0.0091365 | 0.0091365 | 0.0091365 | 0.0091365 | 0.010837 | 0.010897 | 0.010869 | 0.010869
[16 empty] | Specific volume (L/kgda) | 860.0491 | 860.0491 | 860.0491 | 821.7513 | 821.99 | 821.99 | 821.99 | 854.6228 | 857.9035 | 856.3948 | 856.9754
[16 empty] | Enthalpy (J/gda) | 62.7052 | 62.7052 | 62.7052 | 35.8219 | 35.9068 | 35.9068 | 35.9068 | 51.0159 | 52.3067 | 51.7131 | 51.9196
[16 empty] | Mass flow rate (kgda/s) | 0.3317 | 0.3317 | 0.3317 | 0.3317 | 0.3317 | 0.13548 | 0.19612 | n/a* | n/a* | 0.04744 | 0.047539
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6925 | 12.7778 | 12.7862 | 12.7862 | 23.3304 | 24.4403 | 23.9333 | 24.133
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0061658 | 0.0062255 | 0.0061982 | 0.0061982
[16 empty] | Specific volume (L/kgda) | 850.518 | 850.518 | 850.518 | 815.6827 | 815.9259 | 815.95 | 815.95 | 848.3143 | 851.5708 | 850.083 | 850.6546
[16 empty] | Enthalpy (J/gda) | 36.4347 | 36.4347 | 36.4347 | 24.0665 | 24.1529 | 24.1614 | 24.1614 | 39.131 | 40.411 | 39.8262 | 40.0292
[16 empty] | Mass flow rate (kgda/s) | 0.33468 | 0.33468 | 0.33468 | 0.33468 | 0.33468 | 0.13674 | 0.19793 | n/a* | n/a* | 0.050519 | 0.050519
* n/a = not applicable
Note on J61: Wu, Tiejun: Cooling coil is upstream of heating coil