## Intro
Carrier Corporation (“Carrier”) has developed this ASHRAE St.d 170 Spreadsheet; hereinafter referred to as “Std. 170 Spreadsheet” or “Spreadsheet”.
In consideration of Carrier furnishing the reader of this text (“User”) with a copy of the Std. 170 Spreadsheet, it is agreed between them as follows:
It is recognized that the Spreadsheet is not intended to produce highly precise or certifiable results or to handle all of the factors involved in complex or sophisticated building installations.
NO WARRANTIES, EITHER EXPRESS OR IMPLIED, ARE GIVEN BY CARRIER AND CARRIER EXPRESSLY DISCLAIMS ANY IMPLIED WARRANTIES OR MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE OF THIS SPREADSHEET OR THE MATERIALS FURNISHED HEREUNDER.
In no event shall Carrier be liable to User, its customers or any other persons for any special, incidental or consequential damages of any kind arising out of the use of the Spreadsheet or the furnishing to User of any materials related thereto.
User will indemnify, defend and hold Carrier harmless from and against any claims, losses and damages arising on account of the use of the Spreadsheet or its results by User, User's customer and any other person who may use the Spreadsheet or any such materials.
© Carrier Corporation 2018

## 2017 Std 170 Calculator
ASHRAE Standard 170-2017 Minimum Airflow Calculator for HAP | [9 empty] | REV 1 | © Carrier Corporation 2018
Instructions:
This spreadsheet calculates the required Minimum Outdoor Air CFM/sqft input for HAP using ASHRAE Standard 170-2017, Table 7-1 ACH values, which is required for HAP to analyze Healthcare Facilities
Yellow cells are input cells | Blue cells are auto look-up values from Table 7-1 |  |  | Green cells are resulting calculation values to be input into HAP as OA1
When entering ventilation air in the HAP space input, change units to CFM/sqft and enter values in green cells as OA1 only. Leave the OA2 input field blank (as shown in Fig 2 on right)
In HAP system input, under Zone Components tab under Supply Terminals, enter Minimum Supply Airflow ACH rate as indicated in Column "I" (as shown in Fig 1 on right)
Space Designation | System | Zone Terminal | Space Floor Area (sqft) | Floor to Ceiling Height (ft) | Function of Space | Pressurization Relationship to Adjacent Areas | Minimum Outdoor Air ACH | Minimum Supply Air ACH (Enter into HAP as Min Airflow ACH) | All Room Air Exhausted Directly to Outdoors? | Mininum Outdoor Air in CFM/sqft (Enter into HAP as OA1)*
OR-1 | AHU-1 | Zone 1-1 | 2000 | 10 | Critical and intensive care | NR | 2 | 6 | NR | 0.33333
Toilet Room 1 | AHU-2 | Zone 2-1 | 50 | 9 | Toilet room | Negative | NR | 10 | Yes | #VALUE!
Patient Room 100 | AHU-2 | Zone 2-2 | 150 | 9 | Patient room | NR | 2 | 4 | NR (y) | 0.3
X-ray 1A | AHU-2 | Zone 2-3 | 180 | 10 | X-ray (diagnostic and treatment) | NR | 2 | 6 | NR | 0.33333
Newborn Nursery | AHU-2 | Zone 2-3 | 500 | 10 | Newborn nursery suite | NR | 2 | 6 | NR | 0.33333
|  |  | 1000 | 10 | Operating/surgical cystoscopic rooms (m), (o) | Positive | 4 | 20 | NR | 0.66667
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  | NOTES:
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | * if Min OA is NR (#VALUE!) Space Requires No Ventilation Air.
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | In this case enter 0 CFM/ft2 for ventilation in HAP
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | If cell indicates "#N/A" in Blue fields this because no data has
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | been entered yet in Yellow input cells
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | To add additional rows for additional spaces simply right-click on number
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | column on far left side then select "Insert"
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
Comments:

## 2013 Std 170 Calculator
ASHRAE Standard 170-2013 Minimum Airflow Calculator for HAP | [9 empty] | REV 1 | © Carrier Corporation 2018
Instructions:
This spreadsheet calculates the required Minimum Outdoor Air CFM/sqft input for HAP using ASHRAE Standard 170-2013, Table 7-1 ACH values, which is required for HAP to analyze Healthcare Facilities
Yellow cells are input cells | Blue cells are auto look-up values from Table 7-1 |  |  | Green cells are resulting calculation values to be input into HAP as OA1
When entering ventilation air in the HAP space input, change units to CFM/sqft and enter values in green cells as OA1 only. Leave the OA2 input field blank (as shown in Fig 2 on right)
In HAP system input, under Zone Components tab under Supply Terminals, enter Minimum Supply Airflow ACH rate as indicated in Column "I" (as shown in Fig 1 on right)
Space Designation | System | Zone Terminal | Space Floor Area (sqft) | Floor to Ceiling Height (ft) | Function of Space | Pressurization Relationship to Adjacent Areas | Minimum Outdoor Air ACH | Minimum Supply Air ACH (Enter into HAP as Min Airflow ACH) | All Room Air Exhausted Directly to Outdoors? | Mininum Outdoor Air in CFM/sqft (Enter into HAP as OA1)*
OR-1 | AHU-1 | Zone 1-1 | 2000 | 10 | Operating room (Class B and C) | Positive | 4 | 20 | NR | 0.66667
Toilet Room 1 | AHU-2 | Zone 2-1 | 50 | 9 | Toilet room | Negative | NR | 10 | Yes | #VALUE!
Patient Room 100 | AHU-2 | Zone 2-2 | 150 | 9 | Patient room | NR | 2 | 4 | NR | 0.3
X-ray 1A | AHU-2 | Zone 2-3 | 180 | 10 | X-ray (diagnostic and treatment) | NR | 2 | 6 | NR | 0.33333
Newborn Nursery | AHU-2 | Zone 2-4 | 500 | 10 | Newborn nursery suite | NR | 2 | 6 | NR | 0.33333
Delivery Room | AHU-2 | Zone 2-5 | 750 | 12 | Critical and intensive care | NR | 2 | 6 | NR | 0.4
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  | NOTES:
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | * if Min OA is NR (#VALUE!) Space Requires No Ventilation Air.
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | In this case enter 0 CFM/ft2 for ventilation in HAP
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | If cell indicates "#N/A" in Blue fields this because no data has
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | been entered yet in Yellow input cells
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | To add additional rows for additional spaces simply right-click on number
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | column on far left side then select "Insert"
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
Comments:

## 2017 Std 170 - Table 7-1
2017 | ASHRAE Standard 170 - Table 7-1 |  |  |  |  | © Carrier Corporation 2018
| Function of Space | Pressure Relationship to Adjacent Areas | Minimum Outdoor Air ACH | Minimum Total Air ACH | All Room Air Exhausted Directly to Outdoors?
SURGERY & CRITICAL CARE
| Critical and intensive care | NR | 2 | 6 | NR
| Delivery room (Caesarian) (m), (o) | Positive | 4 | 20 | NR
| Emergency department contamination | Negative | 2 | 12 | Yes
| Emergency department exam/treatment room (p) | NR | 2 | 6 | NR
| Emergency department public waiting area | Negative | 2 | 12 | Yes (q)
| Intermediate care (s) | NR | 2 | 6 | NR
| Laser eye room | Positive | 3 | 15 | NR
| Medical/anesthesia gas storage ( r) | Negative | NR | 8 | Yes
| Newborn intensive care | Positive | 2 | 6 | NR
| Operating Room (m), (o) | Positive | 4 | 20 | NR
| Operating/surgical cystoscopic rooms (m), (o) | Positive | 4 | 20 | NR
| Procedure room (o), (d) | Positive | 3 | 15 | NR
| Radiology waiting rooms | Negative | 2 | 12 | Yes (q), (w)
| Recovery room | NR | 2 | 6 | NR
| Substerile service area | NR | 2 | 6 | NR
| Trauma room (crisis or shock) ( c) | Positive | 3 | 15 | NR
| Treatment room (p) | NR | 2 | 6 | NR
| Triage | Negative | 2 | 12 | Yes (q)
| Wound intensive care (burn unit) | NR | 2 | 6 | NR
INPATIENT NURSING
| All anteroom (u) | (e) | NR | 10 | Yes
| AII room (u) | Negative | 2 | 12 | Yes
| Combination AII/PE anteroom | (e) | NR | 10 | Yes
| Combination AII/PE room | Positive | 2 | 12 | Yes
| Continued care nursery | NR | 2 | 6 | NR
| Labor/delivery/recovery (LDR) (s) | NR | 2 | 6 | NR
| Labor/delivery/recovery/postpartum (LDRP) (s) | NR | 2 | 6 | NR
| Newborn nursery suite | NR | 2 | 6 | NR
| Nourishment area or room | NR | NR | 2 | NR
| Patient corridor | NR | NR | 2 | NR
| Patient room | NR | 2 | 4 | NR (y)
| PE anteroom (t) | (e) | NR | 10 | NR
| Protective environment room (t) | Positive | 2 | 12 | NR
| Toilet room | Negative | NR | 10 | Yes
NURSING FACILITY
| Bathing room | Negative | NR | 10 | Yes
| Occupational therapy | NR | 2 | 6 | NR
| Physical therapy | Negative | 2 | 6 | NR
| Resident gathering/activity/dining | NR | 4 | 4 | NR
| Resident room | NR | 2 | 2 | NR
| Resident unit corridor | NR | NR | 4 | NR
RADIOLOGY (v)
| Darkroom (g) | Negative | 2 | 10 | Yes
| X-ray (diagnostic and treatment) | NR | 2 | 6 | NR
| X-ray (surgery/critical care and catheterization) | Positive | 3 | 15 | NR
DIAGNOSTIC AND TREATMENT
| Autopsy room (n) | Negative | 2 | 12 | Yes
| Bronchoscopy, sputum collection, and pentamidine adminsitration | Negative | 2 | 12 | Yes
| Dialysis treatment area | NR | 2 | 6 | NR
| Dialyzer reprocessing room | Negative | NR | 10 | Yes
| ECT procedure room | NR | 2 | 4 | NR
| Endoscope cleaning | Negative | 2 | 10 | Yes
| Gastrointestinal endoscopy procedure room | NR | 2 | 6 | NR
| General examination room | NR | 2 | 4 | NR
| Hydrotherapy | Negative | 2 | 6 | NR
| Laboratory work area, bacteriology (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, biochemistry (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, cytology (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, general (f), (v) | Negative | 2 | 6 | NR
| Laboratory work area, glasswashing (f) | Negative | 2 | 10 | Yes
| Laboratory work area, histology (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, media transfer (f), (v) | Positive | 2 | 4 | NR
| Laboratory work area, microbiology (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, nuclear medicine (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, pathology (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, serology (f), (v) | Negative | 2 | 6 | Yes
| Laboratory work area, sterilizing (f) | Negative | 2 | 10 | Yes
| Medication room | NR | 2 | 4 | NR
| Nonrefrigerated body-holding room (h) | Negative | NR | 10 | Yes
| Nuclear medicine hot lab | Negative | NR | 6 | Yes
| Nuclear medicine treatment room | Negative | 2 | 6 | Yes
| Pharmacy (b) | Positive | 2 | 4 | NR
| Physical therapy | Negative | 2 | 6 | NR
| Special examination room (aa) | N/R | 2 | 6 | NR
| Treament room | N/R | 2 | 6 | NR
STERILIZING
| Sterilizer equipment room | Negative | NR | 10 | Yes
STERILE PROCESSING DEPARTMENT z
| Clean workroom | Positive | 2 | 4 | NR
| Decontamination room | Negative | 2 | 6 | Yes
| Sterile storage room | Positive | 2 | 4 | NR
SERVICE
| Bathroom | Negative | NR | 10 | Yes
| Bedpan room | Negative | NR | 10 | Yes
| Clean linen storage | Positive | NR | 2 | NR
| Dietary storage | NR | NR | 2 | NR
| Food preparation center (i) | NR | 2 | 10 | NR
| Janitor's closet | Negative | NR | 10 | Yes
| Laundry, general | Negative | 2 | 10 | Yes
| Linen and trash chute room | Negative | NR | 10 | Yes
| Soiled linen sorting and storage | Negative | NR | 10 | Yes
| Warewashing | Negative | NR | 10 | Yes
SUPPORT SPACE
| Clean workroom or clean holding | Positive | 2 | 4 | NR
| Hazardous material storage | Negative | 2 | 10 | Yes
| Soiled workroom or soiled holding | Negative | 2 | 10 | Yes
NOTES: | NR = No Requirement
See Std-170 for footnotes

## 2013 Std 170 - Table 7-1
2013 | ASHRAE Standard 170 - Table 7-1 |  |  |  |  | © Carrier Corporation 2018
| Function of Space | Pressure Relationship to Adjacent Areas | Minimum Outdoor Air ACH | Minimum Total Air ACH | All Room Air Exhausted Directly to Outdoors?
SURGERY & CRITICAL CARE
| Operating room (Class B and C) | Positive | 4 | 20 | NR
| Operating/surgical systoscopic rooms | Positive | 4 | 20 | NR
| Delivery room (Caesarean) | Positive | 4 | 20 | NR
| Substerile service area | NR | 2 | 6 | NR
| Recovery room | NR | 2 | 6 | NR
| Critical and intensive care | NR | 2 | 6 | NR
| Intermeditate care | NR | 2 | 6 | NR
| Would intensive care (burn unit) | NR | 2 | 6 | NR
| Newborn intensive care | Positive | 2 | 6 | NR
| Treatment room | NR | 2 | 6 | NR
| Trauma room (crisis or shock) | Positive | 3 | 15 | NR
| Medical/anestesia gas storage | Negative | NR | 8 | Yes
| Laser eye room | Positive | 3 | 15 | NR
| ER waiting rooms | Negative | 2 | 12 | Yes
| Triage | Negative | 2 | 12 | Yes
| ER decontamination | Negative | 2 | 12 | Yes
| Radiology waiting rooms | Negative | 2 | 12 | Yes
| Procedure room (Class A surgery) | Positive | 3 | 15 | NR
| Emergency department exam/treatment room | NR | 2 | 6 | NR
INPATIENT NURSING
| Patient room | NR | 2 | 4 | NR
| Nourishment area or room | NR | NR | 2 | NR
| Toilet room | Negative | NR | 10 | Yes
| Newborn nursery suite | NR | 2 | 6 | NR
| Protective environment room | Positive | 2 | 12 | NR
| All room | Negative | 2 | 12 | Yes
| Combination AII / PE room | Positive | 2 | 12 | Yes
| All anteroom | Positive | NR | 10 | Yes
| PE anteroom | Positive | NR | 10 | NR
| Combination AII / PE anteroom | Positive | NR | 10 | Yes
| Labor/delivery/recovery/postpartum (LDRP) | NR | 2 | 6 | NR
| Labor/delivery/recovery (LDR) | NR | 2 | 6 | NR
| Patient Corridor | NR | NR | 2 | NR
SKILLED NURSING FACILITY
| Resident room | NR | 2 | 2 | NR
| Resident gathering/activity/dining | NR | 4 | 4 | NR
| Resident unit corridor | NR | NR | 4 | NR
| Physical therapy | Negative | 2 | 6 | NR
| Occupational therapy | NR | 2 | 6 | NR
| Bathing room | Negative | NR | 10 | Yes
RADIOLOGY (v)
| X-ray (diagnostic and treatment) | NR | 2 | 6 | NR
| X-ray (surgery/critical care and catheterization) | Positive | 3 | 15 | NR
| Darkroom | Negative | 2 | 10 | Yes
DIAGNOSTIC AND TREATMENT
| Bronchosopy, sputum collection, and pentamindine administration | Negative | 2 | 12 | Yes
| Laboratory, general | Negative | 2 | 6 | NR
| Laboratory, bacteriology | Negative | 2 | 6 | Yes
| Laboratory, biochemsitry | Negative | 2 | 6 | Yes
| Laboratory, cytology | Negative | 2 | 6 | Yes
| Laboratory, glasswashing | Negative | 2 | 10 | Yes
| Laboratory, histology | Negative | 2 | 6 | Yes
| Laboratory, microbiology | Negative | 2 | 6 | Yes
| Laboratory, nuclear medicine | Negative | 2 | 6 | Yes
| Laboratory, pathology | Negative | 2 | 6 | Yes
| Laboratory, serology | Negative | 2 | 6 | Yes
| Laboratory, sterilizing | Negative | 2 | 10 | Yes
| Laboratory, media transfer | Positive | 2 | 4 | NR
| Nonrefrigerated body-holding room | Negative | NR | 10 | Yes
| Autopsy room | Negative | 2 | 12 | Yes
| Pharmacy | Positive | 2 | 4 | NR
| Examination room | NR | 2 | 6 | NR
| Medication room | NR | 2 | 4 | NR
| Gastrointestinal endoscopy procedure room | NR | 2 | 6 | NR
| Endoscope cleaning | Negative | 2 | 10 | Yes
| Treatment room | NR | 2 | 6 | NR
| Hydrotherapy | Negative | 2 | 6 | NR
| Physical therapy | Negative | 2 | 6 | NR
STERILIZING
| Sterilizer equipment room | Negative | NR | 10 | Yes
CENTRAL MEDICAL AND SURGICAL SUPPLY
| Soiled or decontamination room | Negative | 2 | 6 | Yes
| Clean workroom | Positive | 2 | 4 | NR
| Sterile storage | Positive | 2 | 4 | NR
SERVICE
| Food preparation center | NR | 2 | 10 | NR
| Warewashing | Negative | NR | 10 | Yes
| Dietary storage | NR | NR | 2 | NR
| Laundry, general | Negative | 2 | 10 | Yes
| Soiled linen sorting and storage | Negative | NR | 10 | Yes
| Clean linen storage | Positive | NR | 2 | NR
| Linen and trash chute room | Negative | NR | 10 | Yes
| Bedpan room | Negative | NR | 10 | Yes
| Bathroom | Negative | NR | 10 | Yes
| Janitor's closet | Negative | NR | 10 | Yes
SUPPORT SPACE
| Soiled workroom or soiled holding | Negative | 2 | 10 | Yes
| Clean workroom or clean holding | Positive | 2 | 4 | NR
| Hazardous material storage | Negative | 2 | 10 | Yes
NOTES: | NR = No Requirement
See Std-170 for footnotes