## A
Sec5-3Aout.XLS
Output spreadsheet for HVAC BESTEST Cases CE100 through CE200
© Carrier 2023. All rights reserved.
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1507.4668 |  | 141.5649 |  | 3770.3649 | 3770.3649 | -4.3959e-14 | 3628.7999 | 3628.7999 | 0 | 2.4072 | 22.2023 | 0.0075726 | 2.4089 | 22.2023 | 0.0075726 | 2.4037 | 22.2023 | 0.0075726
CE110 | 1049.6476 |  | 123.3037 |  | 3752.1036 | 3752.1036 | 5.5631e-14 | 3628.7999 | 3628.7999 | 0 | 3.4572 | 22.2058 | 0.0064893 | 3.4572 | 22.2058 | 0.0064893 | 3.4572 | 22.2058 | 0.0064893
CE120 | 1003.8574 |  | 115.5789 |  | 3744.3788 | 3744.3788 | 4.6991e-15 | 3628.7999 | 3628.7999 | 0 | 3.6149 | 26.6722 | 0.0081221 | 3.6174 | 26.6723 | 0.0081221 | 3.6096 | 26.6722 | 0.0081221
CE130 | 94.8879 |  | 8.9053 |  | 190.4874 | 190.4874 | 1.8758e-15 | 181.5822 | 181.5822 | 0 | 1.9136 | 22.2047 | 0.0076207 | 1.9157 | 22.2049 | 0.0076207 | 1.9098 | 22.2027 | 0.0076207
CE140 | 64.0044 |  | 7.5187 |  | 189.1009 | 189.1009 | -1.9611e-15 | 181.5822 | 181.5822 | 0 | 2.837 | 22.2048 | 0.0065399 | 2.8371 | 22.205 | 0.0065399 | 2.837 | 22.2027 | 0.0065399
CE150 | 1193.6639 |  | 138.8171 |  | 4501.4008 | 3761.8281 | 739.5727 | 4369.0008 | 3629.6738 | 739.3269 | 3.6602 | 22.1961 | 0.0085379 | 3.0474 | 22.1962 | 0.0085566 | 3.0347 | 22.196 | 0.0084657
CE160 | 1128.8781 |  | 127.2545 |  | 4489.1514 | 3749.5751 | 739.5763 | 4369.0008 | 3629.6738 | 739.3269 | 3.8702 | 26.6626 | 0.010392 | 3.2229 | 26.6627 | 0.010417 | 3.2082 | 26.6625 | 0.010303
CE165 | 1482.1668 |  | 146.9095 |  | 4509.9546 | 3770.3859 | 739.5687 | 4369.0008 | 3629.6738 | 739.3269 | 2.9477 | 23.3293 | 0.0095602 | 2.455 | 23.3294 | 0.0095805 | 2.443 | 23.3292 | 0.009478
CE170 | 630.6992 |  | 71.9842 |  | 2217.2209 | 1477.6187 | 739.6022 | 2150.6261 | 1411.2991 | 739.3269 | 3.4099 | 22.1981 | 0.010792 | 2.2456 | 22.1982 | 0.010809 | 2.2302 | 22.1981 | 0.010709
CE180 | 1080.3239 |  | 118.4387 |  | 4475.4738 | 1516.7638 | 2958.71 | 4369.0008 | 1411.2991 | 2957.7017 | 4.0442 | 22.1921 | 0.016565 | 1.3116 | 22.1922 | 0.016576 | 1.3009 | 22.1921 | 0.016448
CE185 | 1531.8823 |  | 138.2981 |  | 4497.4184 | 1538.7422 | 2958.6762 | 4369.0008 | 1411.2991 | 2957.7017 | 2.852 | 22.1933 | 0.016496 | 0.92543 | 22.1934 | 0.016507 | 0.91693 | 22.1933 | 0.016373
CE190 | 161.7662 |  | 17.7349 |  | 567.4626 | 197.6503 | 369.8122 | 551.2456 | 181.5822 | 369.6635 | 3.4077 | 22.1996 | 0.016437 | 1.1342 | 22.1997 | 0.016448 | 1.1101 | 22.1995 | 0.016323
CE195 | 237.0209 |  | 21.3982 |  | 571.393 | 201.5813 | 369.8117 | 551.2456 | 181.5822 | 369.6635 | 2.3257 | 22.2006 | 0.016383 | 0.77563 | 22.2006 | 0.016395 | 0.75616 | 22.2006 | 0.016261
CE200 | 1461.2629 |  | 152.005 |  | 5476.6051 | 4255.1611 | 1221.4441 | 5335.207 | 4114.1555 | 1221.0514 | 3.6511 | 26.6587 | 0.011592 | 2.8224 | 26.6588 | 0.011617 | 2.8089 | 26.6586 | 0.011495