HVAC Guide Specifications
Carrier Model Number:
35BF-R High Induction Swirl Diffuser

35BF-R-FR Fire Rated Swirl Diffuser
Part 1 ― General

1.01 SYSTEM DESCRIPTION:
High induction swirl diffuser for use in pressurized access floor distribution system.
1.02 QUALITY ASSURANCE:
A.
Unit shall be tested in accordance with ANSI/ ASHRAE Standard 70-1991 at both isothermal and various conditions.
B.
Fire-rated swirl diffuser shall be available and shall meet NFPA-90A.
1.03 DELIVERY AND STORAGE:
Units shall be stored and handled per manufacturer’s recommendations.
Part 2 ― Products
2.01 EQUIPMENT:
The diffuser shall be constructed of high impact polymeric. The diffuser shall have a removable curved slot helical throw diffuser core. The diffuser core design shall produce a vertical, high induction helical air pattern. A high induction swirl air pattern is acceptable. The trim ring shall have a 1-in. flange for use with carpeting. The dust receptacle shall have an integral flow regulator and shall extend 53/4 in. below top of access floor panel. The diffuser shall have an external open/close indicator and internal open/close stop to allow visual determination of damper position. The flow regulator shall be manually operated without removing the diffuser core. The diffuser shall have a positive compression quick mount ring for installation into access floor panel. The access floor diffuser shall be assembled such that the access floor panel is not removed from the floor system for installation of the diffuser.

The diffuser core and trim ring finish shall be gray. The dust receptacle, flow regulator, and quick mount ring finish shall be black.






