
System Fan Coil Unit

HVAC Guide Specifications

Size Range: 600 to 4000 Nominal Cfm
Carrier Model Numbers: 

 42BHE (Horizontal Fan Coil Unit)

 42BVE (Vertical Fan Coil Unit)

· General

· SYSTEM DESCRIPTION

Horizontal and vertical, 2-pipe or 4-pipe, belt-driven, galvanized casing model fan coil unit for ducted installation above the ceiling or within floor-mounted cabinet, with full access to internal components.

· QUALITY ASSURANCE

· Unit shall be constructed in accordance with ETL and ETL, Canada standards. Units comply with the minimum requirements of the US and Canadian national product safety standard, UL 60335-2-40/CSA C22.2 No. 236. Factory-installed motors and electric heaters shall be UL approved. Insulation and adhesive shall meet NFPA-90A requirements for flame spread and smoke generation.

· Coils shall be tested in accordance with AHRI standard 410, latest edition. Each coil shall be factory tested for leakage at 300-psig air pressure with coil submerged in water. 

· DELIVERY, STORAGE AND HANDLING

Unit shall be handled and stored in accordance with the manufacturer’s instructions.

· Products

· EQUIPMENT

· General:

Factory-assembled, horizontal and vertical, draw-thru type fan coil unit for ducted installation above the ceiling or floor mounting. Unit shall be complete with water coils, fan(s), motor, belt drive, drain pan, and filter.

· Casing:

Construction shall be heavy-gage galvanized steel, lined with one-in. thick fiberglass Tuf-Skin™
 II thermal/acoustical insulation. Knockouts shall be provided for hanging the horizontal unit, that will accept 3/8-in. threaded rod at the top and bottom of all unit corners. Supply and return duct connections shall be 1 in. long. Removable side panels shall be provided for access to the fan/motor assembly. Access panels shall be easily removable with hex key tool on vertical unit, and without tools on horizontal unit. A double-sloped drain pan shall be constructed of stainless steel, extending under the full length and width of the coil(s) with a 3/4-in. male nominal pipe thread stainless steel drain connection and 1/2-in. male NPT stainless secondary drain connection (cap when not required). The outside surface of the drain pan shall be insulated with 1/8-in. closed cell insulation. Drain pan is removable from cabinet from same end as coil connections for ease of cleaning.

· Fans:

Belt-driven, double-width fan wheels shall have forward-curved blades and be statically and dynamically balanced. Fan drive shall consist of variable-pitch motor pulley, fixed-diameter blower sheave with keyed shaft, and V-belt. Fan drive shall be designed for 120% of rated fan horsepower. Fans and scrolls shall be of galvanized steel. Bearings are ball bearings, permanently lubricated and sealed for life. Bearings are isolated from the blower housing by rubber mounts set into heavy gage metal support system. The blower housing shall be isolated from the cabinet and motor.

· Coils:

Standard unit shall be equipped with a 4-row coil for installation in a 2-pipe system and additional rows of coil shall be provided as an option for installation in a 4-pipe system. Coils shall have 1/2-in. copper tubes, aluminum fins bonded to the tubes by mechanical expansion and have a working pressure of 250 psig at 200°F. Each coil shall have a manual air vent and sweat connections for copper tubes.

· Operating Characteristics:

A single-circuit coil unit installed in a 2-pipe system shall be capable of providing heating or cooling as determined by the operating mode of the central water supply system. A double-circuit coil unit installed in a 4-pipe system shall be capable of providing sequenced heating and cooling.

· Motor(s):

1. Fan motors shall be open, drip-proof, single-speed, single or 3 phase, suitable for continuous duty at 104°F (40°C). Single-phase motors are capacitor start, include automatic reset thermal overload protection and are available in 115, 208, 230, or 277 volts (60 Hz) or 220 volts (50 Hz). Three-phase motors are available in 208, 230, or 460 volts (60 Hz) or 380 volts (50 Hz). 

2. Motors are Class B, continuous duty rated. Motors are resilient mounted (1/4 to 2 hp), rigid base mounted (3 and 5 hp), NEMA frame motors. Motors are factory wired to unit junction or control box. Motor bearings are permanently lubricated. Motors are mounted on an adjustable base for belt tensioning and alignment. The motor and drive are installed on the same end as the coil connection for ease of service.

· Special Features:

1. Coils:

a. Unit coil(s) shall be equipped with automatic air vent(s).

b. Unit shall be equipped with a high-capacity 6-row or 8-row coil for installation in a 2-pipe system. 

c. For installation in a 4-pipe system, unit shall be equipped with either a 4-row cooling/ 1-row hot water heating split-circuit coil, or a 4/2, 6/1, or 6/2 split-circuit coil as required.

d. Unit shall be equipped with either a 4-row DX (direct expansion) cooling coil or a 6-row DX cooling coil as required.

e. Unit coil(s) shall be copper fin, copper tube with stainless steel end sheets and baffles.

2. Filters:

a. A two-in. pleated filter shall be installed in the unit (standard).

b. One-in. pleated, two 1-in. throwaway or 2-in. pleated MERV 11 filters with 2-in. pre-filter shall be installed as indicated on the equipment schedule.

3. Insulation:

a. Units shall be equipped with 1-in. thick Tuf-Skin™ II insulation (standard).

b. Units are available with 1-in. closed cell, 1-in. anti-microbial fiberglass, or 1-in. foil-faced insulation. 

4. Controls:

a. Unit shall be equipped with 24-v transformer, motor contactor and terminal strip for connection to field or factory provided controller.

b. Unit shall be equipped with interlocking door-disconnect switch with lock-out tag-out compatibility, touch-type fusing, 24-v transformer, motor contactor and terminal strip for connection to field provided controller.

c. Unit shall be equipped with interlocking door-disconnect switch with lock-out tag-out compatibility, separate motor and electric heater touch-type fusing, 24-v transformer, motor contactor and terminal strip for connection to field-provided or factory-provided controller.

d. Fuses comply with NFPA 70E/IP20.

5. Electric Heat:

a. Electric heaters shall be constructed of high-grade resistance wire supported by ceramic insulators on plated steel brackets. The heat elements shall be suspended in front of the outlet, after the blower and coil. An auto and manual thermal limit switch shall protect the heat elements in the event of an air failure.

b. Single-phase heaters shall be available in 115, 208, 230, or 277 volts (60 Hz) or 220 volts (50 Hz). Three-phase electric heat shall be available in 208, 230, or 460 volts (60 Hz) or 380 volts (50 Hz).

c. Electric heaters can be controlled in single, 2, or 3 stages of operation.

6. Mixing Boxes:

a. Mixing boxes shall be preassembled at the factory and shipped separately with base rails. 

b. Mixing boxes shall include a linkage kit, which consists of two crankarms, 2 swivels and a rod, 25 in. long (for unit sizes 06-16) or 84 in. long (for unit sizes 20-40), for the field installation of the actuator.

7. Cabinet:

a. Optional double wall construction with choice of 1-in. fiberglass or 1-in. closed cell insulation with solid or perforated inner liners. An antimicrobial coating can also be added.

b. Optional seismic structural upgrade to meet IBC-2009 and OSHPD seismic certification in accordance with ICC-ES-AS-156.

�Third-party trademarks and logos are the property of their respective owners.








1


1

