
Outdoor 60 Hz Air-Cooled Liquid Chiller

HVAC Guide Specifications

Size Range:
10 to 60 Tons

(35 to 211 kW) Nominal 

Carrier Model Number: 30RC

· General

· SYSTEM DESCRIPTION

· Microprocessor controlled, air-cooled liquid chiller for outdoor installation, utilizing scroll compressors, low sound fans, electronic expansion valve, optional hydronic pump system and fluid storage tank.

For units that incorporate Greenspeed intelligence, all fans are controlled with variable speed fan drive motors. Chiller software shall be specifically developed to coordinate optimal fan speed for application conditions and provide refrigerant circuit optimization, resulting in higher part load efficiency and reduced acoustic levels.

· QUALITY ASSURANCE

· Unit shall be rated in accordance with AHRI (Air-Conditioning, Heating and Refrigeration Institute) Standard 550/590, latest edition (U.S.A.) and all units shall be ASHRAE (American Society of Heating, Refrigerating and Air-Conditioning Engineers) 90.1-2019 compliant.

· Unit construction shall comply with ASHRAE 15 Safety Code, UL (Underwriters Laboratories) latest edition, and ASME (American Society of Mechanical Engineers) applicable codes (U.S.A. codes).

· The management system governing the manufacture of this product is ISO (International Organization for Standardization) 9001:2015 certified.

· An operational test, in which the chiller is run under load, is performed at the factory. This test checks for proper operation of fans as well as various controls and safeties, and a Certificate of Unit Testing, indicating successful end-of-line testing, is provided with the unit.

· DELIVERY, STORAGE AND HANDLING

· Unit controls shall be capable of withstanding 150°F (66°C) storage temperatures in the control compartment.

· Unit shall be stored and handled per unit manufacturer's recommendations.

· Products

· EQUIPMENT

· General:

1. Factory assembled, single-piece chassis, air-cooled liquid chiller. Contained within the unit cabinet shall be all factory wiring, piping, controls, refrigerant charge (R-32), and special features required prior to field start-up.

· Materials of Construction:

1. Frame shall be of heavy-gauge, galvanized steel.

2. Exterior panels shall be galvanized steel with a baked enamel powder or pre-painted finish.

3. Painted parts shall withstand 1000 hours in constant neutral salt spray under ASTM (American Society for Testing and Materials) B117 conditions with a 1 mm scribe per ASTM D1654. After test, painted parts shall show no signs of wrinkling or cracking, no loss of adhesion, no evidence of blistering, and the mean creepage shall not exceed 1/4 in. (Rating ³ per ASTM D1654) on either side of the scribe line. 

· Fans:

1. Condenser fans shall be 9-blade airfoil cross-section, reinforced polymer construction, shrouded-axial type, and shall be statically and dynamically balanced with inherent corrosion resistance.

2. The variable speed drives for the condenser fans on 30RC units with Greenspeed intelligence shall include a DC link reactor.

3. Fan operation shall allow reduced sound levels during scheduled unoccupied operating periods. Manufacturers without unoccupied reduced sound capability shall submit 1/3 octave band data and sound power data as measured according to AHRI 370 as confirmation of unit sound characteristics.

4. Air shall be discharged vertically upward.

5. Fans shall be protected by coated steel wire safety guards.

6. Fan blades shall have serrated edges to minimize the sound that is produced.

· Compressor/Compressor Assembly:

1. Fully hermetic, direct-drive, scroll-type compressors.

2. Compressor motors shall be cooled by refrigerant gas passing through motor windings and shall have either internal line break thermal and current overload protection or external current overload modules with compressor temperature sensors.

3. Compressors shall be mounted on rubber in shear vibration isolators.

4. Staging of compressors shall provide unloading capability.

5. The employment of digital compressors (when selected) provides many additional stages of unloading. 

6. When RTPF coils are employed, each compressor shall be equipped with crankcase heaters to minimize oil dilution.

7. Crankcase heaters shall not be required when microchannel condenser coils are utilized. 

· Brazed Plate Evaporator:

1. Evaporator shall be rated for a refrigerant working-side pressure of 710 psig (4895 kPa) and shall be tested for a maximum water-side pressure of 300 psig (2068 kPa).

2. When the hydronic package is installed, the evaporator shall be rated for a refrigerant working-side pressure of 710 psig (4895 kPa) and shall be tested for a maximum water-side pressure of 150 psig (1034 kPa).

3. Shall be single-pass, ANSI (American National Standards Institute) type 316 stainless steel, brazed plate construction.

4. Shell shall be insulated with 3/4-in. (19 mm) closed-cell, polyvinyl-chloride foam with a maximum K factor of 0.28.

5. Shall incorporate 2 independent refrigerant circuits on sizes 035 to 060; sizes 010 to 030 shall have one independent refrigerant circuit.

6. Evaporator shall have factory-installed heater, to protect Evaporator from ambient temperature freeze down to –20°F (–29°C). Unit shall be provided with a factory-installed flow switch.

7. All connections shall use standard Victaulic-type fittings.

8. Evaporator shall be supplied with a 20 mesh strainer.

· Condenser:

1. Coil shall be air-cooled Novation® heat exchanger technology with microchannel (MCHX) coils and shall have a series of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds.

2. Coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for fins, tubes, and manifolds in combination with a corrosion-resistant coating.

3. Tubes shall be cleaned, dehydrated, and sealed.

4. Assembled condenser coils shall be leak tested and pressure tested at 656 psig (4522 kPa).

· Refrigeration Components:

Refrigerant circuit components shall include filter drier, moisture indicating sight glass, electronic expansion device and complete operating charge of both refrigerant R-32 and compressor oil. Per Department of Transportation regulations, when any A2L refrigerant is employed, there must be a suction service valve on any chiller containing a charge of 20 kg or more. 

Therefore, no suction service valve is required or included on any unit employing microchannel condenser coils or any 010-030 units employing RTPF coils.

Therefore, a suction service valve is included on all 30RC035-060 chillers which employ Al/Cu coils.

· Controls, Safeties, and Diagnostics:

1. Unit controls shall include the following minimum components:

a. Microprocessor with non-volatile memory. Battery backup system shall not be accepted.

b. Separate terminal block for power and controls.

c. Control transformer to serve all controllers, relays, and control components.

d. ON/OFF control switch.

e. Replaceable solid-state controllers.

f. Pressure sensors shall be installed to measure suction and discharge pressure for each circuit. Thermistors shall be installed to measure evaporator entering and leaving fluid temperatures, outdoor ambient temperature, and discharge temperature.

2. Unit controls shall include the following functions:

a. Automatic circuit primary/secondary for dual circuit chillers.

b. Hermetic scroll compressors are maintenance free and protected by an auto-adaptive control that minimizes compressor wear.

c. Capacity control based on leaving chilled fluid temperature and compensated by rate of change of return-fluid temperature with temperature set point accuracy to 0.1°F (0.06°C).

d. Limiting the chilled fluid temperature pull-down rate at start-up to an adjustable range of 0.2°F to 2°F (0.11°C to 1.1°C) per minute to prevent excessive demand spikes at start-up.

e. Seven-day time schedule.

f. Leaving chilled fluid temperature reset from return fluid and outside air temperature.

g. Chilled water pump start/stop control and primary/standby sequencing to ensure equal pump run time.

h. Dual chiller control for parallel chiller applications with the addition of an EMM, but without the addition of other hardware modules and control panels (additional thermistors and wells are required).

i. Timed maintenance scheduling to signal maintenance activities for pumps, condenser coil cleanings, strainer maintenance and user-defined maintenance activities.

j. Boiler enable signal to initiate system heating mode.

k. Low ambient protection to energize evaporator and hydronic system heaters.

l. Periodic pump start to ensure pump seals are properly maintained during off-season periods.

m. Single step demand limit control activated by remote contact closure.

n. Nighttime sound mode to reduce the sound of the machine by a user-defined schedule.

3. Diagnostics:

a. The control panel shall include, as standard, a display:

1) Color touch screen display with stylus.

2) Display shall allow a user to navigate through menus, select desired options, and modify data.

b. Features of the display shall include:

1) Multiple connection ports for USB, Ethernet, or BACnet
 (MS/TP or IP), Modbus1-RTU (Remote Terminal Unit), LEN (local equipment network), and Carrier Comfort Network® (CCN) connections. 

NOTE: BACnet (MS/TP or IP) may require additional programming.

2) Automatic reporting of alarms over email.

3) Ability to graphically plot trends of system performance and conditions over time.

4) Graphical summary display of current chiller operation and water conditions.

5) Display shall allow access to configuration, maintenance, service, set point, time schedules, alarm history, and status data.

6) Three levels of password protection against unauthorized access to configuration and maintenance information, and display set up parameters.

7) Full compatibility with the Carrier Comfort Network® (CCN) system to provide email alarm notification and to provide network capability to fully monitor and control chiller.

8) Display shall be capable of displaying the last 50 alarms, with clear full text description and time and date stamp, and will store a snapshot of operating conditions before and after the 10 most recent alarms.

9) Display run hours and number of starts for machine and individual compressors.

10) The control system shall allow software upgrade without the need for new hardware modules.

4. Safeties:

a. Unit shall be equipped with thermistors and all necessary components in conjunction with the control system to provide the unit with the following protections:

1) Reverse rotation.

2) Low chilled fluid temperature.

3) Motor overtemperature.

4) High pressure.

5) Electrical overload.

6) Thermal overload.

7) Loss of refrigerant charge.

b. Condenser fan motors shall have internal overcurrent protection.

· Operating Characteristics:

1. Unit shall be capable of operating down to –20°F (–29°C) on unit sizes 010 and 015.

2. Unit shall be capable of operating down to 45°F (7.2°C) on unit sizes 020-030, and down to 32°F (0°C) on unit sizes 035-060 as standard. These unit sizes are also capable of lower starting and operating temperatures with the inclusion of wind baffles and high-efficiency variable condenser fans.

3. Unit shall be capable of starting and running at outdoor ambient temperatures up to 120°F (50°C) for all sizes. Unit shall additionally be able to stay online when running with a 125°F (52°C) ambient temperature.

4. Unit shall be capable of starting up with 95°F (35°C) entering fluid temperature to the evaporator.

· Fan Motors:

1. Condenser fan motors shall be totally enclosed, air over, 3-phase type with permanently lubricated bearings and Class F insulation.

· Electrical Requirements:

1. Unit/module primary electrical power supply shall enter the unit at a single electrical box.

2. Unit shall operate on 3-phase power at the voltage shown in the equipment schedule.

3. Control points shall be accessed through terminal block.

4. Unit shall be shipped with factory control and power wiring installed.

5. Unit shall have a standard SCCR (short circuit current rating) of 10 kA.

· Chilled Water Circuit:

1. Chilled water circuit shall be rated for 300 psig (2068 kPa). Units with optional pump package are rated for 150 psig (1034 kPa) working pressure.

2. Solid-state flow monitor with integral relay shall be factory installed and wired.

3. Brass body strainer with 20 mesh screen and ball type blow down.

4. Optional hydronic package (applies to 280/230 and 460-v unit sizes except as noted, with or without the use of VFD [variable frequency drive]):

a. Field pipe connections shall be carbon steel Victaulic type.

b. Optional single or primary /stand-by operation pump systems.

c. Dual pump systems shall have a pump discharge check valve.

d. For dual-pump packages, the equipment shall have one pump operating, and a simple transition to the back-up pump shall be accomplished by means of a valve which shall be supplied with this configuration.

e. For dual-pump packages, when servicing is required, the pump removal/installation process shall require neither the chiller to be drained nor the installation of a blank flange to replace the pump vertical in-line, being removed/installed.

f. Pumps shall be single stage design, capable of being serviced without disturbing piping connections.

1) Pump casing shall be of class 30 cast iron.

2) The impeller shall be of cast bronze, closed type, dynamically balanced, keyed to the shaft and secured by locking cap screw.

3) The hydronic kit will be provided with a flush line connection to ensure lubrication at the seal face and allow for positive venting of the seal chamber.

4) Each port shall be fitted with an isolation valve that allows the units to operate in parallel or standby, yet may be used to isolate one pumping unit for servicing or removal with the other pump still running.

5) Pump shall be rated for 150 psig (1034 kPa) working pressure.

6) The pump piping shall have gauge tappings at the suction and discharge lines and include drain ports. 
7) Dual pumps shall allow for the servicing of one pump without draining the chilled water loop.

8) Motors shall be TEFC 3-phase type with grease-lubricated ball bearings.

9) Each pump shall be factory tested per Hydraulic Institute Standards.

10) Pump motors shall be VFD compatible.

g. Fluid expansion tank shall be factory installed within the chiller cabinet insulates, pre-charged and rated for a maximum working pressure of 150 psig (1034 kPa).

h. Water pressure taps (2) shall be factory installed across the evaporator and rated for 150 psig (1034 kPa).

i. Combination valve (which includes check, isolation, and modulation) shall be factory installed. Pressure/temperature taps (2) shall be factory installed to measure the pressure differential across the combination valve.

j. Hydronic assembly shall have factory-supplied electric freeze protection to –20°F (–29°C) when optional heaters are used.

· Special Features:

Certain standard features are not applicable when the features designated by * are specified. For assistance in amending the specifications, contact your Carrier representative.

1. High-efficiency variable condenser fans:

All fans on the unit shall have variable speed fan motors to provide higher part load efficiency and reduced acoustic levels. Each fan circuit shall have a factory-installed, independent variable speed drive with display. Variable speed drives are rated IP-55 enclosures and UL Listed. The use of this option or accessory, with the addition of antifreeze in the evaporator circuit and wind baffles or hail guards, shall allow running with outdoor ambient temperatures down to –20°F (–28.9°C). This feature is standard on sizes 010 and 015.

2. *
Low-Ambient Operation:

Unit shall be capable of starting as low as and operating down to –20°F (–29°C) with the use of high-efficiency variable condenser fans. In addition, adequate field-supplied antifreeze with suitable corrosion inhibitor protection shall be field-installed in the evaporator circuit. Field-installed wind baffles or factory-installed hail guards shall also be required. If significant low-load operation is anticipated, then hot gas bypass is recommended. High-efficiency variable condenser fans are standard on sizes 010 and 015.

NOTE: The motors associated with low ambient head pressure control will be open type and shall have class B insulation.

3. Unit-Mounted Non-Fused Disconnect:

Unit shall be supplied with factory-installed, non-fused electrical disconnect for main power supply. This option shall be included with the high SCCR option.

4. Optional Condenser Coil Materials:

a. E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum microchannel coils shall be capable of withstanding 10,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) B-117 Standard.

b. Aluminum fin/copper tube coils:

Coil shall be constructed of seamless copper tubes mechanically bonded to aluminum fins. Fins shall have wavy enhancements. These condenser coils are recommended for remote evaporator applications. These coils are not recommended for corrosive environments.

c. E-coated aluminum-fin coils:

Coil shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss; 60° of 65 to 90% per ASTM ID523‑89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). E-coated aluminum-fin coils shall be capable of withstanding 10,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) B-117 Standard. Coil construction shall be aluminum fins mechanically bonded to copper tubes.

5. Hot Gas Bypass:

Unit shall be equipped with factory or field-installed, microprocessor-controlled, hot gas bypass that shall permit unit operation down below the minimum standard step of capacity. The factory option is not available on sizes 010 and 015 or on any application with a leaving fluid temperature below 38°F (3.3°C). Option and accessory not available on units with the digital compressor option.

6. Energy Management Module:

A factory or field-installed module shall provide the following energy management capabilities: cooling set point and demand limit control; 2-point demand limit control (from 15% to 100%) activated by a remote contact closure; discrete input for “Ice Done” indication for ice storage system interface and dual chiller leaving water temperature for parallel dual chiller control or chilled water reset based upon space temperature.

7. Hail Guards:

Unit shall be supplied with factory or field-installed, louvered, sheet metal panels which securely fasten to the chiller and provide condenser coil protection against hail and other physical damage. This option or accessory directly covers the coil(s) on all sizes. Hail guards also provide the functionality of wind baffles. 

8. Vibration Isolation:

Vibration isolation pads shall be supplied for field installation at unit mounting points. Pads shall help to reduce vibration transmission into the occupied space.

9. Chilled Water Storage Tank:

a. Fluid storage tank shall be rated for a maximum of 150 psig (1034 kPa).

b. Shall provide a minimum 4 gallon per ton (3.7 L per kW) fluid storage capacity.

c. Shall fit under the chiller to minimize system footprint requirements. Tanks fitted outside of chiller footprint shall not be acceptable.

d. Tank shall be constructed a cold rolled carbon steel shell.

e. Tank shall be insulated with 3/4-in. (19 mm) closed-cell, polyvinyl-chloride foam with a maximum K factor of 0.28.

f. Tank shall be baffled to prevent temperature stratification.

g. Tank shall have Victaulic connections. 

h. Tank shall have vent and drain plugs accessible from outside tank enclosure.

i. Internal heaters shall provide freeze protection to –20°F (–29°C). The included heater thermostat prevents overheating of the fluid.

10. BACnet (MS/TP or IP):

Shall provide a factory-installed interface between the chiller and a BACnet Local Area Network (LAN) and allows integration with i-Vu® Open control system or a third-party BACnet building automation system. Field configuration is required.

11. LonWorks Translator:

Unit shall be supplied with field-installed interface between the chiller and a Local Operating Network (LON, i.e., LonWorks FT-10A ANSI/EIA-709.1). Field programming shall be required.

12. GFI Convenience Outlet:

Shall be factory or field installed to provide the chiller with a 4 amp GFI receptacle. The receptacle shall have independent fuse protection. The convenience outlet is a 115-v female receptacle. When this item is factory-installed, remote connectivity is also included.

13. Compressor Blankets:

Shall provide factory or field-installed sound blankets around each compressor in conjunction with low-sound AeroAcoustic™ fans to provide significant chiller sound reduction.

14. High SCCR (Short Circuit Current Rating):

The optional high SCCR (short circuit current rating) device shall allow the chiller to tolerate a 65 kA (208/230-v, 380-v and 460-v) and 25 kA (575V) short circuit current for a brief period of time while protecting the downstream components. The high SCCR option shall provide a higher level of protection than the standard unit. The selection of this option includes a non-fused disconnect.

15. Digital Compressor Option:

Shall provide a factory-installed digital compressor to provide incremental steps for tighter temperature control (not available on any application with a leaving fluid temperature below 38°F [3.3°C]).

16. Wind Baffles:

Wind baffles shall be field installed to facilitate operation down to –20°F (–29°C) when used in conjunction with high-efficiency variable condenser fans.

17. Suction Line Insulation:

Shall provide a tubular, closed-cell form of insulation that is factory-installed on the chiller suction piping.

18. Phase Loss Monitor:

Shall be factory installed to provide the unit with protection against phase loss.

19. Remote Connectivity:

Shall be factory-installed to provide a secure cellular system which communicates operating information to a central operating site. The selection of this option automatically includes GFI convenience outlet.

20. Dry Shipment:

30RC030-060 units requiring container shipment (ocean freight), and whose operational refrigerant charge is 12 kg or more (see Physical Data), shall comply with transportation rules and be shipped without refrigerant. Dry shipment shall require that the unit be shipped from the factory with a nitrogen holding charge as opposed to a charge of refrigerant. When the dry shipment option is employed, all labor and refrigerant costs shall be handled locally.

�Third-party trademarks and logos are the property of their respective owners.








1


1

