
Commercial Air-Cooled Condensers with Puron® Refrigerant (R‑410A), R‑513A, or R‑134a Refrigerant, 50/60 Hz

HVAC Guide Specifications

Size Range: 

18 to 130 Nominal Tons (63 to 457 Nominal kW)

Carrier Model Number: 
09DPM, 09DPS

· General

· SYSTEM DESCRIPTION

Outdoor-mounted, air-cooled condenser suitable for refrigerant R‑410A, R‑513A, or R‑134a on the ground or rooftop installation. The 09DPS unit shall have one refrigeration circuit and 

the 09DPM unit shall have two independent refrigeration circuits capable of field conversion to single circuit. Unit shall have air-cooled coils, propeller-type condenser fans, a control box, and shall discharge condenser air vertically upward as shown on certified drawings. Unit shall be used in refrigeration circuit with 30MPA or 30HXA air-cooled condenserless chillers.

· QUALITY ASSURANCE

· Unit construction shall comply with latest edition of ASHRAE 15 Safety Code, UL 1995, and ASME applicable codes (U.S.A. codes).

· Unit shall be manufactured in a facility registered to ISO 9001: 2015 Manufacturing Quality Standard.

· Base unit shall be constructed in accordance with UL standards and CSA.

· Painted parts shall withstand 1000 hours in constant neutral salt spray under ASTM B117 conditions with a 1mm scribe per ASTM D1654. After test, painted parts shall show no signs of wrinkling or crackling, no loss of adhesion, no evidence of blistering, and the main creepage shall not exceed 1/4 in. (rating ³ 4 per ASTM D1654) on either side of the scribe line.

· Design pressure shall be 650 psig (4482 kPa).

· Unit shall be functional checked at the factory.

· Unit shall be rated using refrigerants R‑410A, R‑513A, and R‑134a. Ratings shall be listed at minimum (5°F subcooling) and maximum (15°F subcooling) refrigerant charge.

· DELIVERY, STORAGE, AND HANDLING

Unit shall be shipped as single package and shall be stored and handled per unit manufacturer's recommendations.

· WARRANTY (FOR INCLUSION BY SPECIFYING ENGINEER)

· Products

· EQUIPMENT

· General:

Factory assembled, single-piece, air-cooled remote condenser. Contained within the unit enclosure shall be all factory wiring, piping, controls, nitrogen holding charge, and special features required prior to field start-up.

· Unit Cabinet:

1. Cabinet shall be galvanized steel casing with a baked enamel powder or pre-painted finish.

2. Painted parts shall withstand 1000 hours in constant neutral salt spray under ASTM B117 conditions with a 1 mm scribe per ASTM D1654. After test, painted parts shall show no signs of wrinkling or crackling, no loss of adhesion, no evidence of blistering, and the main creepage shall not exceed 1/4-in. (rating ³ 4 per ASTM D1654) on either side of the scribe line.

3. Control box access panels shall be removable for service access.

4. Lifting holes shall be provided to facilitate rigging.

· Fans:

1. Condenser fans shall be direct-drive propeller type, discharging air vertically upward.

2. All condenser fan motors shall be totally enclosed 3-phase type with permanently lubricated ball bearings, class F insulation, and internal, automatic-reset thermal overload protection.

3. Shafts shall have inherent corrosion resistance.

4. Fan blades shall be statically and dynamically balanced.

5. Condenser-fan openings shall be equipped with PVC-coated steel wire safety guards.

· Condenser Coils:

1. Coil shall be air-cooled microchannel heat exchanger (MCHX) and shall have a series

2.  of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds. Microchannel coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for the fins, tubes and manifolds in combination with a corrosion-resistant coating on the tubes. 

3. Tubes shall be cleaned, dehydrated, and sealed.

4. Assembled condenser coils shall be leak tested and pressure tested at 650 psig (4482 kPa).

5. To plan the unit installation and for ease of maintenance/coil removal on unit sizes 09DP065-130, all refrigerant piping entering and leaving the condenser coils shall be located on only one side of the condensing unit so the coils can be removed (when needed) from the side free of piping. This is important to consider because removing the coils from the header side, although possible, involves extra labor due to extra bending and brazing of the coil headers.

· Refrigeration Components:

Refrigeration circuit components shall include liquid line temperature relief device and nitrogen holding charge.

· Controls and Safeties:

Unit controls shall include:

1. Unit shall have a temperature fusible plug for safety on each refrigerant circuit. 

2. Self-contained low voltage control circuit.

3. Cycle condenser fans to maintain proper head pressure control.

· Operating Characteristics:

1. Unit shall be capable of rejecting the required heat at the required cfm and be capable of operating down to moderate ambient temperatures with standard factory supplied fan cycling.

2. Head pressure fan cycling control utilizes temperature switches for 09DP018-035 and 065 units.

3. Head pressure fan cycling control utilizes temperature and pressure switches for 09DP040-060 and 075-130 units.

· Electrical Requirements:

1. A dual power supply of the correct voltage shall be required for each series unit. A 3-phase power circuit voltage and a 24 volt single-phase control circuit shall be required.

2. The number of control circuits shall depend on the unit application, whether it is matched with one unit or two units.

3. Power supplies for all units shall enter the control box through factory-punched entrance holes in the control box shelf.

4. Terminal blocks shall be supplied for field wiring connections.

5. Units shall utilize electromechanical fan cycling head pressure controls to control proper head pressure.

· Special Features:

1. Optional Condenser Coil Materials:

a. E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum microchannel coils shall be capable of withstanding 8,000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) B-117 Standard.

b. Aluminum fin/copper tube coils:

Coil shall be constructed of seamless copper tubes mechanically bonded to aluminum fins. Fins shall have wavy enhancements. These condenser coils are recommended with remote cooler applications. These coils are not recommended for corrosive environments.

c. E-coated aluminum-fin coils:

Coil shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss; 60° of 65 to 90% per ASTM ID523-89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). E-coated aluminum-fin coils shall be capable of withstanding an 8000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) (U.S.A.) B-117 Standard. Coil construction shall be aluminum fins mechanically bonded to copper tubes.

2. Sound Reduction:

a. Low sound fan for sound reduction is available as a factory-installed option or field-installed accessory for all units.

b. Low sound fans shall be direct driven, 9-blade, airfoil cross-section type with rein-forced polymer construction and shrouded axial fan. Fan shall be statically and dynamically balanced with inherent corrosion resistance.

3. Non-Fused Disconnect:

A non-fused disconnect is available as a factory-installed option for all units having single point power connection units.

4. High Short Circuit Current Rating (SCCR):

The optional high SCCR interrupt capability shall allow the unit to tolerate a 65 kA (208/230v, 380v and 460-v units) or 25 kA (575-v units) short circuit current for a brief period of time while protecting downstream components. The high SCCR option shall provide a higher level of protection than the standard unit (option for 60 Hz only). High interrupt shall be available as factory-installed option on all units.

5. Security Grilles/Hail Guards:

Units shall be supplied with factory-installed or field-installed louvered, sheet metal panels which securely fasten to the unit to provide condenser coil protection against hail and physical damage.

6. Vibration Isolation Pads:

Neoprene vibration isolation pads (24 in. x 3 in. x 1/4 in.) shall be available for field installation to reduce vibration transmission from the compressor through the floor and into the conditioned space.

1


1

