 “Masterformat” as published by the Construction Specification Institute. Please feel free to copy this specification directly into your building spec.[image: image1.wmf]
WeatherMaster® Gas Heat/Electric Cooling Packaged Rooftop

HVAC guide specifications

Size range: 3 to 12.5 Nominal Tons

Carrier Model Number: 48HC*04-14

· (23 06 80) Schedules for decentralized 
HVAC equipment

· (23 06 80.13) Decentralized Unitary HVAC Equipment Schedule

· (23 06 80.13.A.) Rooftop unit (RTU) schedule

· Schedule is per the project specification requirements.

· (23 07 16) HVAC equipment insulation

· (23 07 16.13) Decentralized, Rooftop Units:

· (23 07 16.13.A.) Evaporator fan compartment:

· Interior cabinet surfaces shall be insulated with a minimum 1/2-in. thick, minimum 1 1/2-lb density, flexible fiberglass insulation bonded with a phenolic binder, neoprene coated on the air side.

· Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

· Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

· 
(23 07 16.13.B.) Gas Heat Compartment:

· Aluminum foil-faced fiberglass insulation shall be used.

· Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

· (23 09 13) Instrumentation and control devices for HVAC

· (23 09 13.23) Sensors and Transmitters

· (23 09 13.23.A.) Thermostats

· Thermostat must

· energize both “W” and “G” when calling for heat.

· have capability to energize 2 different stages of cooling, and 2 different stages of heating.

· include capability for occupancy scheduling.

· (23 09 23) Direct-digital control system for HVAC

· (23 09 23.13) Decentralized, Rooftop Units:

· (23 09 23.13.A.) PremierLink™ Controller

· Shall be ASHRAE 62 compliant.

· Shall accept 18-32 VAC input power.

· Shall have an operating temperature range from –40°F (–40°C) to 158°F (70°C), 10% to 95% RH (non-condensing).

· Shall include an integrated economizer controller to support an economizer with 4 to 20 mA actuator input and no microprocessor controller.

· Controller shall accept the following inputs: space temperature, setpoint adjustment, outdoor air temperature, indoor air quality, outdoor air quality, indoor relative humidity, compressor lock-out, fire shutdown, enthalpy, fan status, remote time clock/door switch.

· Shall accept a CO2 sensor in the conditioned space, and be Demand Controlled Ventilation (DCV) ready.

· Shall provide the following outputs: economizer, fan, cooling stage 1, cooling stage 2, heat stage 1, heat stage 2, heat stage 3/exhaust/ reversing valve/ dehumidify/ occupied.

· Unit shall provide surge protection for the controller through a circuit breaker.

· Shall be Internet capable, and communicate at a Baud rate of 38.4K or faster.

· Shall have an LED display independently showing the status of activity on the communication bus, and processor operation.

· Shall include an EIA-485 protocol communication port, an access port for connection of either a computer or a Carrier technician tool, an EIA-485 port for network communication to intelligent space sensors and displays, and a port to connect an optional LonWorks
 plug-in communications card.

· Shall have built-in Carrier Comfort Network® (CCN) protocol, and be compatible with other CCN devices, including ComfortLink and ComfortVIEW™ controllers.

· Shall have built-in support for Carrier technician tool.

· Software upgrades will be accomplished by local download. Software upgrades through chip replacements are not allowed.

· Shall be shock resistant in all planes to 5G peak, 11ms during operation, and 100G peak, 11ms during storage.

· Shall be vibration resistant in all planes to 1.5G at 20-300 Hz.

· Shall support a bus length of 4000 ft (1219 m) max, 60 devices per 1000 ft (305 m) section, and 1 RS-485 repeater per 1000 ft (305 m) sections.

· (23 09 23.13.B.) RTU Open Protocol, Direct Digital Controller:

· Shall be ASHRAE 62 compliant.

· Shall accept 18-30VAC, 50-60Hz, and consume 15VA or less power.

· Shall have an operating temperature range from –40°F (–40°C) to 130°F (54°C), 10% to 90% RH (non-condensing).

· Shall include built-in protocol for BACnet
 (MS/TP and PTP modes), Modbus
 (RTU and ASCII), Johnson N2 and LonWorks. LonWorks Echelon processor required for all Lon applications shall be contained in separate communication board.

· Shall allow access of up to 62 network variables (SNVT). Shall be compatible with all open controllers.

· Baud rate Controller shall be selectable using a dip switch.

· Shall have an LED display independently showing the status of serial communication, running, errors, power, all digital outputs, and all analog inputs.

· Shall accept the following inputs: space temperature, setpoint adjustment, outdoor air temperature, indoor air quality, outdoor air quality, compressor lock- out, fire shutdown, enthalpy switch, and fan status / filter status / humidity / remote occupancy.

· Shall provide the following outputs: economizer, variable frequency drive, fan, cooling stage 1, cooling stage 2, heat stage 1, heat stage 2, exhaust reversing valve/high fan speed.

· Shall have built-in surge protection circuitry through solid-state polyswitches. Polyswitches shall be used on incoming power and network connections. Polyswitches will return to normal when the “trip” condition clears.

· Shall have a battery backup capable of a minimum of 10,000 hours of data and time clock retention during power outages.

· Shall have built-in support for Carrier technician tool.

· Shall include an RS-485 protocol communication port, an access port for connection of either a computer or a Carrier technician tool, an RS-485 port for network communication to intelligent space sensors and displays, and a port to connect an optional LonWorks communications card.

· Software upgrades will be accomplished by either local or remote download. No software upgrades through chip replacements are allowed.

· (23 09 23.13.C.) ComfortLink Unit Controls shall contain:

· Four button detailed English scrolling marquee display.

· CCN (Carrier Comfort Network) capable.

· Unit control with standard suction pressure transducers and condensing temperature thermistors.

· Shall provide a 5°F temperature difference between cooling and heating set points to meet ASHRAE 90.1-2016 Energy Standard.

· Shall provide and display a current alarm list and an alarm history list.

· Service run test capability.

· Shall accept input from a CO2 sensor (both indoor and outdoor).

· Configurable alarm light shall be provided which activates when certain types of alarms occur.

· Compressor minimum run time (3 minutes) and minimum off time (5 minutes) are provided.

· Service diagnostic mode.

· Economizer control (optional).

· Control multiple capacity stages.

· Unit shall be complete with self-contained low voltage control circuit.

· Unit shall have 0°F low ambient cooling operation.

· (23 09 33) Electric and electronic control system for HVAC

· (23 09 33.13) Decentralized, Rooftop Units

· (23 09 33.13.A) General:

· Shall be complete with self-contained low-voltage control circuit protected by a resettable circuit breaker on the 24-v transformer side. Transformer shall have 75VA capability.

· Shall utilize color-coded wiring.

· Shall include a central control terminal board to conveniently and safely provide connection points for vital control functions such as: smoke detectors, phase monitor, economizer, thermostat, DDC control options, loss of charge, freeze switch, high pressure switches.

· The heat exchanger shall be controlled by an integrated gas controller (IGC) microprocessor. See heat exchanger section of this specification.

· Unit shall include a minimum of one 8-pin screw terminal connection board for connection of control wiring.

· (23 09 33.23.B) Safeties:

· Compressor over-temperature, over-current.

· Low-pressure switch.

· Units with 2 compressors shall have different sized connectors for the circuit 1 and circuit 2 loss of charge switches. They shall physically prevent the cross-wiring of the safety switches between circuits 1 and 2.

· Loss of charge switch shall use different color wire than the high pressure switch. The purpose is to assist the installer and service technician to correctly wire and/or troubleshoot the rooftop unit.

· High-pressure switch.

· Units with 2 compressors shall have different sized connectors for the circuit 1 and circuit 2 high pressure switches. They shall physically prevent the cross-wiring of the safety switches between circuits 1 and 2.

· High-pressure switch shall use different color wire than the low-pressure switch. The purpose is to assist the installer and service technician to correctly wire and/or troubleshoot the rooftop unit.

· Automatic reset, motor thermal overload protector.

· Heating section shall be provided with the following minimum protections.

· High-temperature limit switches.

· Induced draft motor speed sensor.

· Flame rollout switch.

· Flame proving controls.

· (23 09 93) Sequence of operations for HVAC controls

· (23 09 93.13) Decentralized, Rooftop Units:

· (23 09 93.13.A) INSERT SEQUENCE OF OPERATION

· (23 40 13) Panel air filters

· (23 40 13 13) Decentralized Rooftop Units:

· (23 40 13 13.A) Standard Filter Section

· Shall consist of factory-installed, low velocity, throwaway 2-in. thick fiberglass filters of commercially available sizes.

· Unit shall use only one filter size. Multiple sizes are not acceptable.

· Filters shall be accessible through an access panel with “no-tool” removal as described in the unit cabinet section of this specification (23 81 19.13.G).

· (23 81 19) Self-contained air conditioners

· (23 81 19.13) Small-Capacity Self-Contained Air Conditioners (48HC**04-14)

· (23 81 19.13.A) General

· Outdoor, rooftop mounted, electrically controlled, heating and cooling unit utilizing hermetic scroll compressor(s) for cooling duty and gas combustion for heating duty.

· Factory assembled, single piece heating and cooling rooftop unit. Contained within the unit enclosure shall be all factory wiring, piping, controls, and special features required prior to field start-up.

· Unit shall use Puron® refrigerant.

· Unit shall be installed in accordance with the manufacturer’s instructions.

· Unit must be selected and installed in compliance with local, state, and federal codes.

· (23 81 19.13.B.) Quality Assurance

· Unit meets ASHRAE 90.1-2016 and IECC-2015 minimum efficiency requirements.

· 3-phase units are ENERGY STAR
 qualified.

· Unit shall be rated in accordance with AHRI Standards 210/240 and 340/360.

· Unit shall be designed to conform to ASHRAE 15.

· Unit shall be UL-tested and certified in accordance with ANSI Z21.47 Standards and UL or ETL-listed and certified under Canadian standards as a total package for safety requirements.

· Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

· Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

· Unit casing shall be capable of withstanding 500-hour salt spray exposure per ASTM B117 (scribed specimen).

· Roof curb shall be designed to conform to NRCA Standards.

· Unit shall be subjected to a completely automated run test on the assembly line. The data for each unit will be stored at the factory, and must be available upon request.

· Unit shall be designed in accordance with UL Standard 1995, including tested to withstand rain.

· Unit shall be constructed to prevent intrusion of snow and tested to prevent snow intrusion into the control box up to 40 mph.

· Unit shake tested to assurance level 1, ASTM D4169 to ensure shipping reliability.

· High Efficiency Motors listed shall meet section 313 of the Energy Independence and Security Act of 2007 (EISA 2007).

· (23 81 19.13.C) Delivery, Storage, and Handling

· Unit shall be stored and handled per manufacturer’s recommendations.

· Lifted by crane requires either shipping top panel or spreader bars.

· Unit shall only be stored or positioned in the upright position. 

· (23 81 19.13.D) Project Conditions

· As specified in the contract.

· (23 81 19.13.E) Operating Characteristics

· Unit shall be capable of starting and running at 125°F (52°C) ambient outdoor temperature, meeting maximum load criteria of AHRI Standard 340/360 at ± 10% voltage.

· Compressor with standard controls shall be capable of operation from 35°F (2°C), ambient outdoor temperatures. Accessory kits are necessary if mechanically cooling at ambient temperatures below 35°F (2°C).

· Unit shall discharge supply air vertically as shown on contract drawings.

· Unit shall be factory configured and ordered for vertical supply and return configurations.

· Unit shall be factory furnished in vertical configurations.

· Unit shall be capable of mixed operation: vertical supply with horizontal return or horizontal supply with vertical return.

·  (23 81 19.13.F) Electrical Requirements

· Main power supply voltage, phase, and frequency must match those required by the manufacturer.

· Control Panel SCCR (short circuit current rating): 5kA RMS at Rated Symmetrical Voltage.

· 
(23 81 19.13.G) Unit Cabinet

· Unit cabinet shall be constructed of galvanized steel, and shall be bonderized and coated with a pre-painted baked enamel finish on all externally exposed surfaces.

· Unit cabinet exterior paint shall be: film thickness, (dry) 0.003 inches minimum, gloss (per ASTM D523, 60°): 60, Hardness: H-2H Pencil hardness.

· Evaporator fan compartment interior cabinet insulation shall conform to AHRI Standards 340/360 minimum exterior sweat criteria. Interior surfaces shall be insulated with a minimum 1/2-in. thick, 1 lb density, flexible fiberglass insulation, neoprene coated on the air side. Aluminum foil-faced fiberglass insulation shall be used in the heat compartment.

· Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

· Base of unit shall have a minimum of four locations for factory thru-the-base gas and electrical connections (factory-installed or field-installed) standard. Connections shall be internal to the cabinet to protect from environmental issues.

· Base Rail:

· Unit shall have base rails on a minimum of 2 sides.

· Holes shall be provided in the base rails for rigging shackles to facilitate maneuvering and overhead rigging.

· Holes shall be provided in the base rail for moving the rooftop by fork truck.

· Base rail shall be a minimum of 16 gauge thickness.

· Condensate Pan and Connections:

· Shall be a sloped condensate drain pan made of a non-corrosive material.

· Shall comply with ASHRAE Standard 62.

· Shall use a 3/4-in. 14 NPT drain connection at the end of the drain pan. Connection shall be made per manufacturer’s recommendations.

· Top Panel:

· Shall be a multi-piece top panel linked with water tight flanges and interlocking systems.

· Gas Connections:

· All gas piping connecting to unit gas valve shall enter the unit cabinet at a single location on side of unit (horizontal plane).

· Thru-the-base capability

· Standard unit shall have a thru-the-base gas-line location using a raised, embossed portion of the unit basepan.

· Optional, factory-approved, water-tight connection method must be used for thru-the-base gas connections.

· No basepan penetration, other than those authorized by the manufacturer, is permitted.

· Electrical Connections:

· All unit power wiring shall enter unit cabinet at a single, factory-prepared, knockout location.

· Thru-the-base capability

· Standard unit shall have a thru-the-base electrical location(s) using a raised, embossed portion of the unit basepan.

· Optional, factory-approved, water-tight connection method must be used for thru-the-base electrical connections.

· No basepan penetration, other than those authorized by the manufacturer, is permitted.

· Component Access Panels (standard):

· Cabinet panels shall be easily removable for servicing.

· Unit shall have one factory installed, tool-less, removable, filter access panel.

· Panels covering control box and filters shall have molded composite handles while the blower access door shall have an integrated flange for easy removal.

· Handles shall be UV modified, composite. permanently attached, and recessed into the panel.

· Screws on the vertical portion of all removable access panel shall engage into heat resistant, molded composite collars.

· Collars shall be removable and easily replaceable using manufacturer recommended parts.

· 
(23 81 19.13.H.) Gas Heat

· General:

· Heat exchanger shall be an induced draft design. Positive pressure heat exchanger designs shall not be allowed.

· Shall incorporate a direct-spark ignition system and redundant main gas valve.

· Gas supply pressure at the inlet to the rooftop unit gas valve must match that required by the manufacturer.

· The heat exchanger shall be controlled by an integrated gas controller (IGC) microprocessor.

· IGC board shall notify users of fault using an LED (light-emitting diode).

· The LED shall be visible without removing the control box access panel.

· IGC board shall contain algorithms that modify evaporator-fan operation to prevent future cycling on high temperature limit switch.

· Unit shall be equipped with anti-cycle protection with one short cycle on unit flame roll-out switch or 4 continuous short cycles on the high temperature limit switch. Fault indication shall be made using an LED.

· Standard Heat Exchanger Construction:

· Heat exchanger shall be of the tubular-section type constructed of a minimum of 20-gauge steel coated with a nominal 1.2 mil aluminum-silicone alloy for corrosion resistance.

· Burners shall be of the in-shot type constructed of aluminum-coated steel.

· Burners shall incorporate orifices for rated heat output up to 2000 ft (610m) elevation. Additional accessory kits may be required for applications above 2000 ft (610m) elevation, depending on local gas supply conditions.

· Each heat exchanger tube shall contain multiple dimples for increased heating effectiveness.

· Optional Stainless Steel Heat Exchanger Construction:

· Use energy saving, direct-spark ignition system.

· Use a redundant main gas valve.

· Burners shall be of the in-shot type constructed of aluminum-coated steel.

· All gas piping shall enter the unit cabinet at a single location on side of unit (horizontal plane).

· The optional stainless steel heat exchanger shall be of the tubular-section type, constructed of a minimum of 20-gauge type 409 stainless steel.

· Type 409 stainless steel shall be used in heat exchanger tubes and vestibule plate.

· Complete stainless steel heat exchanger allows for greater application flexibility.

· Optional Low NOx Heat Exchanger Construction:

· Low NOx reduction shall be provided to reduce nitrous oxide emissions to meet California’s Air Quality Management District (SCAQMD) low-NOx emissions requirement of 40 nanograms per joule or less.

· Primary tubes and vestibule plates on low NOx units shall be 409 stainless steel. Other components shall be aluminized steel.

· Induced Draft Combustion Motor and Blower:

· Shall be a direct-drive, single inlet, forward-curved centrifugal type.

· Shall be made from steel with a corrosion-resistant finish.

· Shall have permanently lubricated sealed bearings.

· Shall have inherent thermal overload protection.

· Shall have an automatic reset feature.

· 
(23 81 19.13.I.) Coils

· Standard Aluminum Fin/Copper Tube Coils:

· Standard evaporator and condenser coils shall have aluminum lanced plate fins mechanically bonded to seamless internally grooved copper tubes with all joints brazed.

· Evaporator coils shall be leak tested to 150 psig, pressure tested to 450 psig, and qualified to UL 1995 burst test at 1775 psig.

· Condenser coils shall be leak tested to 150 psig, pressure tested to 650 psig, and qualified to UL 1995 burst test at 1980 psig.

· Optional Pre-Coated Aluminum-Fin Condenser Coils (3-phase models only):

· Shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments.

· Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube.

· Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.

· Corrosion durability of fin stock shall be confirmed through testing to be no less than 1000 hours salt spray per ASTM B117-90.

· Corrosion durability of fin stock shall be confirmed through testing to have no visible corrosion after 48 hour immersion in a room temperature solution of 5% salt, 1% acetic acid.

· Fin stock coating shall pass 2000 hours of the following: one week exposure in the prohesion chamber followed by one week of accelerated ultraviolet light testing. Prohesion chamber: the solution shall contain 3.5% sodium chloride and 0.35% ammonium sulfate. The exposure cycle is one hour of salt fog application at ambient followed by one hour drying at 95°F (35°C).

· Optional Copper-Fin Evaporator and Condenser Coils (3-phase models only):

· Shall be constructed of copper fins mechanically bonded to copper tubes and copper tube sheets.

· Galvanized steel tube sheets shall not be acceptable.

· A polymer strip shall prevent coil assembly from contacting the sheet metal coil pan to minimize potential for galvanic corrosion between coil and pan.

· Optional E-Coated Aluminum-Fin Evaporator and Condenser Coils (3-phase models only):

· Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins.

· Coating process shall ensure complete coil encapsulation of tubes, fins and headers.

· Color shall be high gloss black with gloss per ASTM D523-89.

· Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges.

· Superior hardness characteristics of 2H per ASTM D3363-92A and cross-hatch adhesion of 4B-5B per ASTM D3359-93.

· Impact resistance shall be up to 160 in.-lb (ASTM D2794-93).

· Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D224-92 and ASTM D870-92).

· Corrosion durability shall be confirmed through testing to be no less than 6000 hours salt spray per ASTM B117-90.

· Optional E-Coated Aluminum-Fin, Aluminum Tube Condenser Coils:

· Shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers.

· Coating process shall ensure complete coil encapsulation, including all exposed fin edges.

· E-coat thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas, including fin edges, shall be provided.

· Shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross-hatch adhesion of 4B-5B per ASTM D3359-02.

· Shall have superior impact resistance with no cracking, chipping or peeling per NSF/ANSI 51-2002 Method 10.2.

· (23 81 19.13.J) Refrigerant Components

· Refrigerant circuit shall include the following control, safety, and maintenance features:

· Thermostatic Expansion Valve (TXV) shall help provide optimum performance across the entire operating range. Shall contain removable power element to allow change out of power element and bulb without removing the valve body.

· Refrigerant filter drier.

· Service gauge connections on suction and discharge lines.

· Pressure gauge access through a specially designed access port in the top panel of the unit.

· There shall be gauge line access port in the skin of the rooftop, covered by a black, removable plug.

· The plug shall be easy to remove and replace.

· When the plug is removed, the gauge access port shall enable maintenance personnel to route their pressure gauge lines.

· This gauge access port shall facilitate correct and accurate condenser pressure readings by enabling the reading with the compressor access panel on.

· The plug shall be made of a leak proof, UV-resistant, composite material.

· Compressors:

· Unit shall use one fully hermetic, scroll compressor for each independent refrigeration circuit.

· Models shall be available with single compressor/single stage cooling designs on 04-07 models, single compressor/2-stage cooling on 07 size, and 2 compressor/2-stage cooling models on 08-12 sizes.

· Compressor motors shall be cooled by refrigerant gas passing through motor windings.

· Compressors shall be internally protected from high discharge temperature conditions.

· Compressors shall be protected from an over-temperature and over-amperage conditions by an internal, motor overload device.

· Compressor shall be factory mounted on rubber grommets.

· Compressor motors shall have internal line break thermal, current overload and high pressure differential protection.

· Crankcase heaters shall be utilized on all models to protect compressor with specific refrigerant charge.

· (23 81 19.13.K) Filter Section

· Filters access is specified in the unit cabinet section of this specification.

· Filters shall be held in place by a preformed slide out filter tray, facilitating easy removal and installation.

· Shall consist of factory-installed, low velocity, throw-away 2-in. thick fiberglass filters.

· Filters shall be standard, commercially available sizes.

· Only one size filter per unit is allowed.

· (23 81 19.13.L) Evaporator Fan and Motor

· Evaporator fan motor:

· Shall have permanently lubricated bearings.

· Shall have inherent automatic-reset thermal overload protection or circuit breaker.

· Shall have a maximum continuous bhp rating for continuous duty operation; no safety factors above that rating shall be required.

· Belt-driven evaporator fan:

· Belt drive shall include an adjustable-pitch motor pulley and belt break protection system.

· Shall use rigid pillow block bearing system with lubricate fittings at are accessible or lubrication line.

· Blower fan shall be double-inlet type with forward-curved blades.

· Shall be constructed from steel with a corrosion resistant finish and dynamically balanced.

· Standard on all 04-14 size models with Humidi-MiZer option.

· (23 81 19.13.M) Condenser Fans and Motors

· Condenser fan motors:

· Shall be a totally enclosed motor.

· Shall use permanently lubricated bearings.

· Shall have inherent thermal overload protection with an automatic reset feature.

· Shall use a shaft down design on all sizes.

· Condenser fans:

· Shall be a direct driven propeller type fan.

· Shall have aluminum blades riveted to corrosion resistant steel spiders and shall be dynamically balanced.

·  (23 81 19.13.N) Special Features Options and Accessories

· EnergyX® and Economizer:

· System Description:

· One-piece EnergyX (Energy Recovery Ventilation) unit is an electrically controlled ventilation air pre-conditioner utilizing an AHRI 1060 certified Energy Recovery Cassette to reduce the cooling and heating loads placed on the primary HVAC unit by untreated outdoor air. Building exhaust air shall be introduced to the EnergyX unit through ductwork. Unit shall be designed as a factory-installed option to be used with WeatherMaster 48HC units for use in vertical return applications only.

· Quality Assurance:

· Unit shall be designed in accordance with UL Standard 1995.

· Energy Recovery unit shall be ETL tested and certified.

· Rooftop unit and Energy Recovery unit shall be ETL certified as one single system.

· Roof curb or curb extension shall be designed to conform to NRCA Standards.

· Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

· Unit casing shall be capable of withstanding ASTM No. 141 (Method 6061) 500-hour salt spray test.

· Unit shall contain AHRI 1060 certified Energy Recovery Cassette.

· Unit leakage rates shall be capable of meeting ASHRAE Standard 62.1 requirements for use of class-2 exhaust with class-1 ventilation air.

· Products:

· Equipment (Standard): The EnergyX unit shall be a factory assembled, single piece unit. Contained within the unit enclosure shall be all factory wiring with a single, pre-determined point of power input and a single point of 24-volt control wiring.

· Unit Cabinet:

· Unit cabinet shall be constructed of galvanized steel coated with a pre-painted baked enamel finish.

· All models shall have hoods installed over outside air intake and exhaust openings. Outside air hood shall have aluminum water entrainment filters.

· All models have 1-in., 2 pound density fiberglass insulation.

· Hinged access doors with compression latches shall be provided on all units for access to fans and filters. Hinged doors shall be provided with at least one handle capable of being locked.

· Exhaust air stream shall have back-draft dampers to prevent air penetration during off cycles.

· Holes shall be provided in the base rails for rigging shackles to facilitate overhead rigging.

· Blowers:

· Blowers shall be direct drive with variable speed motors.

· Blower wheel shall be made of steel with a corrosion resistant finish. It shall be dynamically balanced, double-inlet type with backward-curved blades.

· Blower shall be mounted on neoprene vibration isolation pads.

· Motor shall be high efficiency and have thermal overload protection.

· Filter Section:

· Standard filter section shall accept commercially available, 2-in. pleated filter(s).

· Controls and Safeties:

· The EnergyX unit shall operate in conjunction with rooftop unit fan.

· Electrical Requirements:

· All unit power wiring shall enter unit cabinet at a single location.

· Energy Recovery Cassette:

· The energy recovery media shall have a minimum of 70% effectiveness at nominal unit airflow.

· Energy wheel performance shall be AHRI Standard 1060 Certified and bear the AHRI Certified Product Seal.

· The energy recovery cassette shall be an UL Recognized component for electrical and fire safety.

· The wheel shall be coated with silica gel desiccant, permanently bonded without the use of binders or adhesives.

· Coated wheels shall be washable with detergent or alkaline coil cleaner and water.

· The silica gel shall not dissolve or deliquesce in the presence of water or high humidity.

· The substrate shall be made of a lightweight polymer and shall not degrade or require additional coatings for application in coastal environments.

· The wheel polymer layers shall be wound continuously with one flat and one structured layer in an ideal parallel plate geometry providing laminar flow and minimum pressure drop.

· The polymer layers shall be captured in a stainless steel wheel frame or aluminum and stainless steel segment frames that provide a rigid and self-supporting matrix.

· Energy recovery wheels greater than 19 inches in diameter shall be provided with removable wheel segments.

· Wheel frame shall be a welded hub, spoke and rim assembly of stainless, plated, and or coated steel and shall be self supporting without the wheel segments in place.

· Wheel segments shall be removable without the use of tools to facilitate maintenance and cleaning.

· Wheel rim shall be continuous rolled stainless steel and the wheel shall be connected to the shaft by means of taper locks.

· Wheel bearings shall provide an L-10 life of 400,000 hours.

· Drive belts of stretch urethane shall be provided for wheel rim drive without the need for external tensioners or adjustment.

· Supply and Exhaust Air Frost Control Option:

· Factory-installed frost protection module shall sense pressure differential across the energy recovery cassette.

· Supply blower shall be shut-off if the pressure differential across the energy recovery cassette exceeds an adjustable set point. Blower shall remain off for an adjustable time period.

· Exhaust blower and wheel shall remain in operation in order to remove any frost build-up on the wheel.

· EnergyX Maintenance Indicator Package:

· A factory-installed switch shall monitor EnergyX blowers and wheel motor amp draw and send a signal to field-supplied 24-v indicator upon amperage surge that maintenance required.

· Filter Maintenance Indicator:

· A factory-installed differential pressure switch shall measure pressure drop across the outside air filter and activate a field-supplied 24-v indicator when airflow is restricted. It shall not interrupt EnergyX operation. Switch set point shall be adjustable.

· EnergyX Free Cooling with Enthalpy and Stop/Jog Control:

· An enthalpy sensor shall prevent the wheel from rotating if the outside air conditions are acceptable for free cooling. Both exhaust and supply blowers will remain on.

· Stop-Jog-Control shall energize the wheel periodically during the free cooling operation of the EnergyX unit to prevent dirt build-up on the wheel.

· Economizer Option:

· The economizer shall be integrated in the energy recovery module and shall allow air to bypass the energy recovery wheel for free cooling and fail safe operation. Tilting wheel mechanisms shall not be allowed.

· The economizer damper shall be motorized with factory installed, 24-volt Belimo actuator.

· The EnergyX unit shall be capable of using the economizer in a free cooling operation.

· The economizer shall utilize enthalpy sensor controls when in the economizer mode.

· CO2 Sensor:

· The modulating airflow energy recovery unit shall be capable of incorporating a CO2 sensor for use with Demand Controlled Ventilation.

· The CO2 sensor shall connect to the base rooftop unit’s digital controller.

· The modulating airflow energy recovery unit shall use at a minimum, a high and low CFM airflow set point when a CO2 sensor is used.

· Roof Curb Extension (HC04-14 sizes with EnergyX) Accessory for use with EnergyX units:

· The energy recovery module shall us the standard rooftop unit rooftop curb.

· Rooftop extensions, support rails or other devices that come in contact with the roof surface to support the energy recovery module shall not be allowed.

· A horizontal adapter curb shall be used to convert vertical return air applications into horizontal return air applications. The supply airflow shall be convertible via the base rooftop unit operation and restrictions.

· Staged Air Volume System (SAV™) for 2-stage cooling models only:

· Evaporator fan motor:

· Shall have permanently lubricated bearings.

· Shall have a maximum continuous bhp rating for continuous duty operation; no safety factors above that rating.

· Shall be Variable Frequency duty and 2-speed control.

· Shall contain motor shaft grounding ring to prevent electrical bearing fluting damage by safely diverting harmful shaft voltages and bearing currents to ground.

· Variable Frequency Drive (VFD). Only available on 2-speed indoor fan motor option (SAV):

· Factory-supplied VFDs qualify, through ABB for a 12-month warranty from date of commissioning or 18 months from date of sale, whichever occurs first.

· Shall be installed inside the unit cabinet, mounted, wired and tested.

· Shall contain Electromagnetic Interference (EMI) frequency protection.

· Insulated Gate Bi-Polar Transistors (IGBT) used to produce the output pulse width modulated (PWM) waveform, allowing for quiet motor operation.

· Self diagnostics with fault and power code LED indicator. Field accessory Display Kit available for further diagnostics and special setup applications.

· RS485 capability standard.

· Electronic thermal overload protection.

· 5% swinging chokes for harmonic reduction and improved power factor.

· All printed circuit boards shall be conformal coated.

· Integrated EconoMi$er® IV, EconoMi$er 2, and EconoMi$er X Low Leak Rate Models. (Factory-installed on 3-phase models only. Field installed on all 3 and 1-phase models.)

· Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.

· Independent modules for vertical or horizontal return configuration shall be available. Vertical return modules shall be available as a factory-installed option.

· Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

· Shall include all hardware and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.

· Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

· Low leak rate models shall be equipped with dampers not to exceed 2% leakage at 1 in. wg pressure differential.

· Economizer controller on EconoMi$er IV models shall be Honeywell W7212 that provides:

· Combined minimum and DCV maximum damper position potentiometers with compressor staging relay.

· Functions with solid state analog enthalpy or dry bulb changeover control sensing.

· LED indicators for: when free cooling is available, when module is in DCV mode, when exhaust fan contact is closed.

· Economizer controller on EconoMi$er X models shall be the Honeywell W7220 that provides: 

· 2-line LCD interface screen for setup, configuration and troubleshooting.

· On-board Fault Detection and Diagnostics (FDD) that senses and alerts when the economizer is not operating properly, per California Title 24.

· Sensor failure loss of communication identification.

· Automatic sensor detection.

· Capabilities for use with multiple-speed indoor fan systems.

· Utilize digital sensors: Dry bulb and Enthalpy.

· Economizer controller on EconoMi$er 2 models with PremierLink™ controller shall be 4-20mA design and controlled by the PremierLink controller. PremierLink controller does not comply with California Title 24 Fault Detection and Diagnostic (FDD) requirements.

· Economizer controller on EconoMi$er 2 models with RTU Open controller shall be a 4-20mA design controlled directly by the RTU Open controller. RTU Open controller meets California Title 24 Fault Detection and Diagnostic (FDD) requirements.

· Shall be capable of introducing up to 100% outdoor air.

· Shall be equipped with a barometric relief damper capable of relieving up to 100% return air and contain seals that meet ASHRAE 90.1-2016 and IECC-2015 requirements.

· Shall be designed to close damper(s) during loss-of-power situations with spring return built into motor.

· Dry bulb outdoor air temperature sensor shall be provided as standard. Enthalpy sensor is also available on factory-installed only. Outdoor air sensor setpoint shall be adjustable and shall range from 40 to 100°F (4 to 38°C). Additional sensor options shall be available as accessories.

· The economizer controller shall also provide control of an accessory power exhaust unit function. Factory set at 100%, with a range of 0% to 100%.

· The economizer shall maintain minimum airflow into the building during occupied period and provide design ventilation rate for full occupancy.

· Dampers shall be completely closed when the unit is in the unoccupied mode.

· Economizer controller shall accept a 2 to 10 Vdc CO2 sensor input for IAQ/DCV control. In this mode, dampers shall modulate the outdoor air damper to provide ventilation based on the sensor input.

· Compressor lockout temperature on W7220 is adjustable from –45°F to 80°F, set at a factory default of 32°F. Others shall open at 35°F (2°C) and close at 50°F (10°C).

· Actuator shall be direct coupled to economizer gear. No linkage arms or control rods shall be acceptable.

· Economizer controller shall provide indications when in free cooling mode, in the DCV mode, or the exhaust fan contact is closed.

· Integrated EconoMi$er2, and EconoMi$er X Ultra Low Leak Rate Models. (Factory-installed on 3 phase models only. Field-installed on all 3 and 1 phase models):

· Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.

· Independent modules for vertical or horizontal return configuration shall be available. Vertical return modules shall be available as a factory-installed option.

· Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

· Shall include all hardware and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.

· Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

· Ultra low leak design meets California Title 24 section 140.4 and, ASHRAE 90.1-2016 and IECC-2015 requirements for 4 cfm per sq. ft. on the outside air dampers and 10 cfm per sq. ft. on the return dampers.

· Economizer controller on EconoMi$er X models shall be the Honeywell W7220 that provides:

· 2-line LCD interface screen for setup, configuration and troubleshooting.

· On-board Fault Detection and Diagnostics (FDD) that senses and alerts when the economizer is not operating properly, per California Title 24.

· Sensor failure loss of communication identification.

· Automatic sensor detection.

· Capabilities for use with multiple-speed indoor fan systems.

· Utilize digital sensors: Dry bulb and Enthalpy.

· Economizer controller on EconoMi$er 2 models with RTU Open controller shall be a 4-20mA design controlled directly by the RTU Open controller. RTU Open controller meets California Title 24 Fault Detection and Diagnostic (FDD) requirements.

· Shall be capable of introducing up to 100% outdoor air.

· Shall be equipped with a barometric relief damper capable of relieving up to 100% return air and contain seals that meet ASHRAE 90.1-2016 and IECC-2015 requirements.

· Shall be designed to close damper(s) during loss-of-power situations with spring return built into motor.

· Dry bulb outdoor air temperature sensor shall be provided as standard. Enthalpy sensor is also available on factory-installed only. Outdoor air sensor setpoint shall be adjustable and shall range from 40°F to 100°F (4°F to 38°C). Additional sensor options shall be available as accessories.

· The economizer controller shall also provide control of an accessory power exhaust unit function. Factory set at 100%, with a range of 0% to 100%.

· The economizer shall maintain minimum airflow into the building during occupied period and provide design ventilation rate for full occupancy.

· Dampers shall be completely closed when the unit is in the unoccupied mode.

· Economizer controller shall accept a 2-10 Vdc CO2 sensor input for IAQ/DCV control. In this mode, dampers shall modulate the outdoor air damper to provide ventilation based on the sensor input.

· Compressor lockout temperature on W7220 is adjustable from –45°F to 80°F, set at a factory default of 32°F. Others shall open at 35°F (2°C) and closes at 50°F (10°C).

· Actuator shall be direct coupled to economizer gear. No linkage arms or control rods shall be acceptable.

· Economizer controller shall provide indications when in free cooling mode, in the DCV mode, or the exhaust fan contact is closed.

· Two-Position Damper (Factory-installed on 3 Phase Models Only. Field-installed on all 3 and 1 Phase Models)

· Damper shall be a Two-Position Damper. Damper travel shall be from the full closed position to the field adjustable %-open setpoint.

· Damper shall include adjustable damper travel from 25% to 100% (full open).

· Damper shall include single or dual blade, gear driven dampers and actuator motor.

· Actuator shall be direct coupled to damper gear. No linkage arms or control rods shall be acceptable.

· Damper will admit up to 100% outdoor air for applicable rooftop units.

· Damper shall close upon indoor (evaporator) fan shutoff and/or loss of power.

· The damper actuator shall plug into the rooftop unit’s wiring harness plug. No hard wiring shall be required.

· Outside air hood shall include aluminum water entrainment filter.

· Not available with Staged Air Volume (SAV-) models.

· Manual Damper:

· Manual damper package shall consist of damper, air inlet screen, and rain hood which can be preset to admit up to 25 or 50% outdoor air for year round ventilation.

· Not available with Staged Air Volume (SAV) models.

· Humidi-MiZer® Adaptive Dehumidification System (3-phase models only):

· The Humidi-MiZer adaptive dehumidification system shall be factory-installed and shall provide greater dehumidification of the occupied space by two modes of dehumidification operations in addition to its normal design cooling mode:

· Subcooling mode further sub cools the hot liquid refrigerant leaving the condenser coil when both temperature and humidity in the space are not satisfied.

· Hot gas reheat mode shall mix a portion of the hot gas from the discharge of the compressor with the hot liquid refrigerant leaving the condenser coil to create a two-phase heat transfer in the system, resulting in a neutral leaving air temperature when only humidity in the space is not satisfied.

· Includes head pressure controller.

· Head Pressure Control Package (Motormaster®):

· Controller shall control coil head pressure by condenser-fan speed modulation or condenser-fan cycling and wind baffles.

· Shall consist of solid-state control and condenser-coil temperature sensor to maintain condensing temperature at outdoor ambient temperatures down to –20°-F (–29°-C).

· Low Ambient Controller (Factory-installed only):

· Controller shall control coil head pressure by condenser-fan speed modulation or condenser-fan cycling and wind baffles.

· Shall consist of solid-state control and condenser-coil temperature sensor to maintain condensing temperature at outdoor ambient temperatures down to 0°-F (–18°-C). (Not available on 11 size models as standard unit cooling operation down to 0°-F /–18°-C).

· Propane Conversion Kit:

· Package shall contain all the necessary hardware and instructions to convert a standard natural gas unit for use with liquefied propane, up to 2000 ft (610m) elevation.

· Additional accessory kits may be required for applications above 2000 ft (610m) elevation.

· Flue Shield (04-12 models only):

· Flue shield shall provide protection from the hot sides of the gas flue hood.

· Condenser Coil Hail Guard Assembly (Factory-installed option on 3-phase models. Field-installed on all 3 and 1 phase models):

· Shall protect against damage from hail.

· Shall be of louvered style.

· Unit-Mounted, Non-Fused Disconnect Switch:

· Switch shall be factory-installed, internally mounted.

· National Electric Code (NEC) and UL or ETL approved non-fused switch shall provide unit power shutoff.

· Shall be accessible from outside the unit.

· Shall provide local shutdown and lockout capability.

· Sized only for the unit as ordered from the factory. Does not accommodate field-installed devices.

· HACR Breaker:

· These manual reset devices provide overload and short circuit protection for the unit. Factory wired and mounted with the units, with access cover to help provide environmental protection. On 575V applications, HACR breaker can only be used with WYE power distribution systems. Use on Delta power distribution systems is prohibited.

· Sized only for the unit as ordered from the factory. Does not accommodate field-installed devices.

· Convenience Outlet:

· Powered convenience outlet. (Not available on single phase models):

· Outlet shall be powered from main line power to the rooftop unit.

· Outlet shall be powered from line side or load side of disconnect by installing contractor, as required by code. If outlet is powered from load side of disconnect, unit electrical ratings shall be UL certified and rated for additional outlet amperage.

· Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.

· Outlet shall include 15 amp GFI receptacles with independent fuse protection.

· Voltage required to operate convenience outlet shall be provided by a factory-installed step down transformer.

· Outlet shall be accessible from outside the unit.

· Outlet shall include a field-installed “Wet in Use” cover.

· Factory-installed non-powered convenience outlet:

· Outlet shall be powered from a separate 115-120v power source.

· A transformer shall not be included.

· Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.

· Outlet shall include 15 amp GFI receptacles.

· Outlet shall be accessible from outside the unit.

· Outlet shall include a field-installed “Wet in Use” cover.

· Field-installed non-powered convenience outlet:

· Outlet shall be powered from a separate 115-120v power source.

· A transformer shall not be included.

· Outlet shall be field-installed and internally mounted with easily accessible 115-v female receptacle.

· Outlet shall include 20 amp GFI receptacles. This kit provides a flexible installation method which allows code compliance for height requirements of the GFCI outlet from the finished roof surface as well as the capability to relocate the outlet to a more convenient location.

· Outlet shall be accessible from outside the unit.

· Outlet shall include a field-installed “Wet in Use” cover.

· Flue Discharge Deflector:

· Flue discharge deflector shall direct unit exhaust vertically instead of horizontally.

· Deflector shall be defined as a “natural draft” device by the National Fuel and Gas (NFG) code.

· Thru-the-Base Connectors:

· Kits shall provide connectors to permit gas and electrical connections to be brought to the unit through the unit basepan.

· Minimum of four connection locations per unit.

· Propeller Power Exhaust:

· Power exhaust shall be used in conjunction with an integrated economizer.

· Independent modules for vertical or horizontal return configurations shall be available.

· Horizontal power exhaust shall be mounted in return ductwork.

· Power exhaust shall be controlled by economizer controller operation. Exhaust fans shall be energized when dampers open past the 0 to 100% adjustable setpoint on the economizer control.

· Roof Curbs (Vertical):

· Full perimeter roof curb with exhaust capability providing separate air streams for energy recovery from the exhaust air without supply air contamination.

· Formed galvanized steel with wood nailer strip and shall be capable of supporting entire unit weight.

· Permits installation and securing of ductwork to curb prior to mounting unit on the curb.

· High Altitude Gas Conversion Kit:

Package shall contain all the necessary hardware and instructions to convert a standard natural gas unit to operate from 2000 to 7000 ft (610 to 2134m) elevation with natural gas or from 0 to 7000 ft (900 to 2134m) elevation with liquefied propane.

· Outdoor Air Enthalpy Sensor:

The outdoor air enthalpy sensor shall be used to provide single enthalpy control. When used in conjunction with a return air enthalpy sensor, the unit will provide differential enthalpy control. The sensor allows the unit to determine if outside air is suitable for free cooling.

· Return Air Enthalpy Sensor:

The return air enthalpy sensor shall be used in conjunction with an outdoor air enthalpy sensor to provide differential enthalpy control.

· Indoor Air Quality (CO2) Sensor:

· Shall be able to provide demand ventilation indoor air quality (IAQ) control.

· The IAQ sensor shall be available in duct mount, wall mount, or wall mount with LED display. The setpoint shall have adjustment capability.

· Smoke Detectors (factory-installed only):

· Shall be a four-wire controller and detector.

· Shall be environmental compensated with differential sensing for reliable, stable, and drift-free sensitivity.

· Shall use magnet-activated test/reset sensor switches.

· Shall have tool-less connection terminal access.

· Shall have a recessed momentary switch for testing and resetting the detector.

· Controller shall include:

· One set of normally open alarm initiation contacts for connection to an initiating device circuit on a fire alarm control panel.

· Two Form-C auxiliary alarm relays for interface with rooftop unit or other equipment.

· One Form-C supervision (trouble) relay to control the operation of the Trouble LED on a remote test/reset station.

· Capable of direct connection to two individual detector modules.

· Can be wired to up to 14 other duct smoke detectors for multiple fan shutdown applications

· Horn/Strobe Annunciator:

· Provides an audible/visual signaling device for use with factory-installed option or field-installed accessory smoke detectors.

· Requires installation of a field-supplied 24-v transformer suitable for 4.2 VA (AC) or 3.0 VA (DC) per horn/strobe accessory.

· Requires field-supplied electrical box, North American 1-gang box, 2-in. (51 mm) x 4-in. (102 mm).

· Shall have a clear colored lens.

· Winter Start Kit:

· Shall contain a bypass device around the low pressure switch.

· Shall be required when mechanical cooling is required down to 25°F (–4°C).

· Shall not be required to operate on an economizer when below an outdoor ambient of 40°F (4°C).

· Time Guard:

· Shall prevent compressor short cycling by providing a 5-minute delay (±2 minutes) before restarting a compressor after shutdown for any reason.

· One device shall be required per compressor.

· Condensate Overflow Switch (for units with electro-mechanical controls only):

This sensor and related controller monitors the condensate level in the drain pan and shuts down compression operation when overflow conditions occur. It includes:

· Indicator light — solid red (more than 10 seconds on water contact — compressors disabled), blinking red (sensor disconnected).

· 10 second delay to break — eliminates nuisance trips from splashing or waves in pan (sensor needs 10 seconds of constant water contact before tripping).

· Disables the compressor(s) operation when condensate plug is detected, but still allows fans to run for economizer.

· Hinged Access Panels:

· Shall provide easy access through integrated quarter turn latches.

· Shall be on major panels of — filter, control box, fan motor and compressor

· Display Kit for Variable Frequency Drive:

· Kit allows the ability to access the VFD controller programs to provide special setup capabilities and diagnostics.

· Kit contains display module and communication cable.

· Display Kit can be permanently installed in the unit or used on any SAV™ system VFD controller as needed.

· Foil faced insulation:

· Throughout unit cabinet air stream, non-fibrous and cleanable foil faced insulation is used.

· California OSHPD Seismic Certification Label:

· Units meet the seismic capacity requirements of the International Code Council Evaluation Service (ICC-ES) document AC156 (Acceptance Criteria for Seismic Qualification by Shake--Table Testing of Nonstructural Components and Systems) and per International Building Code (IBC 2009) at an SDS (g) value of 2.00 z/h=1.0, Ip=1.5 and certified by independent structural engineers.

· Units shall include a certification label that meets the CA OSHPD Special Seismic Certification pre-approval labeling requirements on the external chassis of the unit.

�	LonWorks is a registered trademark of Echelon Corporation.





�BACnet is a registered trademark of ASHRAE (American Society of Heating, Refrigerating and Air-Conditioning Engineers).





�Modbus is a registered trademark of Schneider Electric.





�ENERGY STAR is a registered trademark of the U.S. Environmental Protection Agency.








2


3

