
Two-Stage Water Source Heat Pumps with Puron® Refrigerant (R-410A)

HVAC Guide Specifications

Size Range:
 18,500 to 78,700 Btuh Cooling Capacity



 14,400 to 84,000 Btuh Heating Capacity

Carrier Model Number:
 50PTH, 50PTV

· General

· SYSTEM DESCRIPTION

· Single-package horizontally and vertically mounted water source heat pump with Puron refrigerant (R-410A) and electronic controls.

· Equipment shall be completely assembled, piped and internally wired. Capacities and characteristics as listed in the schedule and the guide specifications that follow.

· QUALITY ASSURANCE

· All equipment shall be rated and certified in accordance with ANSI/AHRI/ASHRAE/ISO (American National Standard Institute/Air-Conditioning, Heating and Refrigeration Institute/American Society of Heating, Refrigerating, and Air-Conditioning Engineers/International Organization for Standardization) 13256-1, latest edition, and ETL listed to UL (Underwriters Laboratories) standard 1995. The units shall have AHRI/ISO and ETL labels.

· All units shall be factory tested in all operating modes and safety switch operation shall be verified. Quality control system shall automatically perform via computer: triple leak check, pressure tests, evacuate and accurately charge system, perform detailed heating and cooling mode tests, and quality cross check all operational and test conditions to pass/fail data base. 

NOTE: If unit fails on any cross check, system shall not allow unit to ship. 

· Serial numbers will be recorded by factory and furnished to contractor on report card for ease of unit warranty status. Units shall be prewired and precharged in factory.

· Product

· EQUIPMENT

· General:

Units shall be designed to operate throughout the range of entering fluid temperature of 40°F to 120°F in the cooling mode and 20°F to 90°F in the heating mode. Equivalent units from other manufacturers can be proposed provided approval to bid is given 10 days prior to bid closing. 

· Basic Construction:

Units shall have the airflow arrangement as shown on the plans. If units with these arrangements are not used, the contractor supplying the water source heat pumps is responsible for any extra costs incurred by other trades and must submit detailed mechanical drawings showing ductwork requirements and changes or relocation of any other mechanical or electrical system. If other arrangements make servicing difficult the contractor must provide access panels and clear routes to ease service. The architect must approve all changes 10 days prior to bid.

1. All units shall have stainless steel drain pans to comply with this project’s IAQ (indoor air quality) requirements. No exceptions shall be allowed.

2. All water source heat pumps shall be fabricated from heavy gage G-90 galvanized posts and panels. All interior surfaces shall be lined with 1/2 in. thick, 1.5 lb/cu ft dual-density insulation for thermal insulation and acoustic attenuation. Insulation must be non-combustible, non-hydroscopic and anti-fungal. Insulation must meet NFPA (National Fire Protection Association) 90A and 90B for fire protection as well as Fire Hazard classification 25/50 (per ASTM [American Society for Testing and Materials] E84 and UL 723 and CAN/ULC S102-M88), ASTM C1071, erosion requirements of UL181 and be certified to meet GREENGUARD indoor air quality standards for low emitting products. One blower access panel and two compressor compartment access panels shall be removable with supply and return air ductwork in place.

3. Unit shall have a floating basepan consisting of a 1/2 in. thick high density rubber pad between the compressor base plate and the unit basepan to prevent transmission of vibration to the structure.

4. All units shall have a factory-installed 4-sided filter rack capable of accepting either one or 2 in. filters. Units shall have a 1 in. thick throwaway type fiberglass filter as standard. The filter rack shall incorporate a 1 in. duct flange. The contractor shall purchase one spare set of filters and replace factory-shipped filters upon completion of start-up.

5. Cabinets shall have separate holes and knockouts for entrance of line voltage and low voltage control wiring. Supply and return water connections shall be brass FPT fittings and shall be securely mounted flush to the cabinet allowing for connection to a flexible hose without the use of a back-up wrench. Water connections which protrude through the cabinet shall not be allowed.

6. Hanging brackets shall be provided as standard for horizontal units.

7. All units shall have condensate overflow switch, air-coil and water-coil Freeze sensor as standard.

· Access Panels:

All units (horizontal and vertical) must have a minimum of three access panels for serviceability of compressor compartment. Units having only one access panel to compressor, heat exchangers, expansion device, or refrigerant piping shall not be acceptable.

· Unit Removal:

Contractor must ensure that units can be easily removed for servicing and coordinate locations of electrical conduit and lights with the electrical contractor.

· Compressor:

1. Two-stage hermetic compressor specifically designed for heat pump operation and shall be internally protected with thermal overload protection and mounted on rubber vibration isolators.

2. The compressor shall have a dual level vibration isolation system.

3. Compressor shall be located in an insulated compartment away from airstream to minimize sound transmission.

· Fan and Motor Assembly:

1. Units shall have a direct-drive centrifugal fan. A constant torque electronically commutated motor shall be used for premium efficiency. These motors shall feature 5 pre-programmed torque settings that can be changed in the field to match design requirements. 460-v, 3 ph, 60 Hz units with these motors must be able to operate without the need for a neutral wire for the motor.

2. The fan motor shall be isolated from the housing by torsionally flexible isolation. 

3. The fan and motor assembly must be capable of overcoming the external static pressures as shown on the schedule. External static pressure rating of the unit shall be based on a wet coil. Ratings based on a dry coil shall NOT be acceptable.

4. All units shall have removable blower inlet ring as standard for ease of service and maintenance.

5. Optional pre-programmed high efficiency constant airflow ECM (electronically commutated motor) fan motor.

· Refrigerant Circuit:

1. Units shall use R-410A refrigerant. All units shall have a factory sealed and fully charged refrigerant circuit with the following components:

2. Bi-directional refrigerant metering thermal expansion valves. Finned tube refrigerant-to-air heat exchanger not exceeding 14 fins per inch. Refrigerant-to-air heat exchangers shall utilize enhanced aluminum fins and rifled copper tube construction rated to withstand 600 psig refrigerant working pressure. All air coils shall have non-ferrous aluminum end plates.

3. Optional coated coils to have copper tubes with tin coating and aluminum fins coated to pass 1000 hour ASTM B117 salt fog testing.

4. Reversing valve. Reversing valves shall be 4-way solenoid activated refrigerant valves which shall fail to the heating operation should the solenoid fail to function. Reversing valves which fail to the cooling operation shall not be allowed. 

5. Coaxial (tube in tube) refrigerant-to-water heat exchanger. Refrigerant-to-water heat exchangers shall be insulated and with copper inner water tube and steel outer refrigerant tube design rated to withstand 600 psig working refrigerant pressure and 400 psig working water pressure. Shell and tube style refrigerant-to-water heat exchangers shall be treated as pressure vessels and shall require refrigerant pressure relief valves piped to the exterior of the building. The contractor supplying the water source heat pumps with shell and tube heat exchangers shall be responsible for any additional installation costs. Brazed plate water-to-refrigerant heat exchangers shall require additional centrifugal separators added to the supply water piping at each unit. Each separator shall have an automated clean out valve piped to a waste line. The contractor supplying water source heat pumps with brazed plate heat exchangers shall be responsible for any additional costs. 

6. Optional cupronickel water coil to have the refrigerant to water heat exchanger made of a cupronickel inner water tube construction.

7. Safety controls including both a high pressure and low pressure switch. Temperature sensors shall not replace these safety switches. 

8. Access fittings shall be factory-installed on high and low pressure refrigerant lines to facilitate field service.

9. Activation of any safety device shall prevent compressor operation via a lockout circuit. The lockout circuit shall be reset at the thermostat or at the contractor supplied disconnect switch. Units which may be reset at the disconnect switch only shall not be acceptable.

· Controls and Safeties:

1. Electrical:

A control box shall be located within the unit and shall contain a transformer, controls for the compressor, reversing valve and fan motor operation and shall have a terminal block for low voltage field wiring connections. The transformer shall be rated for a minimum 75 va. All units shall be nameplated for use with time delay fuses or HACR (Heating, Air-Conditioning, and Refrigeration) circuit breakers. Unit controls shall be 24-v.

2. Solid-State Safety Circuit:

All units shall have a solid-state safety control circuit with the following features:

a. Anti-short cycle time delay on compressor operation.

b. Random start on power up mode.

c. Brown out/surge/power interruption protection.

d. Low pressure switch 120-second bypass timer.

e. Shutdown on the following fault indications:

1) High or low refrigerant pressure safety switches inputs.

2) Freeze sensors shall monitor refrigerant temperature to the water coil in the heating mode and refrigerant coil in the cooling mode.

3) Condensate sensor input.

f. Alarm output which closes for selectable dry contact closure or 24 vac remote fault indication.

g. Alarm output selectable for constant output for general alarm notification, or pulse out-put for annunciation of the specific fault alarm. 

h. Selectable reset of unit at thermostat or dis-connect.

i. Automatic intelligent reset. Unit shall automatically reset after a safety shutdown and restart after the anti-short cycle timer and random start timer expire. Should a fault re-occur within 60 minutes after reset, then a permanent lockout will occur. Reset attempts shall be selectable for either 2 or 4 tries. A condensate overflow will place the unit in an immediate hard lockout.

j. Ability to defeat time delays for servicing.

k. A light-emitting diode (LED) to indicate safety alarms. The LED shall annunciate the following alarms:

1) High refrigerant pressure,

2) Low refrigerant pressure,

3) Low refrigerant temperature to the water coil in the heating operation,

4) High level of condensate in the drain pan,

5) Brown out/surge/power interruption.

l. The LED will display each fault condition as soon as the fault occurs. If a permanent lockout occurs, then the fault LED will display the type of fault until the unit is reset.

m. UL listed, UL Canada listed, and RFI (radio frequency interference), ESD (electrostatic discharge), and transient protected.

n. Freeze Protection: 

A freeze stat shall sense the entering refrigerant temperature to the coaxial coil (in the heating mode) and shall activate the compressor lockout circuit when the refrigerant temperature drops below either 15°F or 30°F. The factory default is 30°F and the temperature setting may be set at 15°F by cutting the resistor (R42) located above the dip switch. The freeze stat may not provide protection in case of loss of flow in the heating mode. A flow switch or pressure differential switch is recommended to prevent unit operation in case of loss of flow. A second freeze sensor shall be mounted at the refrigerant inlet to the air coil. Should the refrigerant temperature drop below 30°F the unit will go into a soft lockout.

3. Deluxe D Controls:

Optional electronic Deluxe D control shall have all the features of the Complete C control with the following additional features:

a. 75 va transformer.

b. Energy Management Switch to enable remote operation of WSHP.

c. Boilerless system control can switch automatically to electric heat at low loop water temperature.

d. Phase loss and reversal protection shall be provided on the unit to protect the compressor from operating in reverse rotation.

e. Auxiliary pump relay to enable a pump operation when calling for compressor operation.

4. WSHP Open Multiple Protocol Controls:

a. Units shall have all the features above (Complete C Board) and the state of the art WSHP Open multiple protocol interface board. All point objects will have the ability to be viewed in the Equipment Touch™, System Touch™ or field assistant user interface. The following points must be available at a central or remote computer location:

1) Space temperature

2) Leaving water temperature

3) Discharge air temperature

4) Command of space temperature set point

5) Cooling status

6) Heating status

7) Low temperature sensor alarm

8) High pressure switch alarm

9) Fan on/off position of space thermostat

10) Unoccupied/occupied command

11) Cooling demand

12) Heating demand

13) Fan “ON/AUTO” command

14) Fault prevention with auto reset

15) Itemized fault code viewed with Equipment Touch interface

b. Additional WSHP Open multiple protocol control features shall include:

1) Three-speed fan control. Controller shall automatically, based upon space temperature input, operate the fan at the lowest of 3 selectable speeds to achieve space temperature set point.

2) Two-position OA (outdoor air) damper

3) Modulating OA damper with DCV (demand controlled ventilation)

4) Hot gas reheat solenoid valve

5) Two-position water economizer control

6) Modulating water economizer control

7) Single-stage electric auxiliary heat

8) Power fail restart delay

9) 2-stage compression control

5. Multiple-protocol WSHP Open controller remote ZS sensors for DDC control options. Only Carrier ZS sensors can be used with the WSHP Open controller. Sensors are available as follows, and all sensors below offer monitoring of space temperature only, or space temperature and CO2, or space temperature and humidity, or space temperature and CO2 and humidity.

a. ZS Standard sensor with a communication port.

b. ZS Plus sensor with communication port, occupancy status indicator, local occupancy override and setpoint adjustment.

c. ZS Pro sensor with communication port, occupancy status indicator, local occupancy override, setpoint adjustment, LCD display, alarm indicator and fan speed control.

d. ZS Pro-F sensor with communication port, occupancy status indicator, local occupancy override, setpoint adjustment, LCD display, alarm indicator, fan speed control, cooling/heating/fan only mode control and F to C conversion.

· Piping:

1. Supply and return water connections shall be copper FPT fittings and shall be securely mounted flush to the cabinet corner post allowing for connection to a flexible hose without the use of a back-up wrench.

2. All water connections and electrical knockouts must be in the compressor compartment corner post so as to not interfere with the serviceability of unit. Contractor shall be responsible for any extra costs involved in the installation of units that do not have this feature.

· Factory-Installed Options:

1. Mute package to include compressor blanket. 

2. Hot gas reheat to be installed and controlled by a humidistat connected to the H terminal and shall start the unit in the reheat mode should the humidity be above set point once the thermostat control is satisfied. Sensible cooling or heating requirements shall take precedence over hot gas reheat. 

3. A non-fused factory-mounted disconnect shall be installed on the unit.

4. A two-way solenoid water valve shall be factory mounted in the interior of the unit. The valve shall cycle open whenever there is a call for compressor operation and the valve shall be equipped with an end switch. The two-way motorized solenoid valve is rated for a 300 psig working pressure.

5. An internal secondary pump shall be installed in the unit, 208/230 volts only.

6. Factory-installed UL listed electric heater packages shall be available for the units. Available only on vertical units with top discharge and horizontal units with end blow configuration.

7. Closed cell foam (CCF) shall be installed on interior surfaces of water source heat pump and shall meet the density and compression requirements of ASTM D 1056, the water absorption requirements of ASTM D-1667 and the tensile and elongation requirements of ASTM D-412. Closed cell foam shall meet the flammability requirements of FMVSS302 and UL 94.

· Accessories:

1. Hose Kits and Valves: 

All units shall be connected to main water supply and return headers with hoses. The hoses shall be 2 ft long, braided stainless steel rated to 400 psig at 265°F. Hoses may contain optional ball valves with P/T (pressure/temperature) ports, Y strainers with blow down valves and/or autoflow regulators as specified in the schedule.

2.  Electric Duct Heaters:

a. Duct heater shall be slip-in type and shall be UL approved for zero clearance to combustible surfaces. The heater shall bear a UL/CSA (Canadian Standards Association) label. Control panel and element housing shall be constructed of heavy gauge galvanized steel. All heating elements shall be made of nickel/chromium resistance wire with ends terminated by means of staking and heliarc welding to machine screws. Heating element support structure shall consist of galvanized steel wire formed and constructed to support ceramic bushings through which the heating element passes. Control cabinet shall be constructed of heavy gauge galvanized steel with multiple knockouts for field wiring. Control cabinet shall have a solid cover also of heavy gauge galvanized steel and held in place with hinges and tool-release latches. 

b. Duct heater shall be supplied with primary over temperature protection by built in disc type automatic reset thermal cutouts and secondary over temperature protection by built in disc type manually resettable thermal cutouts. These devices must function independently of one another and are not acceptable if series connected in the control circuit wiring. A disconnecting magnetic control circuit is required. All duct heaters will require either a fan interlock circuit or an airflow switch.

c. Over-current protection by means of factory-installed fusing within the control cabinet shall be provided for heaters rated at more than 48 amps. Heating elements shall be subdivided and fused accordingly.

d. All wiring, component sizing, component spacing and protective devices within the control cabinet shall be factory-installed and comply with NEC (National Electrical Code) and UL standards. All heaters shall function properly with a 60 Hz power supply. 
e. A wiring diagram depicting layout and connections of electrical components within the control cabinet shall be affixed to the inside of the control cabinet cover.

f. A rating plate label shall be affixed to the exterior of the control cabinet cover which states model number, serial number, volts, amps, phase, frequency, control volts, volt-amps and minimum airflow requirements.

1


1

