
Packaged Water Source Heat Pumps

Engineering Guide Specifications 

Size Range: 2 to 6 Nominal Tons
 

Carrier Model Number: 50WT

· General

· SYSTEM DESCRIPTION

· Install water source heat pumps, as indicated on the plans with capacities and characteristics as listed in the schedule and the specifications that follow. Units shall be horizontal or vertical configurations. All equipment shall be rated and certified in accordance with ANSI/AHRI/ASHRAE/ISO (American National Standard Institute/Air-Conditioning, Heating and Refrigeration Institute/American Society of Heating, Refrigerating, and Air-Conditioning Engineers/International Organization for Standardization) 13256-1. All equipment shall be tested, investigated, and determined to comply with the requirements of the standards for Heating and Cooling Equipment UL-60335-2-40 for the United States and CSA C22.2 No. 60335-2-40 for Canada, by Intertek Testing Laboratories (ETL). The units shall have AHRI/ISO and ETL-US-C labels.

· Units shall be supplied completely factory built and capable of operation with an entering water temperature range from 20 to 110°F. Quality control system shall automatically perform via computer: triple leak check, pressure tests, evacuation and accurate charging of system, detailed heating and cooling mode tests, and quality cross checking all operational and test conditions to pass/fail criteria.

· Units shall be individually packaged on wooden skids with protective corner posts and plastic stretch wrapping for maximum protection.

· QUALITY ASSURANCE

· All equipment listed in this section must be rated in accordance with ANSI/AHRI/ASHRAE/ISO 13256-1 performance standard, latest edition. The applicable units shall have an AHRI/ISO label. Standard cabinet panel insulation shall meet NFPA (National Fire Protection Association) 90A requirements, air erosion and mold growth limits of UL-181, stringent fungal resistance test per ASTM-C1071 and ASTM G21 and zero level bacteria growth per ASTM (American Society for Testing and Materials) G22.

· All units shall be factory tested in all operating modes and safety switch operation shall be verified.

· Serial numbers will be recorded by the factory and furnished to the contractor for ease of unit warranty status. 

· WARRANTY

The manufacturer shall warranty the unit's parts for a period of 12 months from start-up or 18 months from shipping (whichever occurs first). The manufacturer shall warranty the compressor (parts only) for a period of up to 5 years from shipping.

[Optional] Units shall have the option for an extended warranty.

· Product

· EQUIPMENT

· General: Units shall be completely assembled, piped, internally wired, and fully charged at the factory. 

· Basic Construction:

1. The cabinet shall be fabricated from heavy gauge galvanized steel for superior corrosion protection. All interior surfaces shall be lined with 1/2 in. thick, multi-density, coated, fiberglass insulation. Insulation must be non-combustible, non‑hydroscopic and anti-fungal. Insulation must meet NFPA 90A and 90B for fire protection as well as Fire Hazard classification 25/50 (per ASTM E84 and UL 723 and CAN/ULC S102-M88), ASTM C1071, erosion requirements of UL181 and be certified to meet GREENGUARD indoor air quality standards for low emitting products. One blower access panel and two compressor compartment access panels shall be removable with supply and return air ductwork in place. 

2. [Optional] Closed Cell Foam (CCF): CCF shall be installed on interior surfaces of water source heat pump and shall meet the density and compression requirements of ASTM D 1056, the water absorption requirements of ASTM D-1667 and the tensile and elongation requirements of ASTM D-412. Closed cell foam shall meet the flammability requirements of FMVSS302, UL94 and ASTM E84.

3. Units shall have the following airflow arrangements available. The contractor shall be responsible for all extra costs incurred as a result of the unavailability of these airflow arrangements. 

a. Horizontal units: Left Return/Right Discharge, Left Return/Back Discharge, Right Return/Left Discharge, Right Return/Back Discharge. Horizontal units shall have a fully field convertible discharge from back to side or side to back. The discharge conversion shall require no additional components. 

b. Vertical units: Left Return/Top Discharge, Right Return/Top Discharge.

4. All units shall have a stainless-steel drain pan as standard to comply with this project’s IAQ (indoor air quality) requirements. Painted steel or plastic is not acceptable. Drain pan must include a condensate overflow safety switch that will shut the unit down in an overflow event.

5. Unit shall have a floating compressor or pan consisting of a 1/2 in. thick high density elastomeric pad between the compressor base plate and the unit base pan to prevent transmission of vibration to the structure.

6. Units shall have a 1 in., two-sided filter rack with 1 in. thick throwaway type fiberglass filter as standard. 

7. [Optional] MERV 8 Filters: Units shall have a gasketed 2 in., four-sided filter rack with a pleated MERV 8 filter. The filter rack shall incorporate a 1 in. duct flange. 

8. [Optional] MERV 13 Filters: Units shall have a gasketed 2 in. or 4 in., four-sided filter rack with a pleated MERV 13 filter. The filter rack shall incorporate a 1 in. duct flange.

9. Cabinets shall have separate holes and knockouts for entrance of line voltage and low voltage control wiring. Supply and return water connections shall be brass female pipe thread (FPT) fittings and mounted flush to cabinet exterior. Connections that require a backup wrench or that extrude past the unit corner post are not acceptable. Condensate connection shall be stainless steel female pipe thread fittings. Plastic is not acceptable.

10. [Optional] Selectable Water Connections: Units shall be selectable for either front left or front right water connections. 

11. Hanging brackets shall be provided for horizontal units and supplied with rubber grommets for field installation.

12. [Optional] Ultra Low Leakage Construction: Unit construction shall allow for cabinet air leakage less than 2% of the nominal unit airflow rate.

13. [Optional] Compressor blanket shall be installed in the unit for additional sound attenuation.

14. [Optional] 208/230-1 phase factory-installed UL listed single stage electric heater shall be available for the units. Available only on vertical units with top discharge and horizontal units with back discharge. Units provided with the factory-installed electric heater shall be configured with a dual-point power connection. Specifically, one power leg will supply power to both the fan motor and the electric heater, while the second power leg will be dedicated to the compressor.

15. [Optional] Extra quiet package shall be provided on unit sizes 024-070. This option includes 1 in. thick fiberglass insulation and compressor blanket.

· Fan and Motor Assembly:

1. The fan shall be direct-drive centrifugal forward curved type with a dynamically balanced wheel. The housing and wheel shall be designed for quiet low velocity operation. The blower housing shall feature a removable inlet ring to facilitate removal and servicing of the fan motor. The fan motor shall be Constant Airflow ECM (Electronically Commutated Motor) for premium fan efficiency and constant air delivery over a wide range of external static pressures. These motors shall be field adjustable for ± 15% of nominal design airflow. These motors shall provide feedback to the unit control box to verify motor operating mode and delivered CFM.

2. Blowers shall have inlet rings to allow removal of wheel and motor from one side without removing housing.

3. Units supplied without permanently lubricated motors must provide external oilers for easy service.

4. The fan and motor assembly must be capable of overcoming the external static pressures as shown on the schedule.

5. The airflow/static pressure rating of the unit shall be based on a wet coil and a standard clean filter in place.

· Refrigerant Components:

1. Units shall use R-454B refrigerant. All units shall have a factory sealed and fully charged refrigerant circuit.

2. Hermetic Compressor:

Two stages scroll compressor shall be specifically designed for R-454B refrigerant and shall be internally sprung, externally isolated and with thermal overload protection.

3. Refrigerant metering shall be accomplished with a thermostatic expansion valve. Units with only capillary tubes are not acceptable.

4. The finned tube heat exchanger shall be constructed of lanced aluminum fins not exceeding sixteen fins per inch bonded to rifled copper tubes in a staggered pattern and will have a 600 psig working refrigerant pressure. The heat exchanger shall have aluminum end sheets.

5. [Optional] The finned tube heat exchanger shall have an optional protective coil coating. This corrosion protection shall consist of tin-plated copper tubing with coated aluminum fins that must pass 1,000 hours of ASTM B117 salt fog testing. Painted, dipped or e-coated heat exchangers are not acceptable.

6. Reversing Valve: Reversing valves shall be four-way solenoid activated refrigerant valves that will fail in the heating operation should the solenoid fail to function. Reversing valves that fail to the cooling operation shall not be allowed.

7. Coaxial (tube in tube) refrigerant-to-water heat exchanger. Refrigerant-to-water heat exchangers shall be of copper inner water tube and steel outer refrigerant tube design rated to withstand 600 psig working refrigerant pressure and 400 psig working water pressure. Shell and tube style refrigerant to water heat exchangers shall be treated as pressure vessels and shall require refrigerant pressure relief valves piped to the exterior of the building. The contractor supplying the water source heat pumps with shell and tube heat exchangers shall be responsible for any additional installation costs. Brazed plate water-to-refrigerant heat exchangers shall require additional centrifugal separators added to the supply water piping at each unit. Each separator shall have an automated clean out valve piped to a waste line. The contractor supplying water source heat pumps with brazed plate heat exchangers shall be responsible for any additional costs.

8. [Optional] Cupronickel coaxial water-to-refrigerant heat exchangers shall be provided, with cupronickel inner water tube construction.

9. [Optional] On/Off Hot Gas Reheat (HGRH) shall be available for dehumidification, and controlled by a thermostat with dehumidification output, humidistat, or DDC control connected to the unit H terminal and shall start the unit in the reheat mode when the humidity is above the set point once the space temperature is satisfied. Cooling or heating requirements shall take precedent over HGRH.

10. [Optional] Modulating Hot Gas Reheat (HGRH) shall be available for dehumidification, and controlled by TruVu™ DDC controller and shall start the unit in the reheat mode when the humidity is above the set point once the space temperature is satisfied. Cooling or heating requirements shall take precedent over HGRH.

11. [Optional] Hot Gas Bypass (HGBP): Units shall be supplied with an ETL listed hot gas bypass valve with factory supplied and installed controls to prevent air coils from frost development by taking hot gas and bypassing the water coil and expansion device and reintroducing the hot gas into the refrigeration line prior to the air coil. The hot gas bypass valve shall maintain a minimum refrigerant suction pressure to allow for a light load cooling module or a low entering air temperature cooling mode. The HGBP valve shall be factory set for opening pressure to 105 psig, this set point can be adjusted (95 to 115 psig) in the field.

12. [Optional] Hot water generator: Unit sizes 024-070 shall be equipped with factory installed internal heat recovery kit for domestic hot water production. This kit shall include an internally protected hot water circulation pump, copper double wall vented coaxial water-to-refrigerant heat exchanger, 120°F hot water temperature limit switch and an on/off switch/circuit breaker.

13. A2L refrigerant leak detection system shall be provided for unit sizes 060-070; the refrigerant leak detection system is required by UL-60335-2-40. 

14. [Optional] A2L refrigerant leak detection system shall be available for units where the refrigerant leak detection system is required by local codes. 

15. Safety controls shall include both a high pressure and low-pressure switch. Temperature sensors shall not replace these safety switches.

16. Refrigerant pressure test ports shall be factory installed on high and low-pressure refrigerant lines to facilitate field service. Unit shall be equipped with a dedicated accesses panel for the test ports not requiring removal of the primary cabinet panels to access the test ports.

17. Activation of any safety device shall prevent compressor operation via a lockout circuit. The lockout circuit shall be reset at the thermostat or at the contractor supplied disconnect switch. Units which may be reset at the disconnect switch only shall not be acceptable.

· Hydronic Factory Installed Options:

1. [Optional] Waterside Economizer: Waterside economizer shall be completely installed at the factory, with an additional condensate drain pan, motorized 3-way valve, and all internal electric controls. Waterside economizer assembly shall be rated at minimum 450 psig and UL (Underwriters Laboratories) listed for applications with the heat pump. This option is externally mounted outside the unit.

2. [Optional] Units shall have a 2-way electrically operated shut-off (solenoid) valve with end switch mounted internally in the unit cabinet. The two-way motorized solenoid valve is rated for a 300 psig working pressure. The valve shall be factory wired to open with compressor operation.

3. [Optional] Units shall have an optional water flow regulating valve set to 3 gallons per minute of water flow per nominal ton of refrigeration capacity.

4. [Optional] Flow proving switch (differential pressure switch) shall energize relay and disable unit operation when no water flow to the unit.

· Controls and Safeties:

1. Electrical:

a. Controls and safety devices will be factory wired and mounted within the unit. Controls shall include fan relay, compressor contactor, 24-v transformer, reversing valve coil, and Unit Protection Module (UPM). The standard transformer shall be rated for a minimum 75 VA, or 100 VA for units with TruVu™ controller. All units shall be name plated for use with time-delay fuses or HACR circuit breakers. Unit controls shall be 24-v and provide heating or cooling as required by the remote thermostat/sensor.

b. All units shall have a factory installed and labeled terminal strip input for field provided thermostat or DDC controller.

c. Units shall include a factory provided wiring diagram on the inside of the control access panel.

d. Control box shall be mounted on a hinge and capable of swinging out and full removal.

e. All units shall have a Unit Protection Module (UPM) printed circuit board which implements following equipment safeties: 

1) anti-short cycle time delay (5-minute delay on break)

2) random start time delay on initial power

3) brownout / surge / power interruption protection

4) 120 second low pressure switch bypass timer

5) high refrigerant pressure shutdown

6) low refrigerant pressure shutdown

7) water coil freeze protection shutdown

8) air coil freeze protection shutdown

9) high condensate level shutdown

10) 24 VAC alarm output for remote fault indication

11) refrigerant leak shutdown

12) intelligent alarm reset

The UPM shall automatically reset after a safety shutdown. Restart the unit if the cause of the shutdown no longer exists (except for low temperature and high condensate level shutdowns). Should a fault re-occur within 60 minutes after reset, then a “hard” lockout will occur. A light-emitting diode (LED) shall indicate the following alarms: brownout, high refrigerant pressure, low refrigerant pressure, low water temperature and a high level of condensate in the drain pan, refrigerant leak fault. The LED will display each fault condition as soon as the fault occurs. If a hard lockout occurs, then the fault LED will display the type of fault until the unit is reset.

The UPM shall feature the following field configurable adjustments:

a) lock out reset on thermostat interruption or power reset

b) two or four restart attempts before a hard lockout

c) test mode (reduces all time delays to 5 seconds for diagnostic work)

d) air/water coil freeze limit trip

f. [Optional] Units shall have all the features above (UPM) and additionally TruVu™ DDC controller shall have an advanced controls logic and include following features:

1) Three-speed fan control. Controller shall automatically, based upon space temperature input, operate the fan at the lowest of 3 selectable speeds to achieve space temperature set point.

2) Two-position OA (outdoor air) damper.

3) Modulating OA damper with DCV (demand controlled ventilation).

4) Hot gas reheat solenoid valve.

5) Two-position water economizer control.

6) Modulating water economizer control.

7) Two stage electric auxiliary heat control.

8) Scheduling.

9) Adaptive optimal start.

10) Equipment performance monitoring.

11) Alarm status

TruVu™ controller must be capable of communicating over BACnet®
 IP, supporting direct connection or daisy chain topologies using BACnet®/IP for seamless integration into building automation systems, and shall have the ability to be viewed in the TruVu™ Equipment Touch (ET), or field assistant user interface.

g. [Optional] Non-fused electrical disconnect shall be installed on the unit.

h. [Optional] Units shall have a short circuit current rating (SCCR) of no less than 65 kA.

i. [Optional] Boilerless control shall activate an electric heater and disable compressor when water temperature drop below set point. 

j. [Optional] Energy management switch to enable remote operation of WSHP (water source heat pump).

k. [Optional] Pump-valve relay to enable a pump/valve operation when calling for compressor operation.

l. [Optional] Compressor status relay shall be provided to monitor a status of the compressor via normally open set of dry contact.

· Accessories:

1.  Hydronic accessories:

a. Hose Kits

All units shall be connected to main water supply and return headers with hoses. The hoses shall be 2 or 3 feet long, braided stainless steel rated to 400 psig at 265°F. Hoses may contain optional ball valves with P/T ports, Y strainers with blow down valves and/or auto flow regulators as specified in the schedule.

b. Two-position motorized isolation valve (2-way solenoid valve)

Two-position motorized isolation valve (2-way solenoid valve) with end switch shall be available for field installation. The two-way motorized solenoid valve is rated for a 125 psig working pressure. The valve shall be field wired to open with compressor operation.

c. Ball Valves (Brass Body)

Valves shall be available for shutoff and balancing water flow. Available with memory, memory stop, and pressure temperature ports. (600WOG at 325°F)

d. Y Strainers (Bronze Body)

Strainers are “Y” type configuration with a brass cap. Strainer screen shall be made of stainless steel. (600WOG at 325°F)

2.  Controls accessories:

a. Carrier commercial thermostat controls are available as follows:

1) Edge®
 Pro 7-day programmable thermostat offers 2-stage heat, 2-stage cool, remote contact input, remote sensor capability, pre-occupancy purge, soft start, manual/auto changeover, 4 settings per day, 24 vac, backlit LCD, keypad lockout, no batteries required, 5-minute compressor protection, never lost memory, 3 security levels, and temperature display in °F or °C.

2) Comfort Pro Programmable Thermostat, 2-stage Heat /2-stage Cool G/E, plus 1-stage auxiliary or emergency heat HP&WSHP, or 2-stage cool/heat only, Touch n Go™ program (OCC/UNOCC/ LIMIT), Passcode protection, remote sensor capability with override, random start, Manual/Auto-Changeover, Outdoor/supply/return temp, hospitality mode, option battery powered.

3) Carrier Connect™ Wi-Fi 7-day programmable/non-programmable; 4.3 in. touch screen, web enabled (portal), smartphone app, 1-2 stage heat/1-3 stage cool, G/E, HP (with 2-stage aux heat), remote sensor capability, manual/auto-changeover, humidify/dehumidify/Humidi-MiZer®.

4) Non-Branded Wi-Fi 7-day programmable/non-programmable; 4.3 in. touch screen, web enabled (portal), smartphone app, 1-2 stage heat/1-3 stage cool, G/E, HP (with up to 2-stage aux heat), remote sensor capability, manual/auto-changeover, humidify/dehumidify/Humidi-MiZer®.

5) ComfortVu BACnet®, 24 vac Thermostat offers a large backlit LCD display and intuitive push-button controls for easy operation, BACnet® MS/TP port, 2 universal inputs, 22 universal outputs, and 4 relay outputs. It allows control over up to 3 stages of heating and 2 stages of cooling, along with up to 3 fan speeds.

b. ZS sensors for TruVu™ DDC (direct digital controls) control option. Sensors shall be available as follows, and all sensors below offer monitoring of space temperature only, or space temperature and CO2, or space temperature and humidity, or space temperature and CO2 and humidity.

1) ZS Standard sensor with a communication port.

2) ZS Plus sensor with communication port, occupancy status indicator, local occupancy override and set point adjustment.

3) ZS Pro sensor with communication port, occupancy status indicator, local occupancy override, set point adjustment, LCD (liquid crystal diode) display, alarm indicator and fan speed control.

4) ZS Pro-F sensor with communication port, occupancy status indicator, local occupancy override, set point adjustment, LCD display, alarm indicator, fan speed control, cooling/heating/fan only mode control and °F to °C conversion.

5) TruVu™ Equipment Touch (ET) for unit start-up and commissioning shall be available in 7 and 10 in. touch screen sizes for panel or wall mounting. All point objects will have the ability to be viewed in the TruVu™ ET user interface.

3. Electric Duct Heaters:

a. Duct heater shall be slip-in type and shall be UL approved for zero clearance to combustible surfaces. The heater shall bear a UL/CSA label. Control panel and element housing shall be constructed of heavy gauge galvanized steel. All heating elements shall be made of nickel/chromium resistance wire with ends terminated by means of staking and heliarc welding to machine screws. Heating element support structure shall consist of galvanized steel wire formed and constructed to support ceramic bushings through which the heating element passes. Control cabinet shall be constructed of heavy gauge galvanized steel with multiple knockouts for field wiring. Control cabinet shall have a solid cover also of heavy gauge galvanized steel, held in place with hinges and tool-release latches.

b. Duct heater shall be supplied with primary over temperature protection by built in disc type automatic reset thermal cutouts and secondary over temperature protection by built in disc type manually resettable thermal cutouts. These devices must function independently of one another and are not acceptable if series connected in the control circuit wiring. A disconnecting magnetic control circuit is required. All duct heaters will require either a fan interlock circuit or an airflow switch.

c. Over-current protection by means of factory-installed fusing within the control cabinet shall be provided for heaters rated at more than 48 amps. Heating elements shall be subdivided and fused accordingly.

d. All wiring, component sizing, component spacing and protective devices within the control cabinet shall be factory installed and comply with UL standards. All heaters shall function properly with a 60 Hz power supply.

e. A wiring diagram depicting layout and connections of electrical components within the control cabinet shall be affixed to the inside of the control cabinet cover.

f. A rating plate label shall be affixed to the exterior of the control cabinet cover which states model number, serial number, volts, amps, phase, frequency, control volts, volt-amps and minimum airflow requirements.
�Third-party trademarks and logos are the property of their respective owners.





�Third-party trademarks and logos are the property of their respective owners.








1


1

