
Single-Duct VAV Terminal Unit

HVAC Guide Specifications

Size Range: Nominal 23 to 7100 cfm

Carrier Model Number:


 35EA (Analog Electronic Controls)


 35EB (Open BACnet™
 VAV Electronic Controls)


 35EC (VAV CCN Controls)


 35ED (BACnet™ VAV Electronic Controls)


 35EN (No control units; factory-mounted actuator or field mounted)


 35EP (Pneumatic Control Units)


 35ET (TruVu BACnet™ VAV Electronic Controls)


 35EV (VVT® CCN Controls)


 35EW (TruVu BACnet™ VVT Electronic Controls)

· General

· SYSTEM DESCRIPTION:

· Factory-assembled, externally powered, variable air volume control terminal. Unit shall be complete with a damper assembly, flow sensor, externally mounted volume controller, collars for duct connection, and all required features. Control box shall be clearly marked with an identification label that lists such information as nominal cfm, maximum and minimum airflow limits, coil-type and coil hand, where applicable.

· QUALITY ASSURANCE

· Insulation shall meet National Fire Protection Association (NFPA) 90A requirements for flame spread and smoke generation and Underwriters Laboratory (UL) 181 requirements for anti-erosion, corrosion, and fungus properties.

· Hot water coils, when specified, shall be tested for leakage at 250 psig with the coil submerged in water.

· Electric heating coils, when specified, shall be UL or Engineering Testing Laboratory (ETL) listed and designed to comply with UL Standard 1096.

· Sound power levels shall be Air-Conditioning, Heating, and Refrigeration Institute (AHRI) certified in accordance with the requirements of AHRI 880.

· Products

· EQUIPMENT

· General:

Factory-assembled, externally powered, variable air volume control terminal. Unit shall be complete with a damper assembly, flow sensor, externally mounted volume controller, collars for duct connection and all required features. Control box shall be clearly marked with an identification label that lists such information as nominal cfm, maximum and minimum airflow limits, coil-type and coil hand, balancing chart, and tagging data, where applicable.

· Unit Cabinet:

Constructed of 22-gauge (20-gauge optional) galvanized steel with round or rectangular inlet collar and rectangular discharge with slip and drive connection. All primary air inlet collars shall accommodate standard flex duct sizes

· Insulation:

1. Standard casing shall be lined with 1/2-in. thick, 1/2-lb/cf dual-density fiberglass insulation that meets UL 181 and NFPA 90A. Insulation shall be attached to the unit casing by adhesive and weld pins.

2. Optional Insulation:

a. 1-IN.-THICK INSULATION: Unit casing shall be lined with dual-density, 1-in. thick, 1/2-lb/cf density fiberglass insulation that meets UL 181 and NFPA 90A.

b. CELLULAR INSULATION: Unit casing shall be lined with 1/2-in. or 1-in. thick, 1/2-lb/cf density, smooth surface, polyolefin, closed-cell foam insulation for fiber-free application. Cellular insulation meets UL 181 and NFPA 90A and does not support mold or bacteria growth. Insulation shall be attached to the unit casing by adhesive and weld pins.

c. STERILINER INSULATION: Unit casing shall be lined with 13/16-in. thick, 4-lb/cf density, rigid-board insulation with nylon-reinforced foil covering insulation fibers that meets UL 181 and NFPA 90A. Liner shall be attached to unit casing by adhesive and weld pins with full-seam-length Z-strips to enclose and seal the insulation cut edges.

d. NO LINER: Unit casing shall be equipped with no internal insulation liner.

e. STERILWALL INSULATION: Unit casing shall be lined with 1/2-in. or 1-in. thick, 1/2-lb/cf density insulation, meeting UL 181 and NFPA 90A, enclosed between the unit casing and a non-perforated internal sheet metal cover extending over the fiberglass insulation, as well as covering the liner cut edges.

f. PERFORATED DOUBLE WALL: Unit casing shall be lined with 1/2-in. thick, 1/2-lb/cf dual-density fiberglass insulation that meets UL 181 and NFPA 90A, enclosed between the unit casing and a perforated internal sheet metal cover extending over the fiberglass insulation, as well as covering the liner cut edges.

· Damper Assembly:

1. The control air damper assembly shall be constructed of heavy gauge galvanized steel with 1/2-in. solid shaft rotating in Delrin®1 bearings. Damper shaft shall be marked on the end to indicate damper position. Damper blade shall incorporate a flexible gasket for tight airflow shutoff and operate over a full 90 degrees.

· Controls:

1. Units shall have pressure-independent pneumatic, analog, or communicating controls, as specified, capable of maintaining required airflow set points ±5% of the unit’s capacity at any inlet pressure up to 6 in. wg. The controllers shall be capable of resetting between factory or field-set maximum and minimum (>350 fpm inlet duct velocity) set points to satisfy the room thermostat demand.

2. The unit shall be equipped with an amplified flow probe located in the unit inlet. Air flow for the pressure independent controller (supplied by others) shall be determined with a factory-supplied 12-point total pressure, center-averaging cross flow sensor, having a magnification resulting in no greater than 2625 fpm at 1 in. developed signal.

· Special Features:

1. Hot Water Heating Coil:

Coil shall be mounted in a minimum 20-ga. galvanized steel casing with slip and drive discharge connections and factory mounted on the base unit as shown on the equipment drawings. Coils shall have:

a. Aluminum fins (10 fins per in.) bonded to the copper tubes by mechanical expansion. 

b. Number of coil rows and circuits shall be selected to provide performance as required by the plans.

c. Up to 4 rows as shown on equipment drawings or designed on the equipment schedule. Right or left-hand fittings with sweat connection sizes as indicated on equipment drawings.

2. Electric Heating Coil:

Electric coils shall be supplied by the terminal unit manufacturer and shall be ETL listed in accordance with UL standards. Construct coil casing with minimum of 20-gauge zinc-coated steel. Elements shall be nickel‑chrome and supported by ceramic isolators. The integral control panel shall be housed in a NEMA (National Electrical Manufacturers) 1 enclosure, with access door to all controls and safety devices. Electric coils shall contain a primary automatic reset thermal cutout and differential pressure airflow switch for proof of airflow. Heaters shall: 

a. Be designed for the capacity, electrical characteristics and steps of control as shown on the equipment schedule.

b. Have open coil construction with 80% nickel, 20% chromium wire supported in free-floating ceramic bushings. Coil frame shall be constructed of corrosion resistant steel.

c. Be factory wired and include all limit switches.

d. Have electric coils that shall include fused or non-fused door interlocking disconnect switch, alternating current (AC) solid state relays (SSRs) for silent operation, fuse block, dust tight enclosure construction, all mounted and/or wired within the control enclosure.

e. Have an SSR proportional control of electric heat that shall meet the requirements of ASHRAE (American Society of Heating, Refrigerating and Air-Conditioning Engineers) Standard 62, Addenda N.

f. Have an SSR proportional electronic controlled electric heater with control of the leaving air temperature limiting the unit discharge temperature to a set value.

3. Sound Attenuator:

The integral sound attenuator section shall consist of a continuous extension of the standard zinc-coated steel casing. When electric heat is required, the attenuator will be used as a standard feature.

�Third-party trademarks and logos are the property of their respective owners.








1


1

