
Commercial Packaged Air-Handling Unit

HVAC Guide Specifications

Size Range: 12.5 to 30 Tons, Nominal Cooling

Carrier Model Numbers: 40RLA (Direct-Expansion Coil) and 40RLS (Chilled Water Coil)

· General

· System Description

· Indoor, packaged air-handling unit for use in commercial split systems. Unit shall have a multi-position design and shall be capable of horizontal or vertical installation on a floor or in a ceiling, with or without ductwork. (Only vertical units are to be applied without ductwork.)

· Unit with direct-expansion coil shall use Puron Advance™ (R-454B) in a refrigerant circuit with a matching air-cooled condensing unit. Unit with chilled water coil shall be used in a chilled water circuit.

· Quality Assurance

· Coils shall be designed and tested in accordance with ASHRAE™
 15 Safety Code for Mechanical Refrigeration (U.S.A.)

· Unit shall be constructed in accordance with UL Standard 60335-1 and 60335-2-40, and shall carry the UL and UL, Canada, labels.

· Unit insulation and adhesive shall comply with NFPA-90A (U.S.A.) requirements for flame spread and smoke generation.

· Unit shall be manufactured in a facility registered to the ISO 9001 manufacturing quality standard.

· Direct-expansion and chilled water coils shall be burst and leak tested at 435 psi.

· Delivery and Storage

· Units shall be stored and handled per manufacturer’s recommendations.

· Safeties

· A2L Refrigerant Leak Dissipation System
(Electromechanical):

1. Leak dissipation system shall consist of control board and A2L sensor certified to UL 60335-2-40.

2. System shall be designed for the life of the unit.

3. Dissipation system shall be automatic and disable compressors on 38AX condensing units.

4. Refrigerant leak sensor shall be installed in UL certified location and orientation. Sensor shall be self-correcting and resettable. Single use refrigerant leak sensor shall not be permitted.

5. Factory installed dissipation controller shall use onboard microprocessor and include:

a. Automatic reset after a dissipation event has occurred.

b. Onboard LED with flash code to indicate current unit status and hardware failures.

c. Depressible “Test” button to allow for a system test and recall/reset of leak detection history.

d. 24V dry contact alarm terminal to allow for external notification of leak detection.

6. Dissipation control board shall be accessible via normal maintenance locations and LED shall be visible.

7. Dissipation system shall “Fail Safe” per UL requirements.

8. Dissipation shall allow smoke and building fire systems to override in case of event.

· Products

· Equipment

· Indoor mounted, draw-thru, packaged air-handling unit that can be used in a suspended horizontal configuration or a vertical configuration. Unit shall consist of forward-curved belt-driven centrifugal fan(s), motor and drive assembly, pre-wired fan motor contactor, factory-installed refrigerant metering devices (direct-expansion coil units), cooling coil, 2 in. (51 mm) disposable air filters, and condensate drain pans for vertical or horizontal configurations.

1. Cabinet shall be constructed of mill-galvanized steel.

2. Cabinet panels shall be fully insulated with
1/2 in. (12.7 mm) fire-retardant material.

3. Unit shall contain non-corroding condensate drain pans for both vertical and horizontal applications. Drain pans shall have connections on right and left sides of unit to facilitate field connection. Drain pans shall have the ability to be sloped toward the right or left side of the unit to prevent standing water from accumulating in pans.

4. Unit shall have factory-supplied 2 in. (51 mm) throwaway-type filters installed upstream from the cooling coil. Filter access shall be from either the right or left side of the unit.

· Coils:

DX coil is 4-row and consists of copper tubes with sine-wave aluminum fins bonded to the tubes by mechanical expansion. Suction and liquid line connections or supply and discharge connections shall be made on the same side of the coil.

1. Direct-expansion coils shall feature factory installed thermostatic expansion valves (TXVs) for refrigerant control. The TXVs shall be Puron Advance™ R-454B compatible and capable of external adjustment. Coil tubing shall be internally rifled to maximize heat transfer.

2. Chilled water coils shall be rated for an operating pressure of not less than 300 psig (2069 kPag).

· Operating Characteristics:

1. When combined with matching 38AX condensing unit the system shall be capable of starting and running at ambient outdoor temperatures from 35°F (2°C) to 125°F (52°C) in cooling mode.

2. Unit shall operate at ±10% from rated voltage.

· Motor:

1. Fan motor of the size and electrical characteristics specified on the equipment schedule shall be factory supplied and installed.

2. Motors rated at 1.3 through 3.7 hp shall have inherent thermal overload protection. Motors rated at 5 hp shall be protected by a circuit breaker.

3. Evaporator-fan motor shall have permanently lubricated, sealed bearings and inherent
automatic-reset thermal overload protection or manual reset calibrated circuit breakers. Evaporator motors are designed specifically for Carrier and do not have conventional horsepower (hp) ratings listed on the motor nameplate. Motors are designed and qualified in the “air-over” location downstream of the cooling coil and carry a maximum continuous bhp rating that is the maximum application bhp rating for the motor; no “safety factors” above that rating may be applied.

4. All evaporator-fan motors 5 hp and larger shall meet the minimum efficiency requirements as established by the Energy Policy Act of 1992 (EPACT), effective October 24, 1997.

· Control Box:

1. Shall include an easily accessible Unit Control Board to conveniently and safely provide connection points for vital control functions such as: smoke detectors, phase monitor, economizer, thermostat, and low and high pressure switches. Controller shall also provide an intuitive means to adjust the indoor fan speed through a simple switch and pot adjustment design.

· Staged Air Volume System (SAV™) for 2-stage cooling models (standard):

1. Evaporator fan motor.

a. Shall have permanently lubricated bearings.

b. Shall have a maximum continuous bhp rating for continuous duty operation; no safety factors above that rating.

c. Shall be Variable Frequency duty and 2‑speed control.

d. Shall contain motor shaft grounding ring to prevent electrical bearing fluting damage by safely diverting harmful shaft voltages and bearing currents to ground.

2. Variable Frequency Drive (VFD) Standard:

a. Shall be installed inside the unit cabinet, mounted, wired and tested.

b. Shall contain Electromagnetic Interference (EMI) frequency protection.

c. Insulated Gate Bi-Polar Transistors (IGBT) used to produce the output pulse width modulated (PWM) waveform, allowing for quiet motor operation.

d. Self diagnostics with fault and power code LED indicator. Field accessory Display Kit available for further diagnostics and special setup applications.

e. RS485 capability standard.

f. Electronic thermal overload protection.

g. 5% swinging chokes for harmonic reduction and improved power factor.

h. All printed circuit boards shall be conformal coated.

· Special Features:

1. Alternate Motor and Drive:
An alternate motor and/or medium-static or high-static drive shall be available to meet the airflow and external static pressure requirements specified on the equipment schedule.

2. External Paint:
Where conditions require, units shall be painted with an American Sterling Gray finish.

3. Hot Water Coil:
Coil shall be 2-row, U-bend coil with copper tubes and aluminum plate fins bonded to the tubes by mechanical expansion. Coil shall be mounted in a galvanized steel housing that shall be fastened to the unit’s fan deck for blow-thru heating operation. Coil shall have maximum working pressure of 150 psig.

4. Steam Distributing Coil:
Coil shall consist of one row of copper tubes with aluminum plate fins, and shall have inner steam distributing tubes. Coil shall be mounted in a galvanized steel housing and shall be fastened to the unit’s fan deck for blow-thru heating operation. Coil shall have maximum working pressure of 20 psig at 260°F.

5. Electric Heaters:
Heaters for nominal 240v, 480v, or 575v, 3‑phase, 60 Hz shall be factory-supplied for field installation as shown on the equipment drawings. Electric heat assembly shall be UL (U.S.A.) and UL, Canada, agency approved, and shall have single-point power wiring. Heater assembly shall include contactors with 24-v coils, power wiring, 24-v control wiring terminal blocks, and a hinged access panel. Electric heaters shall not be used with air discharge plenum.

6. Air Discharge Plenum:
Plenum shall be factory-supplied to provide free-blow air distribution for vertical floor-mounted units. A grille with moveable vanes for horizontal or vertical airflow adjustment shall be included. Plenum shall be field-assembled and field-installed on the unit’s fan deck for blow-thru air distribution. Plenum shall not be used with electric heaters.

7. Return-Air Grille:
Grille shall be factory-supplied for field installation on the unit’s return air opening.

8. Unit Subbase:
Subbase assembly shall be factory-supplied for field installation. Subbase shall elevate floor-mounted vertical units to provide access for correct condensate drain connection.

9. Economizers:

a. Accessory Ultra Low Leak 
EconomizerONE. (Field-installed) Economizer for ventilation or “free” cooling shall be factory provided for field installation on either return air opening of air handler.

1) Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.

2) Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

3) Shall include all hardware, actuator and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.

4) Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

5) Ultra Low Leak design meets California Title 24 section 140.4 and ASHRAE 90.1 requirements for 4 cfm per sq ft on the outside air dampers and 10 cfm per sq ft on the return dampers.

6) Economizer controller on
EconomizerONE models shall be the
Siemens POL224 that provides:

a) Combined minimum and DCV maximum damper position potentiometers with compressor staging relay.

b) Optional configuration via WLAN stick and Siemens Climatix™ smartphone app for easy setup.

c) Functions with solid-state analog enthalpy or dry bulb changeover control sensing.

d) LED indication for free cooling, sensor, and damper operation.

e) One-line LCD interface screen for setup, configuration and troubleshooting.

f) On-board Fault Detection and Diagnostics (FDD) that senses and alerts when the economizer is not operating properly, per California Title 24, ASHRAE 90.1 and IECC®
.

g) Sensor failure loss of communication identification.

h) Capabilities for use with multiple-speed or single speed indoor fan systems.

i) Digital sensors: Dry bulb and Enthalpy.

10. Overhead Suspension Package:

Package shall include necessary brackets to support units in a horizontal ceiling installation.

11. CO2 Sensor:

Sensor shall provide the ability to signal the economizer to open when the space CO2 level exceeds the predetermined setpoint.

12. Condensate Drain Trap:

Trap shall have transparent, serviceable design for easy cleaning. Kit shall include overflow shutoff switch and wiring harness for connection to an alarm if desired.

13. Adaptive Dehumidification System:

The Adaptive Dehumidification System shall be factory-installed and shall provide greater dehumidification of the occupied space by providing a mode of dehumidification operation in addition to its normal design cooling mode:

a. Subcooling mode further sub cools the hot liquid refrigerant leaving the condenser coil when both temperature and humidity in the space are not satisfied.

�Third-party trademarks and logos are the property of their respective owners.





�Third-party trademarks and logos are the property of their respective owners.








4


4

