Fan Coil Unit — Horizontal Models

HVAC Guide Specifications — 42C

Size Range: 200 to 1200 Nominal Cfm

Carrier Model Numbers:

 42CA (Furred-in)

 42CE (Furred-in with Plenum)

 42CG (Cabinet)

 42CK (Furred-in, Telescoping Panel)

· General

· SYSTEM DESCRIPTION

Horizontal, 2-pipe or 4-pipe (or electric heat), room fan coil unit with furred-in, above ceiling cabinet for ducting, or with cabinet for exposed ceiling installations.

· QUALITY ASSURANCE

Units shall be tested and certified in accordance with AHRI (Air-Conditioning, Heating, and Refrigeration Institute) standard 440, latest edition. All base or standard units shall have C-ETL-US listing signifying the units have been examined by ETL and are in compliance with both the US and Canadian applicable standards. Each coil shall be factory tested for leakage at 300 psig air pressure with coil submerged in water. Insulation and adhesive shall meet NFPA (National Fire Protection Association) 90A requirements for flame spread and smoke generation. All equipment wiring shall comply with NEC (National Electrical Code) requirements.

· DELIVERY, STORAGE AND HANDLING

Each unit shall be individually packaged from point of manufacture. Unit shall be handled and stored in accordance with the manufacturer’s instructions.

· Products

· EQUIPMENT

· General:

Factory-assembled, horizontal, blow-thru type fan coil for furred-in, exposed ceiling or ducted installations. Unit shall be complete with water coil(s), fan(s), motor(s), drain pan, and all required wiring, piping, controls and special features. Standard insulation shall be dual density fiberglass insulation.

· Furred-in Base Unit (42CA):

· Casing is heavy gage galvanized steel, lined on the inside with 1/2-in. thick fiberglass insulation, with a 1 in. long collar for supply duct connection. NO filter installed in base unit.

· The drain pan shall be constructed of galvanized steel extending the entire length and width of the coil(s) and shall be pitched for drainage. The inside surface of the drain pan shall be coated with a 2-part closed cell foam insulation.

· Furred-in Units with Plenum (42CE):

Base unit with factory-installed plenum section and 1-in. fiberglass throwaway filter as shown on equipment drawings. The plenum shall be bottom or rear air return, shall enclose the fan/motor assemblies, and shall be lined with 1/2-in. fiberglass insulation. Unit shall have a removable panel to provide access to fan/motor assemblies and unit identification label.

· Cabinet Units (42CG):

Base unit with stamped discharge grille, removable bottom access panel with stamped return-air grille, filter rack and 1-in. fiberglass throwaway filter. The panel shall be fastened with tamper proof quarter-turn fasteners. The cabinet shall be coated with an Arctic White powder-coat finish.

· Ceiling, Furred-in with 2-in. Telescoping Ceiling Panel (42CK):

Base unit with full galvanized upper casing, adjustable height, hinged return-air ceiling panel, and 1-in. fiberglass throwaway filter. Panel shall be coated with an Arctic White powder-coat.

· Fans:

Direct-driven, double-width fan wheels with forward-curved blades shall be statically and dynamically balanced. Scrolls shall be constructed of galvanized steel. Fan wheels shall be constructed of galvanized steel.

· Coils:

Standard base unit shall be equipped with a 3-row or 4-row coil for installation in a 2-pipe system. Additional coil depth and circuiting shall be provided for installation in a 4-pipe system as described in the Special Features section. All coils shall have 1/2-in. copper tubes and aluminum fins (10 fins per inch) spacing. Coil fins are mechanical bonded to tube joints. The copper tubes comply with the ASTM (American Society for Testing and Materials) B-75. The fin thickness is 0.0045-in. and tube thickness is 0.016 inch. All coils shall be leak tested with air at 300 psig under water.

· Controls and Safeties:

The fan motor(s) shall be equipped with integral automatic temperature reset for motor protection.

· Operating Characteristics:

· A one-coil unit installed in a 2-pipe system shall be capable of providing heating or cooling as determined by the operating mode of the central water supply system. 

· A double-circuit coil unit installed in a 4-pipe system shall be capable of providing sequenced heating and cooling.

· Electrical Requirements:

Standard unit shall operate on 115 v, single-phase, 60 Hz electric power. All internal wiring shall be in flexible conduit.

· Motor(s):

· Fan motors shall be 3-speed, 115 v, single-phase, 60 Hz, permanent split capacitor type, permanently lubricated, with sleeve bearings. Motor shall have thermal overload protection with automatic reset and be connected with quick connect electrical plug.

· Special Features:

Certain standard features are not applicable when the features designated by * are specified. See your local Carrier Sales Offices for amending specifications.

· Unit coil(s) shall be equipped with automatic air vents.

· For installation in a 4-pipe chilled water or direct expansion (DX R-410A) system, unit shall be equipped with a 3-row cooling/one-row heating split-circuit coil, a 3-row cooling/2-row heating split-circuit coil, or a 4-row cooling/one-row heating split-circuit coil as required. Coil connections to be as shown on the equipment drawings.

· For installation on a 2-pipe chilled water or direct expansion (DX R-410A) system, units shall be equipped with a 2-row, 3-row, or 4-row, cooling/heating coil.

· Fan motor shall be permanent split-capacitor type, 208, 220, 240, or 277-v, single-phase, 50 or 60 Hz as specified on the equipment schedule.

· Fan motor shall be constant torque electrically commutated type, 115, 208, 220, 240, or 277-v, single phase, 50 or 60 Hz as specified on the equipment schedule. The operating sequence shall be one of the following, as specified:

· 3 Discrete Speed Input, Potentiometer Field Speed Adjustment. For use with a 3-speed thermostat.

· 4 Discrete Speed Input, Potentiometer Field Speed Adjustment. For use with a 3-speed thermostat.

· Variable Airflow for 0 to 10 VDC / 4 to 20 mA Input. Requires a 0 to 10 VDC input signal and is not compatible with a 3-speed thermostat.

· Unit shall be equipped with electric strip heaters mounted on the entering air side of the water coil. Heaters shall include high limit cutout with auto reset and contactor. Capacity and voltage shall be as shown on the equipment schedule. When fan motor and electric heater are selected at the same voltage and connected to a single power source, a junction box and fuse shall be factory furnished and installed to protect the motor and control circuit.

· Filter track and cleanable filter shall be installed in the plenum.

· Drain pan shall include a second drain connection located above the main drain connection to act as an indicator that the main drain is plugged.

· Discharge-air grille with double deflection, aluminum construction with aluminum frame shall be furnished for field installation as shown on the equipment schedule. Aluminum grilles shall have a natural anodized finish (42CG only).

· Double-deflection discharge-air grille with steel core assembly shall be factory installed as shown on equipment schedule. Grille shall be painted to match cabinet (42CG only).

· Manual stop, balancing, combination balance and stop, ball type, and flow control valves shall be factory furnished.

· Motorized 2-way and 3-way valves shall be factory wired and assembled with tubes terminating in belled ends or unions for field attachment to the coil. Valves shall be packaged within unit to prevent shipping damage.

· Heating and/or cooling wall thermostat shall be factory furnished for field installation.

· Automatic changeover device(s) shall be factory wired for field installation on the supply piping.

· Sequenced heating and cooling wall thermostat shall be factory furnished for field installation.

· Unit shall operate on 208, 220, 240, or 277-v, single-phase, 50 or 60 Hz electrical power as specified on the equipment schedule. All wiring shall be in flexible metal conduit.

· Cabinet of 42CG unit or bottom panels of 42CK unit shall be painted with the color specified on the equipment schedule.

· A stainless steel drain pan shall be available for factory installation.

· Factory-installed insulation options shall include foil faced fiberglass or closed cell insulation.

· Control Options:

· 3-speed, 4-position manual fan switch on a wall plate for field-mounting.

· Factory-installed 24-v transformer and relay board for use, with 24-v controls by others.

· Carrier’s Debonair® 24-v digital display programmable or non-programmable thermostat, including factory-installed 24-v transformer, relay board, and changeover sensors, as required. Provides automatic fan speed control based on demand.

· Factory-Installed Carrier Fan Coil Open Controller: BACnet 
based communicating controller with pre-programmed control algorithms; including factory-installed 24-v transformer, relay board, supply air sensor, return air sensor and changeover sensor (as required). Provides automatic fan speed control based on demand.

�BACnet is a registered trademark of ASHRAE (American Society of Heating, Refrigerating, and Air-Conditioning Engineers).








2


3

