
Central Station Air-Handling Unit

HVAC Guide Specifications — Section 15860

Size Range: 1,800 to 15,000 Nominal Cfm
Carrier Model Number: 39LA,LB,LC,LD,LF,LG,LH

· General

· SYSTEM DESCRIPTION

· Indoor mounted central station air-handling unit designed to provide air to a conditioned space as required to meet specified performance requirements for ventilation, heating, cooling, filtration and distribution. Unit shall be assembled for draw-thru application and shall be arranged to discharge conditioned air horizontally or vertically as shown on the contract drawings.

· Unit with a direct-expansion cooling coil shall have the capability to be used in a refrigerant circuit in conjunction with air-cooled condensing units.

· QUALITY ASSURANCE

· Fan performance shall be rated and certified in accordance with AHRI (Air-Conditioning, Heating and Refrigeration Institute) Standard 430 for Central Station Air-Handling Units and subject to verification of rating accuracy by AHRI-sponsored, third party testing.

· All coils shall be rated in accordance with AHRI Standard 410, latest edition. Chilled water, hot water, and steam coils shall be certified, in accordance with AHRI Standard 410.

· Direct expansion coils shall be designed and tested in accordance with ANSI/ASHRAE (American National Standard Institute/American Society of Heating, Refrigerating and Air-Conditioning Engineers) 15 Safety Code for Mechanical Refrigeration.

· Insulation and insulation adhesive shall comply with NFPA (National Fire Protection Association) 90A requirements for flame spread and smoke generation.

· The management system governing the manufacture of this product is ISO 9001:2015 certified.

· Unit shall be constructed in accordance with cULus standards and shall carry the cULus labels.

· DELIVERY, STORAGE AND HANDLING

Unit shall be stored and handled in accordance with the unit manufacturer’s instructions.

· Products

· EQUIPMENT

· General:

Unit shall be a factory-assembled, single-piece central station air handler. Unit may consist of a fan and coil section with factory-installed chilled water or direct expansion coil, preheat or reheat coil, heating coil section, filter section, mixing box or combination filter/mixing box, or access section as indicated on the equipment schedules. Unit base rail shall be 14 gauge galvanized steel.

· Unit Cabinet:

1. Unit panels shall be constructed of 20 gauge galvanized steel. Casing panels shall be removable for easy access to the unit. All panels shall be gasketed to ensure a tight seal.

2. Optional double wall construction shall be available with inner panels constructed of 20 gauge steel.

3. Hinged access doors shall be double wall with 1.5 lb dual-density fiberglass between galvanized steel panels.

4. Insulation for casing panels on unit shall be 1-in. minimum thickness dual-density fiberglass insulation with a nominal density of not less than 1.5 lb per cubic foot.

5. Insulation shall be secured to casing with waterproof adhesive.

6. Condensate drain pans shall be sloped to prevent standing water and constructed of stainless steel; they shall have double wall construction with threaded drain connection.

· Fan Section:

1. Fan sections shall be constructed of galvanized steel and shall have a formed channel base for integral mounting of fan, motor, and casing panels. Fan scroll, wheel, shaft, and bearings are to be rigidly secured to the base unit.

2. Each unit shall have a single fan wheel and scroll. Fans shall be double width, double inlet type, with forward-curved blades. Wheels shall be bonderized steel with baked enamel, or galvanized steel.

3. Fan wheels shall be keyed to the shaft and shall be designed for continuous operation at the maximum rated fan speed and motor horsepower. Fan wheels and shafts shall be selected to operate at least 25% below the first critical speed, and shall be statically and dynamically balanced as an assembly.

4. Fan shafts shall be solid steel, turned, ground and polished.

5. Fan bearings shall be self-aligning, pillow-block regreasable ball type selected for an average life of 200,000 hours at design operation conditions, per ANSI Code B3.15.

6. Fan motor shall be mounted within the fan section casing on slide rails having 2 adjusting screws. Motor shall be NEMA (National Electrical Manufacturing Association) Design B with sizes and electrical characteristics as shown on the equipment schedule.

7. Fan drive shall be designed for a 1.5 service factor and shall be factory mounted and aligned. Belt drive shall be variable or fixed-pitch type.

· Coil Sections:

1. All coils shall have mill galvanized casings. Coils shall be factory leak tested at 450 psig air pressure.

2. Chilled water coils shall have aluminum plate fins with belled collars bonded to 1/2-in. minimum OD copper tubes by mechanical expansion. Coils shall have galvanized steel casings and copper headers with threaded steel pipe connections. Working pressure shall be 300 psig at 200°F. Coils shall be drainable and have non-trapping circuits. No turbulence-promoting devices will be permitted inside the tubes. Headers shall have drain and vent connections.

3. Direct-expansion coils shall have aluminum plate fins with belled collars bonded to 1/2-in. OD copper tubes by mechanical expansion. Coils shall be provided with pressure-type brass distributors with solder-type connections and shall have a minimum of 2 distributors. Coils for full face active or face-split operation shall have intertwined circuits for equal loading on each circuit. Suction and discharge connections shall be on the same end. Coils shall be designed and tested in accordance with ANSI/ASHRAE 15.

a. Coils selected with R-32 or R-454B (A2L refrigerants) shall be equipped with a refrigerant leak detection system which will include a dissipation board and refrigerant sensor(s) mounted within the refrigerant coil section and wired back to the motor starting device (if equipped).

4. Hot water coils shall have aluminum plate fins with belled collars bonded to copper tubes by mechanical expansion. Coils shall have galvanized steel casings and copper headers with threaded steel pipe connections. Working pressure shall be 175 psig at 400°F. Headers shall have drain and vent connections.

5. Steam distributing coils (non-freeze type) shall have aluminum plate fins with an outer copper tube diameter of 1-in. with a 5/8-in. diameter inner distributing tube, galvanized steel casings, and steel headers. Working pressure shall be 175 psig at 400°F.

6. Electric heat coils for use in large air-handling units shall be open wire type, 80% nickel, 20% chromium resistance coils, insulated by floating steatite bushings and supported in a galvanized steel frame. Bushings shall be recessed into embossed openings and stacked into supporting brackets spaced on not more than 4-in. centers. Thermal cutouts for primary and secondary overtemperature protection shall be provided to meet UL (Underwriters Laboratories) and NEC (National Electrical Code) requirements. Maximum element heating density shall be 55 watts/sq inch.

An integral control box shall be furnished by the manufacturer. It shall contain thermal cutouts, primary and secondary control, sub-circuit fusing, airflow switch, and fused control transformer.

· Filter Sections:

1. Each filter section shall be designed and constructed to house the specific type of filter specified on the equipment schedule.

2. Flat filter sections shall accept filters of standard sizes. Sections shall include side access slide rails and hinged door access. Flat filter section shall be arranged with minimum depth in direction of airflow.

3. Angle filter section shall accept 2-in. filters arranged in horizontal V formation. Double-walled hinged doors shall be provided.

· Damper Sections:

1. Mixing boxes and filter mixing boxes shall have parallel blade, interconnecting outside-air and return-air dampers. Damper blades shall have parallel bends for stiffness and shall be welded to 1/2-in. diameter steel rods rotating in nylon bushings and mounted in rigid galvanized steel frames. Dampers shall be sectionalized to limit blade width to no more than 50-in. to minimize blade warpage and to ensure tight closure. All mixing boxes and filter mixing boxes shall have double-walled hinged access doors.

2. All dampers for mixing boxes and filter mixing boxes shall be rated as low-leakage dampers, having a leakage rate not to exceed 2% of air quantity calculated at 2000 fpm velocity through damper and 4.0-in. wg pressure difference. Damper blades shall be gasketed and perimeter sealing strips shall be provided.

· Access Sections:

1. Access sections shall be installed where indicated on the drawings and shall be as specified on the equipment schedule.

2. Access sections shall have double-walled hinged doors.

· Special Features:

The following unit options shall be available. 

1. Coil Section:

a. Chilled water coil with copper plate fins or e-coated fins and stainless steel casing.

b. Direct-expansion coil with copper plate fins or e-coated fins and stainless steel casing.

c. Hot water (U-bend) coil with copper plate fins or e-coated fins and stainless steel casing.

d. Steam distributing coil with copper fins or e‑coated fins.

· Electrical Accessories:

1. Starters:

Factory-supplied starters shall be covered under a 1 year limited warranty from the manufacturer from the date of shipment.

a. Starter without disconnect:

1) Adjustable motor overload with trip indication.

2) Manual overload reset button (accessible without opening enclosure).

3) 115-v fused secondary control transformer (fuse included — fused primary and secondary over 50 amps).

4) Hand/Off/Auto selector switch (accessible without opening enclosure).

5) Separate 4-position terminal strip for remote H-O-A wiring.

6) C series contactors.

7) Horsepower rated for motor applications.

8) NEMA 4 or higher enclosures.

9) Lug connections for field wiring.

10) Factory mounted, wired, and run tested with factory-supplied motor.

11) UL listed.

b. Combination Starter/Disconnect:

1) Non-fused UL 508 disconnect switch with lockable handle (locks not provided).

2) Cover interlock.

3) Adjustable motor overload with trip indication.

4) Manual overload reset button (accessible without opening enclosure).

5) 115-v fused secondary control transformer (fuse included — fused primary and secondary over 50 amps).

6) Hand/Off/Auto selector switch (accessible without opening enclosure).

7) Separate 4-position terminal strip for remote H-O-A wiring.

8) C series contactors.

9) Horsepower rated for motor applications.

10) NEMA 4 or higher enclosures.

11) Lug connections for field power wiring.

12) Factory mounted, wired, and run tested with factory-supplied motor.

13) UL listed.

· Variable Frequency Drives:

1. Referenced Standards and Guidelines:

a. Institute of Electrical and Electronic Engineers (IEEE)

1) IEEE 519-2014, IEEE Recommended Practice and Requirements for Harmonic Control in Electric Power Systems

b. Underwriters Laboratories (as appropriate)

1) UL 508A

2) UL 61800-5-1

c. National Electric Code (NEC)

1) NEC 430.120, Adjustable-Speed Drive Systems

d. CSA Group 

1) CSA C22.2 No. 274

· International Building Code (IBC)

2) IBC 2018 Seismic - referencing ASCE 7-16 and ICC AC-156 

2. Qualifications:

a. Drives shall be UL labeled as a complete assembly. The base VFD shall be UL listed for 100 kA SCCR when installed in accordance with the manufacturer’s guidelines. 

b. CE Mark - The base drive shall conform to the European Union Electromagnetic Compatibility directive, a requirement for CE marking. The base drive shall meet product standard EN 61800-3 for the First Environment restricted distribution (Category C2).

c. The base drive shall be seismically certified and labeled as such in accordance with the 2018 International Building Code (IBC):

d. Seismic importance factor of 1.5, and minimum 2.5 SDS rating is required. 

e. Ratings shall be based upon actual shake test data as defined by ICC AC-156, via all three axis of motion. 

f. Seismic certification of equipment and components shall be provided by HCAI (formerly OSHPD) preapproval.

g. The base drive shall be SEMI-F47 certified. The drive must tolerate voltage sags to 50% for up to 0.2 seconds, sags to 70% for up to 0.5 seconds, and sags to 80% for up to one second. 

h. Factory-mounted variable frequency drives (VFDs) shall be wired to factory-supplied motors.

i. Factory-supplied VFDs are programmed and started up from the factory and qualify the VFD, through ABB, for a 36-month warranty from date of commissioning or 40 months from date of sale, whichever occurs first.

1) The VFD parameters are programmed into the controller and removable keypad. In the event that the VFD fails and needs replacement, the program can then be uploaded to the replacement VFD via the original keypad (compact VFD requires parameters to be restored manually).

3. The drive package as specified herein and defined on the drive schedule shall be enclosed in a UL Type enclosure (enclosures with only NEMA ratings are not acceptable), completely assembled and tested by the manufacturer to ISO 9001 standards.

4. The drive shall provide full rated output from a line of +10% to –15% of nominal voltage. The drive shall continue to operate without faulting from a line of +25% to –35% of nominal voltage.

a. Drives shall be capable of continuous full load operation under the following environmental operating conditions: 

1) Ambient temperature –15 to 40°C (5 to 104°F).

2) Altitude 0 to 1000 m (0 to 3,300 ft) above sea level.

3) Humidity 5 to 95%, non-condensing.

5. All drives shall utilize the same Advanced Control Panel (keypad) user interface. 

a. Plain English text:

1) The display shall be in complete English words for programming and fault diagnostics (alpha-numeric codes are not acceptable). 

2) Safety interlock and run permissive status shall be displayed using predetermined application specific nomenclature, such as: Damper end switch, smoke alarm, vibration trip, and overpressure.

3) Safety interlock, run permissive, Supervisory, external fault status, drive name, drive fault contact info and override shall have the option of additional customized project specific terms, such as: AHU-1 End Switch, Office Smoke Alarm, CT-2 Vibration.

b. The control panel shall include at minimum the followings controls:

1) Four navigation keys (Up, Down, Left, Right) and two soft keys to simplify operation and programming.

2) Hand-Off-Auto selections and manual speed control without having to navigate to a parameter. 

3) Fault Reset and Help keys. The Help key shall include assistance for programming and troubleshooting. 

c. Multiple Home View screens shall be capable of displaying up to 21 points of information. Customizable modules shall include bar charts, graphs, meters, and data lists. Displays shall provide real time graphical trending of output power, frequency, and current within selectable intervals of 15/30/60 minutes and 24 hours.

d. The control panel shall display the following items on a single screen; output frequency, output current, reference signal, drive name, time, and operating mode (Hand vs Auto, Run vs Stop). Bi-color (red/green) status LED shall be included. Drive (equipment) name shall be customizable.

e. There shall be a built-in time clock in the control panel. The clock shall have a battery backup with 10 years minimum life span. Daylight savings time shall be selectable.

f. I/O Summary display with a single screen shall indicate and provide:

1) The status/values of all analog inputs, analog outputs, digital inputs, and relay outputs. Drives that require access to internal or live components to measure these values, are not acceptable. 

2) The programmed function of all analog inputs, analog outputs, digital inputs, and relay outputs.

3) The ability to force individual digital I/O high or low and individual analog I/O to desired value, for increased personal protection during drive commissioning and troubleshooting. Drives that require access to internal or live components to perform these functions, are not acceptable.

g. The drive shall automatically backup parameters to the control panel. In addition to the automatic backup, the drive shall allow two additional unique backup parameter sets to be stored. Backup files shall include a time and date stamp. In the event of a drive failure, the control panel of the original drive can be installed on the replacement drive, and parameters from that control panel can be downloaded into the replacement drive.

h. The control panel shall display local technical support contact information as part of drive fault status. 

i. The control panel shall be removable, capable of remote mounting (not available on compact VFD). 

j. The control panel shall have the ability to store screen shots, which are downloadable via USB.

k. The drive shall generate a QR code, which contains drive identification data, information on the latest events, and values of status and counter parameters. 

l. The LCD screen shall be backlit with the ability to adjust the screen brightness and contrast, with inverted contrast mode. A user-selectable timer shall dim the display and save power when not in use. 

m. The control panel shall include assistants specifically designed to facilitate start-up. Assistants shall include: First Start Assistant, Basic Operation, Basic Control, and PID Assistant.

n. Primary settings for HVAC shall provide quick set-up without the use of alpha-numerical parameters, for commissioning the drive and customer interfaces to reduce programming time.

o. The drive shall be able to operate with the control panel removed (compact VFD includes a non-removable keypad). 

p. The drive shall be able to support a Bluetooth Advanced Control Panel. The Bluetooth control panel shall be FCC and QDL (Qualified Design Listing) certified.

1) A free app (iOS and Android) shall replicate the control panel on a mobile device or tablet. The control panel’s programming and control functionality shall function on the device. Customizing text, such as AHU-1 End Switch, shall be supported by the device’s keyboard.

2) Bluetooth connectivity shall allow uploading, downloading, and emailing of parameter sets.

3) Bluetooth connectivity shall include two pairing modes: Always discoverable with a fixed passcode, and manual discovery with a unique generated passcode every pairing.

4) Bluetooth connectivity shall be capable of being switched.

6. All drives shall have the following hardware features/characteristics as standard:

a. Two (2) programmable analog inputs shall accept current or voltage signals. Current or Voltage selection configured via control panel. Drives that require access to internal components to perform these functions, are not acceptable.

b. Two (2) programmable analog outputs (one (1) analog output on compact VFD drives). At least one of the analog outputs shall be adjustable for current or voltage signal, configured via control panel. Drives that require access to internal components to perform these functions, are not acceptable.

c. Six (6) programmable digital inputs (four (4) digital inputs on compact VFD drives). All digital inputs shall be programmable to support both active high and active low logic, and shall include adjustable on/off time delays. The digital input shall be capable of accepting both 24 VDC and 24 VAC.

d. Three (3) programmable Form-C relay outputs (one (1) Form-C relay output on compact VDF drives). The relay outputs shall include programmable on/off time delays. The relays shall be rated for a continuous current rating of 2 Amps. Maximum switching voltage of 250 VAC / 30 VDC. Open collector and Form-A relays are not acceptable. Drives that have less than (3) Form-C relay outputs shall provide an option card to provide additional relay outputs.

e. Drive terminal blocks shall be color coded for easy identification of function.

f. The drive shall include an isolated USB port for interface between the drive and a laptop. A non-isolated USB port is not acceptable. 

g. An auxiliary power supply rated at 24 VDC, 250 mA shall be included.

h. At a minimum, the drives shall have internal impedance equivalent to 5% to reduce the harmonics to the power line. 5% impedance may be from dual (positive and negative DC link) chokes, or AC line reactor. Drives with only one DC link choke shall add an AC line choke integral to the drive enclosure (alternatively user can select a drive without 5% impedance). Reference the drive schedule to determine if additional harmonic mitigation is required for the system to comply with IEEE 519-2014. 

i. The drive shall have cooling fans that are designed for field replacement. The primary cooling fan shall operate only when required and be variable speed for increased longevity and lower noise levels. Drives whose primary cooling fans are not variable speed, shall include a spare cooling fan.

j. The overload rating of the drive shall be 110% of its normal duty current rating for 1 minute every 10 minutes, 135% overload for 2 seconds every minute. The minimum current rating shall meet or exceed the values in the NEC/UL table 430.250 for 4-pole motors.

k. The input current rating of the drive shall not be greater than the output current rating. Per NFPA 70 430.122, drives with higher input current ratings may require the upstream wiring, protection devices, and source transformers to be upsized.

l. Circuit boards shall be coated per IEC 60721-3-3; Chemical gases Class 3C2 and Solid particles Class 3S2. 

m. Earth (ground) fault detection shall function in both modulating (running) and non-modulating modes. 

n. Coordinated AC transient surge protection system consisting of 4 MOVs (phase-to-phase and phase-to-ground), a capacitor clamp, and internal chokes. The MOVs shall comply with UL 1449 4th Edition. Drives that do not include coordinated AC transient surge protection shall include an external TVSS/SPD (Transient Voltage Surge Suppressor/Surge Protection Device). 

o. The drive shall include a robust DC bus to provide short term power-loss ride through. The DC bus Joule to drive kVA ratio shall be 4.5 J/kVA or higher. An inertia-based ride through function should help maintain the DC bus voltage during power loss events. Drives with control power ride through only, are not acceptable. 

7. All drives shall have the following software features as standard:

a. A Fault Logger that stores the last 16 faults in non-volatile memory. 

1) The most recent 5 faults save at least 9 data points, including but not limited to: Time/date, frequency, DC bus voltage, motor current, DI status, temperature, and status words.

2) The date and time of each fault and fault reset attempt shall be stored in the Fault Logger. 

b. An Event Logger that stores the last 16 warnings or events that occurred, in non-volatile memory.

1) Events shall include, but not limited to: Warning messages, checksum mismatch, run permissive open, start interlock open, automatic reset of a fault, power applied, auto start command, auto stop command, modulating started, and modulating stopped.

2) The date and time of each event’s start and completion points shall be stored in the Event Logger.

3) The drive shall also provide the user the ability to configure what events to log for application specific requirements.

c. Programmable start method. Start method shall be selectable based on the application and function even if the motor was freewheeling in the reverse direction: Flying-start, Normal-start, and Brake-on-start.

d. Programmable loss-of-load (broken belt/coupling) indication. Indication shall be selectable as a control panel warning, relay output, or over network communications. This function to include a programmable time delay to eliminate false loss-of-load indications. 

e. The following three-phase AC motor technologies shall be compatible:

1) Asynchronous induction motors

2) Permanent magnet synchronous (non-salient pole) motor

3) Synchronous reluctance motor (SynRM)

4) Permanent magnet assisted synchronous reluctance motor (PMaSynRM)

f. Motor heating function to prevent condensation build up in the motor. Motor heating adjustment, via parameter, shall be in “Watts.” Heating functions based only on “percent current” are not acceptable.

g. Motor disconnect detection function enables the drive to detect when an output disconnect is opened, disable the drive output, and provide an indication message. Drives without this functionality shall have a disconnect switch auxiliary contact wired through dedicated conduit back to the drive enable control circuit.

h. Motor phase order shall be changeable through software interface.

i. Advanced power metering abilities shall be included in the drive and must be available over network communications. Drives without these data points, must include a separate power meter with each drive. 

1) Instantaneous output power (kW)

2) Total power, broken down by kWh, MWh, and GWh units of measurement. Power meters that only display kWh and roll over or “max out” once the maximum kWh value is reached, are not acceptable. There shall be resettable and non-resettable total power meters within the drive.

3) Time based kWh metering for: current hour, previous hour, current day, and previous day.

4) Energy saving calculation shall be included that shows the energy and dollars saved by the drive.

j. The drive shall include a motor flux optimization circuit that will automatically reduce applied motor voltage to the motor to optimize energy consumption and reduce audible motor noise. 

k. DC bus voltage ripple function shall provide a DC voltage reference for troubleshooting AC line issues or bus capacitor health.

l. Run permissive circuit - There shall be a run permissive circuit for damper or valve control. The drive shall provide a relay output to the damper actuator, monitor end-switch status, and start running the motor based on application requirements. Damper control shall include the following configurable features fully functional in both Hand and Auto modes: 

1) A timeout function that identifies and annunciates a specific warning message when a damper has not opened or closed within the allotted time.

2) Ability to interface with both damper open and damper closed end-switches on a single damper actuator.

3) Sequence control that runs the fan initially at a fixed speed before commanding a discharge air damper to open. Required for all applications feeding a common plenum/space to prevent the fan from freewheeling backwards while damper strokes open.

4) Multiple damper sequence control to support units with discharge air and outside air dampers. The drive shall command and verify the outside air damper is open before ramping the fan to a fixed speed, and then commanding the outside air damper open.

5) Time based damper control for when an end-switch is not provided. For units with outside air and discharge air dampers, both dampers should have independent time based control capability. 

m. Start interlock circuit - Four separate start interlock (safety) inputs shall be provided. When any safety is opened, the motor shall be commanded to stop. The control panel will display the specific safety(s) that are open. The status of each safety shall be transmitted over the network communications. Wiring multiple safeties in series is not acceptable.

n. External fault circuit - Three separate external fault inputs shall be provided. This circuit shall have the same features and functionality as the start interlock circuit, except it shall require a manual reset before the drive is allowed to operate the motor.

o. The drive shall provide automatic protections to allow uninterrupted operations at a reduced speed or switching frequency.

1) Switching frequency control circuit, that reduces the switching frequency based on actual drive temperature and allows higher switching frequency settings without derating the drive. It shall be possible to set a minimum and a target switching frequency. 

2) The drive shall include a temperature limit that when exceeded will reduce the drive output current.

3) Input phase loss protection shall be provided, whereas the output current is automatically derated by 50% if an input phase loss is detected by the drive. 

p. Visual function block adaptive programming allowing custom control schemes, minimizing the need for external controllers (i.e., cooling tower staging logic). A free software tool shall be used to configure adaptive programming.

q. The ability to automatically restart after an over-current, over-voltage, under-voltage, external fault, or loss of input signal protective trip. The number of restart attempts, trial time, and time between attempts shall be programmable. Each of these faults may have automatic restart individually disabled via a parameter selection.

r. Three (3) programmable critical frequency lockout ranges to prevent the drive from operating the load continuously at an unstable speed/load. 

s. The drive shall have three methods to control constant frequency/speed references:

1) Seven (7) programmable preset frequencies/speeds using (3) inputs. 

2) Six (6) different programmable preset frequencies/speed tied to 6 independent control inputs and requires an additional start command (four (4) independent control inputs on compact VFD drives).

3) Six (6) different programmable preset frequencies/speed tied to 6 independent control inputs and does not require any additional start command input (four (4) independent control inputs on compact VFD drives).

t. Two independently adjustable accel and decel ramps sets with 1 - 1800 seconds adjustable time ramps.

u. PID functionality shall be included in the drive. 

1) Programmable “Sleep” and “Wake up” functions to allow the drive to be started and stopped based on the level of a process feedback signal.

2) The drive shall include an independent PID loop for customer use, assigned to an Analog Output. This PID loop may be used for cooling tower bypass valve control, chilled water valve, etc. 

v. At least 4 parameter user sets that can be saved to the permanent memory and recalled using a digital input, timed function, or supervision function.

w. Drive shall be compatible with an accessory that allows the control board to be powered from an external 24 VDC/VAC source, allowing the drive control to remain powered by a UPS during an extended power outage (not applicable on compact VFD).

x. A computer-based software tool shall be available to allow a laptop to program the drive. The drive shall be able to support programming without the need for line voltage. All necessary power shall be sourced via the laptop USB port. 

y. The drive shall include a fireman’s override mode. Upon receipt of a contact closure from the Fire Alarm Life Safety system, the drive shall operate in a dedicated Override mode distinct and separate from the drive’s Normal operation mode. The following features will be available in the drive override function:

1) The Override mode shall be secured by passcode to prevent changes once programmed.

2) The drive shall ignore external inputs and commands not defined as part of the override function.

3) Override operation mode shall be selectable between: single frequency, multiple fixed frequencies, follow an analog input signal, PID control, or come to a forced stop. 

4) High priority safeties shall stop the drive and lower priority safeties shall be ignored in Override mode. 

5) Drive faults shall be defined in Critical and Low priority groups. Critical faults shall stop the drive. Low priority faults shall be reset. Reset trials and timing shall be programmable.

6) The drive shall be configurable to receive from 1 to 3 discrete digital input signals and operate at up to three discrete speeds. 

8. Security Features:

a. The drive manufacture shall clearly define cyber security capabilities for their products.

b. The drive shall include passcode protection against parameter changes.

1) There shall be multiple levels of passcode protection including: End User, Service, Advanced, and Override.

2) The drive shall support a customer generated unique passcode between 0 and 99,999,999.

3) The drive shall log an event whenever the drive passcode has been entered. 

4) The drive shall provide a security selection that prevents any “back door” entry. This selection even prevents the drive manufacturer from being able to bypass the security of that drive.

5) A security level shall be available that prevents the drive from being flashed with new firmware.

c. A checksum feature shall be used to notify the owner of unauthorized parameter changes made to the drive. The checksum feature includes two unique values assigned to a specific programming configuration. 

1) One checksum value shall represent all user editable parameters in the drive except communication setup parameters. A second checksum value shall represent all user editable parameters except communication setup, energy, and motor data parameters. 

2) Once the drive has been commissioned the two values can be independently saved in the drive. 

3) The drive shall be configurable to either: Log an Event, provide a Warning, or Fault upon a parameter change when the current checksum value does not equal the saved checksum value. 

d. The “Hand” and “Off” control panel buttons shall have the option to do the following:

1) Be individually disabled (via parameter) for drives mounted in public areas to prevent unauthorized changes.

2) Require a second button press of “Hand” and “Off” within 5 seconds of the original selection to confirm the change and prevent accidental transition out of “Auto” mode.

9. Network Communications:

a. The drive shall have an EIA-485 port with removable terminal blocks. The onboard protocols shall be BACnet®
 MS/TP, Modbus, and Johnson Controls N2. Optional communication cards for BACnet®/IP, LonWorks, Profibus, Profinet, EtherNet/IP, Modbus TCP, and DeviceNet shall be available. The use of third party gateways are not acceptable. 

b. The drive shall have independent end of line (EOL) termination and biasing switches for EIA-485 networks (not available con compact VFD). 

c. The drive shall contain EIA-485 network self-diagnostics to assist in troubleshooting issues such as incorrect polarity, incorrect baud rate, noise on the wire or addressing errors (not available on compact VFD). 

d. The drive shall have the ability to communicate via two protocols at the same time, one onboard protocol and one option card based protocol. Once installed, the drive shall automatically recognize any optional communication cards without the need for additional programming.

e. The drive shall not require a power cycle after communication parameters have been updated. 

f. The embedded BACnet® connection shall be a MS/TP interface. The drive shall be BTL Listed to Revision 14 or later. Use of non-BTL Listed drives are not acceptable. 

g. The drive shall be classified as an Applications Specific Controller (B-ASC). The interface shall support all BIBBs defined by the BACnet® standard profile for a B-ASC including, but not limited to:

1) Data Sharing: Read Property Multiple-B, Write Property Multiple-B, COV-B

2) Device Management: Time Synchronization-B

3) Object Type Support: MSV, Loop

h. The drive’s relay output status, digital input status, analog input/output values, Hand-Auto status, warning and fault information shall be capable of being monitored over the network. The drive’s start/stop command, speed reference command, relay outputs and analog outputs shall be capable of being controlled over the network. Remote drive fault reset shall be possible.

� Third-party trademarks and logos are the property of their respective owners.








1


1

