
Note about this specification:

This specification is in the “Masterformat” as published by the Construction Specification Institute. Please feel free to copy this specification directly into your building spec.

Weather Expert® High Outdoor Air Cooling Only or Electric Heat Packaged Rooftop

HVAC Guide Specifications:

Size Range: 6 to 10 Nominal Tons

Carrier Model Number: 50LC*H

·  23 06 80 Schedules for Decentralized HVAC Equipment

· 23 06 80.13 Decentralized Unitary HVAC Equipment Schedule

· 23 06 80.13.A. Rooftop unit schedule: 
Schedule is per the project specification requirements.

· 23 07 16 HVAC Equipment Insulation

· 23 07 16.13 Decentralized, Rooftop Units:

· 23 07 16.13.A. Indoor fan compartment:

1. Interior cabinet surfaces shall be insulated with a minimum 1/2 in. thick, minimum 1-1/2 lb density aluminum foil-faced insulation on the air side.

2. Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

3. Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

· 23 07 16.13.B. Electric heat compartment:

1. Aluminum foil-faced fiberglass insulation shall be used.

2. Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

· 23 09 13 Instrumentation and Control Devices for HVAC

· 23 09 13.23 Sensors and Transmitters:

· 23 09 13.23.A. Thermostats:

1. Thermostat must:

a. Have capability to energize 2 different stages of cooling and 2 different stages of heating.

2. Thermostat may:

a. Energize both “Y” and “G” when calling for cooling.

b. Energize both “H” and “G” when calling for dehumidification.

c. Energize “G” when calling for venting.

· 23 09 13.23.B. Sensors/Switches:

1. The unit shall include the following sensors/switches as factory-installed:

a. Return air temperature

b. Return air relative humidity

c. Outdoor air temperature

d. Outdoor relative humidity

e. Refrigerant circuit discharge pressure

f. Refrigerant circuit suction pressure

g. Refrigerant circuit high pressure switch

h. Condensate overflow switch

2. The unit shall include the following as factory provided, field installed:

a. Supply air temperature

· 23 09 23 Direct Digital Control (DDC) System for HVAC

· 23 09 23.13 Decentralized, Rooftop Units:

·  23 09 23.13.A. Carrier SmartVu™ integrated Direct Digital Control (DDC) shall:

1. Include a factory-installed, color, touch-screen control interface that is factory wired and mounted in the unit control panel and is no less than 6.75 in. diagonally and has an environmental range of –4°F (–20°C) to 158°F (70°C), non-condensing.

a. The control interface must:

1) Include an easy-to-understand menu with icon based navigation.

2) Include a combination of graphical and text base screens for status.

3) Include light colored backgrounds on screens. Black or dark gray backgrounds are not acceptable, due to poor visibility in daylight.

2. Have no less than three levels of user access with password protection, including basic access without password, password protected user access, and password protected service access. 

3.  Provide sensor/switch support for the factory installed sensors/switches listed in 23 09 13.23.B. Sensors/Switches, as well as the following field-installed sensors/switches:

a. Return CO2

b. Return or supply air smoke detector

c. Supply duct static pressure

d. Building static pressure

e. Space temperature

f. Space relative humidity

g. Space CO2

h. Mixed air temperature

i. Pre-filter status switch

j. Phase monitor

4. Provide support to the following field-provided control inputs:

a. 2-stage heat/cool thermostat (Y1, Y2, W1, W2, G)

b. Humidistat or thermostat dehumidification output (H)

c. Third-party outdoor air damper modulation (4-20mA)

d. Third-party indoor fan modulation (4-20mA)

e. Third-party exhaust fan modulation (4-20mA)

f. Remote shutdown/occupancy switch

g. Fire shutdown

5. Provide the following field use control outputs:

a. Alarm indicator

b. Damper override relay (heat, dehumidification, pre-occupancy operation)

6. Be capable of fully stand-alone, 2-stage heat/cool thermostat, Third-party DDC input control, or networked operation.

7. Provide control configurations for the following occupancy sources:

a. Local schedule

b. Occupancy switch

c. Network occupancy input

8. Provide network communication compatibility with the following protocols:

a. Carrier Comfort Network® (CCN)

b. BACnet MS/TP

c. BACnet IP

9. Establish demand for cooling or heating based on occupancy status, a demand source, and the source temperature. The control must:

a. Provide configurations for the following cooling/heating demand sources:

1) Space temperature

2) Outdoor air temperature

3) Thermostat or third-party switch inputs

b. Limit control setpoints, settings, and configurations based on the demand source configuration.

c. Provide configurations to disable heating and cooling during the unoccupied period.

d. Provide user configurable temperature setpoints for the occupied and unoccupied periods, if allowed by the demand source.

e. Provide a user configurable supply air temperature setpoint for each demand.

10. Select a cooling or heating (if equipped) mode based on the supply air temperature setpoint established by the cooling or heating demand, the measured or calculated mixed air temperature, the unit configuration, the control settings, and cooling and heating system availability. The control must:

a. Operate the cooling or heating (if equipped) systems based on the supply air temperature setpoint established by the cooling/heating demand.

b. Provide a user configurable compressor lockouts based on outdoor air temperature and mixed air temperature.

c. Provide a user configurable heating (if equipped) lockout based on outdoor air temperature.

11. Establish a demand for dehumidification based on occupancy status, a demand source, and the source humidity. The control must:

a. Provide configurations to prevent dehumidification in the unoccupied period.

b. Provide configurations for the following dehumidification demand sources:

1) Space relative humidity sensor

2) Return air relative humidity

3) Outdoor air dewpoint

4) Humidistat, thermostat dehumidify switch, or third-party switch input

12. Select a dehumidification mode depending on the cooling coil temperature control from the dehumidification demand, the supply air temperature control point from the cooling or ventilation demand, the unit configuration, the control settings, and the dehumidification system availability. The control must:

a. Operate the cooling systems based on the cooling coil temperature control point established by the dehumidification demand and operate the hot gas reheat system based on the supply air temperature control point established by the cooling or ventilation demand.

13. Provide the following indoor fan speed control configurations, depending on the unit configuration and cooling/heating demand source:

1) Constant speed

2) Staged speeds based on demand (staged air volume, SAV™)

3) Variable speeds based on duct static pressure

4) Variable speeds based on building static pressure

14. Provide operation of the unit exhaust fan (if equipped).

a. Provide the following exhaust fan speed control configurations, depending on the unit configuration:

1) Two speeds based on outdoor air damper position

2) Variable speeds based on building pressure

15. Provide operation of the outdoor air damper (if equipped).

a. Provide outdoor air damper fault detection and diagnostics (FDD) in accordance with California Title 24 and ASHRAE 90.1 requirements, if allowed by the demand source. 

b. Provide configurations to disable free cooling with outdoor air based on the following:

1) Outdoor air temperature

2) Outdoor air enthalpy, outdoor air vs. return air enthalpy, or outdoor air vs. return air temperature

3) Outdoor air dewpoint

c. Provide configurations to operate the outdoor air damper position based on:

1) Two-position (closed and 100% OA)

2) Indoor speed mapping

3) A third-party control signal

16. Provide the following alarm capability:

a. Display current active alarm on the home screen.

b. Record the time and date of alarms.

c. Provide an alarm history of the latest 50 alarms.

17.  Provide the following service capability:

a. Display the refrigerant suction and discharge pressure sensor readings on the control interface and over network points, without the need for field provided gauges.

b. Allow trending of unit temperature, pressures, and status/display trends on the control interface.

c. Include a component test mode to allow testing of individual components (if equipped), including the indoor fan, condenser fans, exhaust fan, and outdoor air damper.

d. Include a service run mode to allow testing of unit systems, including the cooling system, heating system, and reheat system.

e. Record run hours and starts for key components, such as compressors, the supply fan, and heating system.

· 23 09 33 Integrated Staging Control (ISC) Board System for HVAC (Electro-Mechanical units)

· 23 09 33.13 Decentralized, Rooftop Units:

· 23 09 33.13.A. General:

1. Shall be complete with self-contained low-volt-age control circuit protected by a resettable circuit breaker on the 24-v transformer side. Transformer shall have 75VA capability.

2. Shall utilize color-coded wiring.

3. Shall include a control and power wiring diagram affixed to the control panel door. 

· 23 09 93 Sequence of Operations for HVAC Controls

· 23 09 93.13 Decentralized, Rooftop Units:

· 23 09 93.13.A. INSERT SEQUENCE OF OPERA-TION

· 23 40 13 Panel Air Filters

· 23 40 13.13 Decentralized, Rooftop Units:

· 23 40 13.13.A. Standard filter section

1. Shall consist of factory-installed, low velocity, throwaway 2 in. thick fiberglass filters of commercially available sizes.

2. Filters shall be accessible through an access panel with “no-tool” removal as described in the unit cabinet section of this specification
(See Part 8 — 23 81 19.13.G).

· 23 81 19 Self-Contained Air Conditioners

· 23 81 19.13 Small-Capacity Self-Contained Air Conditioners (50LC*H 07-12):

· 23 81 19.13.A. General:

1. Outdoor, rooftop mounted, ISC electrically con-trolled, heating and cooling unit utilizing hermetic scroll compressors for cooling duty and optional electric heat for heating duty.

2. Factory assembled, single-piece heating and cooling rooftop unit. Contained within the unit enclosure shall be all factory wiring, piping, controls, and special features required prior to field start-up.

3. Unit shall use Puron® (R-410A) refrigerant.

4. Unit shall be installed in accordance with the manufacturer’s instructions.

5. Unit must be selected and installed in compliance with local, state, and federal codes.

· 23 81 19.13.B. Quality Assurance:

1. Unit meets and exceeds ASHRAE 90.1-2013 minimum efficiency requirements.

2. Unit shall be rated in accordance with AHRI Standards 340/360.

3. Unit shall be designed to conform to ASHRAE 15, 2001.

4. Unit shall be ETL/UL-tested and certified in accordance with ANSI Z21.47 Standards and UL-listed and certified under Canadian standards as a total package for safety requirements.

5. Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.

6. Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

7. Unit casing shall be capable of withstanding 500 hour salt spray exposure per ASTM B117 (scribed specimen).

8. Roof curb shall be designed to conform to NRCA Standards.

9. Unit shall be subjected to a completely auto-mated run test on the assembly line. The data for each unit will be stored at the factory, and must be available upon request.

10. Unit shall be designed in accordance with UL Standard 1995, including tested to withstand rain.

11. Unit shall be constructed to prevent intrusion of snow and tested to prevent snow intrusion into the control box up to 40 mph.

12. Unit shake tested to assurance level 1, ASTM D4169 to ensure shipping reliability.

13. High-Efficiency Motors listed shall meet section 313 of the Energy Independence and Security Act of 2007 (EISA 2007).

· 23 81 19.13.C. Delivery, Storage, and Handling:

1. Unit shall be stored and handled per manufacturer’s recommendations.

2. Lifted by crane requires either shipping top panel or spreader bars.

3. Unit shall only be stored or positioned in the upright position.

· 23 81 19.13.D. Project Conditions:

1. As specified in the contract.

· 23 81 19.13.E. Operating Characteristics:

1. Unit shall be capable of starting and running at 115°F (46°C) ambient outdoor temperature, meeting maximum load criteria of AHRI Standard 340/360 at ±10% voltage.

2. Compressor with standard controls shall be capable of operation down to 40°F (4°C) ambient outdoor temperatures. Low ambient cooling operation may be additional limited by entering air conditions.

3. Unit shall discharge supply air vertically or horizontally as shown on contract drawings.

4. Unit shall be factory configured for vertical supply and return configurations.

5. Unit shall be field convertible from vertical to horizontal airflow on all models. No special kit required on 07 models. Field-installed supply duct kit required for 08-12 size models only.

6. Unit shall be capable of mixed operation vertical supply with horizontal return or horizontal supply with vertical return.

· 23 81 19.13.F. Electrical Requirements:

Main power supply voltage, phase, and frequency must match those required by the manufacturer.

· 23 81 19.13.G. Unit Cabinet:

1. Unit cabinet shall be constructed of galvanized steel, and shall be bonderized and coated with a pre-painted baked enamel finish on all externally exposed surfaces.

2. Unit cabinet exterior paint shall be: 

Film thickness, (dry) 0.003 inches minimum, gloss (per ASTM D523, 60°F / 16°C): 60, Hardness: H-2H Pencil hardness.

3. Evaporator fan compartment interior cabinet insulation shall conform to AHRI Standards 340/360 minimum exterior sweat criteria. Interior surfaces shall be insulated with a minimum 1/2 in. thick, 1 lb density, aluminum foil-faced fiberglass insulation. Aluminum foil-faced fiberglass insulation shall also be used in the heat compartment.

4. Unit internal insulation linings shall be resistant to mold growth in accordance with “mold growth and humidity” test in ASTM C1338, G21, and UL 181 or comparable test method. Air stream surfaces shall be evaluated in accordance with the “Erosion Test” in UL 181, as part of ASTM C1071.

5. Base Rail:

a. Unit shall have base rails on a minimum of 4 sides.

b. Holes shall be provided in the base rails for rigging shackles to facilitate maneuvering and overhead rigging.

c. Holes shall be provided in the base rail for moving the rooftop by fork truck.

d. Base rail shall be a minimum of 16 gauge thickness.

6. Condensate pan and connections:

a. Shall be an internally sloped condensate drain pan made of a non-corrosive material.

b. Shall comply with ASHRAE Standard 62.

c. Shall use a 3/4 in. -14 NPT drain connection, possible either through the bottom or end of the drain pan. Connection shall be made per manufacturer’s recommendations.

7. Top panel:

Shall be a single piece top panel on 07 sizes, 2 piece on 08-12 sizes.

8. Electrical Connections:

a. All unit power wiring shall enter unit cabinet at a single, factory-prepared, knockout location.

b. Thru-the-base capability:

1) Standard unit shall have a thru-the-base electrical location(s) using a raised, embossed portion of the unit basepan.

2) Optional, factory-approved, water-tight connection method must be used for thru-the-base electrical connections.

3) No basepan penetration, other than those authorized by the manufacturer, is permitted.

9. Component access panels (standard):

a. Cabinet panels shall be easily removable for servicing.

b. Unit shall have one factory-installed, tool-less, removable, filter access panel.

c. Panels covering control box, indoor fan, indoor fan motor, gas components (where applicable), and compressors shall have molded composite handles.

d. Handles shall be UV modified, composite, permanently attached, and recessed into the panel.

e. Panels covering the control box, filter, fan motor, and compressor shall be hinged and include quarter turn latches.

f. Screws on the vertical portion of all removable access panel shall engage into heat resistant, molded composite collars.

g. Collars shall be removable and easily replaceable using manufacturer recommended parts.

· 23 81 19.13.H. Coils:

1. Standard Aluminum Fin/Copper Tube Coils:

a. Standard evaporator, hot gas reheat, and condenser coils shall have aluminum lanced plate fins mechanically bonded to seamless internally grooved 5/16 in. diameter copper tubes with all joints brazed.

b. Evaporator and hot gas reheat coils shall be leak tested to 150 psig, pressure tested to 450 psig, and qualified to UL 1995 burst test at 1775 psig.

c. Condenser coils shall be leak tested to 150 psig, pressure tested to 650 psig, and quali-fied to UL 1995 burst test at 1980 psig.

· 23 81 19.13.I. Refrigerant Components:

1. Refrigerant circuit shall include the following control, safety, and maintenance features:

a. Thermostatic Expansion Valve (TXV) shall help provide optimum performance across the entire operating range. Shall contain removable power element to allow change out of power element and bulb without removing the valve body.

b. Refrigerant filter drier - solid core design.

c. Service gauge connections on suction and discharge lines.

d. Single circuit design with tandem compressor and fully activated evaporator coil.

1) Fully modulating low load protection valve that reduces the effective system capacity by redirecting discharge gas into the suction inlet. 2-position low load protection valves, such as hot gas bypass or suction shutoff valves are not acceptable. Low load protection valves that direct discharge gas into the evaporator are not acceptable. 

2) Fully modulating, three-way hot gas reheat valve that directs discharge gas between the condenser and the hot gas reheat coil. On/off or two position hot gas reheat valves are not acceptable.

a) If the hot gas reheat valve shall periodically modulate its highest hot gas reheat output to purge oil that may be entrapped in the hot gas reheat coil.

2. Compressors:

a. Models shall use a minimum of two fully hermetic scroll compressors in a tandem compressor configuration. Single compressor models are not acceptable.

b. Models shall be available with a single refrigerant circuit and a minimum of 3 stages of cooling operation.

1) The compressor shall be capable of operating for a minimum of 2-1/2 hours at it’s lowest stage of operation without the need to increase compressor capacity or speed for the purpose of oil returns.

2) Models that include inverter or variable frequency drive compressors shall include an isolation transformer.

c. Compressor motors shall be cooled by refrigerant gas passing through motor windings.

1) Models that include inverter or variable frequency drive compressors shall also include a refrigerant cooled inverter or VFD.

d. Compressors shall be internally protected from high discharge temperature conditions.

e. Compressors shall be protected from an over-temperature and over-amperage conditions by an internal, motor overload device.

f. Compressor shall be factory mounted on rubber grommets.

g. Compressor motors shall have internal line break thermal, current overload and high pressure differential protection.

h. Crankcase heater shall be standard on each compressor and deactivated whenever a compressor is in operation.

· 23 81 19.13.J. Filter Section:

1. Filter access is specified in the unit cabinet section of this specification.

2. Filters shall be held in place by a pivoting filter tray, facilitating easy removal and installation.

3. Shall consist of factory-installed, low velocity, throw-away 2 in. thick fiberglass filters.

4. Filters shall be standard, commercially available sizes.

5. Only one size filter per unit is allowed.

· 23 81 19.13.L. Indoor Fan and Motor with Eco-Blue™ Technology:

1. Direct Drive Evaporator Fan Motor:

a. Shall have permanently lubricated bearings.

b. Shall have inherent automatic-reset thermal overload protection.

c. Shall be an electronically commutated motor (ECM).

d. Shall have slow ramp up to speed capabilities.

e. Shall not include a belt or sheave system.

f. Shall be internally protected from electrical phase reversal and loss.

g. Motor speed setup and control setup shall be accomplished using the SmartVu™ control.

h. Medium static motor option shall include a minimum 2.4 HP motor and provide up to 2 in. wg external static capability at up to 350 cfm/ton.

2. Indoor Fan:

a. Speed control shall be easily setup from the SmartVu™ control interface. Control configurations shall include:

1) Staged Air Volume (SAV™)

2) Constant volume

3) Variable Air Volume (VAV) duct pressure control

4) Variable Air Volume (VAV) space pressure control

5) Third-party input control

b. Shall be a vane axial fan design with 75% less moving parts than a conventional belt drive system.

c. Shall be constructed of a cast aluminum stator and high impact composite material on rotor and air inlet casing.

d. Shall be patented/patent pending design with a corrosion resistant material and dynamically balanced.

e. Shall have slow ramp up to speed capabilities to help reduce sound and comfort issues typically associated with single speed belt drive systems.

f. Shall be a slide out design with simple screw removal.

g. Fans shall be capable of operating up to 350 cfm/tons.

h. Fans shall be capable of operating down to 130 cfm/tons.

· 23 81 19.13.L. Condenser Fans and Motors:

1. Condenser fan motors:

a. Shall be a totally enclosed – multi-speed ECM motor.

b. Shall use permanently lubricated bearings.

c. Shall have inherent thermal overload protection with an automatic reset feature.

d. Shall use a shaft-down design on 07 models and shaft-up on 08-12 models with rain shield.

2. Condenser Fans:

a. Shall be a direct-driven propeller type fan.

b. Shall have galvanized aluminum (galvalum) blades riveted to corrosion-resistant steel spiders and shall be dynamically balanced.

· 23 81 19.13.N. Special Features Options and Accessories:

1. Electric Heat (factory-installed):

a. Heating Section:

1) Unit shall include a factory-installed electric heater. Electric heater power shall be provided by the main unit power feed (single point power). 

2) Heater element open coil resistance wire, nickel-chrome alloy, strung through ceramic insulators mounted on metal frame. Coil ends are staked and welded to terminal screw slots.

3) Heater assemblies are provided with integral fusing for protection of internal heater circuits not exceeding 48 amps each. Auto reset thermo limit controls, magnetic heater contactors (24-v coil) and terminal block all mounted in electric heater control box (minimum 18 ga galvanized steel) attached to end of heater assembly.

4) Heater shall include a silicon rectifier control (SCR) for modulated heater output. Staged electric heaters or solid state relay (SSR) heaters are not acceptable. 

5) The heater shall include an alarm relay to indicate a high temperature limit switch trip on the SmartVu™ display.

2. High Static Indoor Fan Motor (factory-installed):

a. Shall include a minimum 5 HP motor and provide up to 3 in. wg external static capability at up to 350 cfm/ton.

3. Duct Pressure Control:

a. Shall include a factory-installed duct pressure transducer for supply fan speed modulation based on duct static pressure. 

b. Pneumatic tubing and pressure pickup port are field supplied.

4. Zone Static Pressure Control:

a. Shall include a factory-installed building static pressure transducer for supply fan speed modulation based on zone static pressure. 

b. Pneumatic tubing and pressure pickup port are field supplied.

5. Pre-coated aluminum-fin condenser coils:

a. Shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments.

b. Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube.

c. Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.

d. Corrosion durability of fin stock shall be confirmed through testing to be no less than 1000 hours salt spray per ASTM B117-90.

e. Corrosion durability of fin stock shall be confirmed through testing to have no visible corrosion after 48 hour immersion in a room temperature solution of 5% salt, 1% acetic acid.

f. Fin stock coating shall pass 2000 hours of the following: 

1) One week exposure in the prohesion chamber followed by one week of accelerated ultraviolet light testing. 

a) Prohesion chamber: the solution shall contain 3.5% sodium chloride and 0.35% ammonium sulfate. The exposure cycle is one hour of salt fog application at ambient followed by one hour drying at 95°F (35°C).

6. Optional e-coated aluminum-fin indoor air and/or condenser coils:

a. Shall be available as factory-installed on the indoor air coils (evaporator and hot gas reheat) and or condenser coils.

b. Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins.

c. Coating process shall ensure complete coil encapsulation of tubes, fins and headers.

d. Color shall be high gloss black with gloss per ASTM D523-89.

e. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges.

f. Superior hardness characteristics of 2H per ASTM D3363-92A and cross-hatch adhesion of 4B-5B per ASTM D3359-93.

g. Impact resistance shall be up to 160 in.-lb (ASTM D2794-93).

h. Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92).

i. Corrosion durability shall be confirmed through testing to be no less than 6000 hours salt spray per ASTM B117-90.

7. Condenser Coil Hail Guard Assembly (factory or field installed):

a. Shall protect against damage from hail.

b. Shall be louvered design.

8. Ultra-Low Leak Economizers (factory or field-installed):

a. Available as a factory-installed option (vertical only) or field-installed accessory (vertical or horizontal) on most models. 

b. Ultra-Low Leak economizer dampers meet California’s Title 24 section 140.4 prescriptive requirements for leakage, reliability testing, etc., and ASHRAE 90.1-2013 requirements for damper leakage.

c. Economizers are available with EconoMi$er®2 controls for SmartVu units.

d. Integrated, gear driven opposed blade design type capable of simultaneous economizer and compressor operation.

e. Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.

f. Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.

g. Shall be capable of introducing up to 100% outdoor air.

h. Economizer’s barometric relief dampers shall be sized to allow up to 100% relief (actual results will be based on specific job conditions).

1) EconoMi$er®2 Economizer Controls:

a) For use with factory-installed (vertical only) or field-installed accessory (vertical or horizontal) on all SmartVu units.

b) EconoMi$er2 economizers are controlled by SmartVu, which shall be 4 to 20mA design.

c) SmartVu controls meet California’s Title 24 section 120.2 mandatory requirements for economizer Fault Detection and Diagnosis.

d) The control shall include all sensors to provide free cooling economizer operation based on dry bulb, enthalpy, differential dry bulb, or differential enthalpy changeover control and dewpoint cutoff.

e) Shall be designed to spring return close outside air damper during loss of power.

f) Actuator shall be direct coupled to economizer gear. No linkage arms or control rods shall be acceptable.

g) The economizer shall maintain minimum airflow into the building during occupied period and provide design ventilation rate for full occupancy.

h) Controller shall drive outside air dampers completely closed when the unit is in the unoccupied period.

9. Unit-Mounted, Non-Fused Disconnect Switch (factory-installed):

a. Switch shall be factory-installed, internally mounted.

b. National Electric Code (NEC) and ETL/UL approved non-fused switch shall provide unit power shutoff.

c. Shall be accessible from outside the unit.

d. Shall provide local shutdown and lockout capability.

e. Sized only for the unit as ordered from the factory. Does not accommodate field-installed devices.

10. HACR Breaker (factory-installed):

a. These manual reset devices provide overload and short circuit protection for the unit. Factory wired and mounted with the units, with access cover to help provide environmental protection. On 575-v applications, HACR breaker can only be used with WYE power distribution systems. Use on Delta power distribution systems is prohibited.

b. Sized only for the unit as ordered from the factory. Does not accommodate field-installed devices.

11. Convenience Outlet (factory-installed):

a. Powered convenience outlet:

1) Outlet shall be powered from main line power to the rooftop unit.

2) Outlet shall be powered from line side or load side of disconnect by installing contractor, as required by code. If outlet is powered from load side of disconnect, unit electrical ratings shall be ETL/UL certified and rated for additional outlet amperage.

3) Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.

4) Outlet shall include 15 amp GFI receptacles with independent fuse protection.

5) Voltage required to operate convenience outlet shall be provided by a factory-installed step-down transformer.

6) Outlet shall be accessible from outside the unit.

7) Outlet shall include a field-installed “Wet in Use” cover.

b. Non-powered convenience outlet:

1) Outlet shall be powered from a separate 115/120-v power source.

2) A transformer shall not be included.

3) Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.

4) Outlet shall include 15 amp GFI receptacles with independent fuse protection.

5) Outlet shall be accessible from outside the unit.

6) Outlet shall include a field-installed “Wet in Use” cover.

12. Roof Curbs (field-installed):

a. Full perimeter roof curb with exhaust capability providing separate air streams for energy recovery from the exhaust air without supply air contamination.

b. Formed galvanized steel with wood nailer strip and shall be capable of supporting entire unit weight.

c. Permits installation and securing of ductwork to curb prior to mounting unit on the curb.

13. Thru-the-Bottom Utility Connectors (factory or field-installed):

a. Kit shall provide connectors to permit electrical and gas connections to be brought to the unit through the basepan.

14. Indoor Air Quality (CO2) Sensor (factory or field-installed):

a. Shall be able to provide demand ventilation indoor air quality (IAQ) control.

b. The IAQ sensor shall be available in duct mount, wall mount, or wall mount with LED display. The setpoint shall have adjustment capability.

15. Smoke Detectors (factory or field-installed):

a. Shall be a 4-wire controller and detector.

b. Shall be environmental compensated with differential sensing for reliable, stable, and drift-free sensitivity.

c. Shall use magnet-activated test/reset sensor switches.

d. Shall have tool-less connection terminal access.

e. Shall have a recessed momentary switch for testing and resetting the detector.

f. Controller shall include:

1) One set of normally open alarm initiation contacts for connection to an initiating device circuit on a fire alarm control panel.

2) Two Form-C auxiliary alarm relays for interface with rooftop unit or other equipment.

3) One Form-C supervision (trouble) relay to control the operation of the Trouble LED on a remote test/reset station.

4) Capable of direct connection to two individual detector modules.

5) Can be wired to up to 14 other duct smoke detectors for multiple fan shutdown applications.

16. Horn/Strobe Annunciator (field-installed):

a. Provides an audible/visual signaling device for use with factory-installed option or field-installed accessory smoke detectors.

1) Requires installation of a field-supplied 24‑v transformer suitable for 4.2 VA (AC) or 3.0 VA (DC) per horn/strobe accessory.

2) Requires field-supplied electrical box, North American 1-gang box, 2 in. (51 mm) x 4 in. (102 mm).

3) Shall have a clear colored lens.

17. Double Wall Construction (factory-installed):

a. The indoor air touching sections of the unit interior, including top, sides, and base pan, shall be covered with a galvanized steel liner over the R4 foil faced fiberglass insulation

18. Supply Duct Kit (field-installed):

a. On 08-12 models, a supply air duct cover kit is required when field converting the factory standard vertical duct supply to horizontal duct supply configuration. One required per unit.

19. 4 in. Filter Rack (factory or field-installed):

a.  Shall include a field or factory-installed filter rack that accepts nominal 4 in. filters.

b. Shall include factory or field-installed nominal 4 in. MERV 8 filters.

c. Shall include factory or field installed nominal 4 in. MERV 13 filters.

1


1

