GUIDE SPECIFICATIONS – 50LC**14-26
Note about this specification:
These specifications are written in “Masterformat” as published by the Construction Specification Institute. Please feel free to copy this specification directly into your building spec.
WeatherExpert™ Ultra High Efficient Cooling Only/Electric Heat Packaged Rooftop

HVAC Guide Specifications

Size Range:		12.5 to 23 Nominal Tons

Section	Description
23 06 80	Schedules for Decentralized HVAC Equipment
		23 06 80.13	Decentralized Unitary HVAC Equipment Schedule
		23 06 80.13.A.	Rooftop unit schedule
	1.	Schedule is per the project specification requirements.
23 07 16	HVAC Equipment Insulation
		23 07 16.13	Decentralized, Rooftop Units:
		23 07 16.13.A.	Evaporator fan compartment:
	1.	Interior cabinet surfaces shall be insulated with a minimum 1/2-in. thick, minimum 1 1/2 lb density aluminum foil-faced insulation on the air side.
	2.	Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.
		23 07 16.13.B.	Electric heat compartment:
	1.	Aluminum foil-faced fiberglass insulation shall be used.
	2.	Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.
23 09 13	Instrumentation and Control Devices for HVAC
		23 09 13.23	Sensors and Transmitters
		23 09 13.23.A.	Thermostats
	1.	Thermostat must
	a.	energize both “W” and “G” when calling for heat.
	b.	have capability to energize 3 different stages of cooling, and 2 different stages of heating.
	c.	include capability for occupancy scheduling.
23 09 33	Integrated Staging Control (ISC) System for HVAC
		23 09 33.13	Decentralized, Rooftop Units:
		23 09 33.13.A.	General:
	1.	Shall be complete with self-contained low-voltage control circuit protected by a resettable circuit breaker on the 24-v transformer side. Transformer shall have 75VA capability.
	2.	Shall utilize color-coded wiring.
	3.	Shall include an ISC electro-mechanical control board, to conveniently and safely provide connection points for vital control functions such as: smoke detectors, phase monitor, gas controller, economizer, thermostat, and safety switches.  Shall control all three stages of compressor logic, two or three stages of the indoor fan motor logic as well as staging of the outdoor fan motor. Shall also have a green LED indicator to indicate GO operation as well as a fault LED indicator for thermostat mis-wiring, no fan operation and safety switches
	4.	Unit shall include a minimum of one 8-pin screw terminal connection board for connection of control wiring.
23 09 33.23.B.	Safeties:
	1.	Compressor over-temperature, over current.
	2.	Low-pressure switch. 
	a.	Low pressure switch shall use different color wire than the high pressure switch. The purpose is to assist the installer and service technician to correctly wire and or troubleshoot the rooftop unit.
	3.	High-pressure switch.
	a.	High pressure switch shall use different color wire than the low pressure switch. The purpose is to assist the installer and service technician to correctly wire and or troubleshoot the rooftop unit.
	4.	Automatic reset, motor thermal overload protector.
23 09 93	Sequence of Operations for HVAC Controls
		23 09 93.13	Decentralized, Rooftop Units:
		23 09 93.13	INSERT SEQUENCE OF OPERATION
23 40 13	Panel Air Filters
		23 40 13.13	Decentralized, Rooftop Units:
		23 40 13.13.A.	Standard filter section 
	1.	Shall consist of factory-installed, low velocity, throwaway 2-in. thick fiberglass filters of commercially available sizes.
	2.	Unit shall use only one filter size. Multiple sizes are not acceptable. 
	3.	Filters shall be accessible through a dedicated, weather tight panel.
	4.	4-in filter capabilities shall be capable with pre-engineered and approved Carrier filter track field installed accessory. This kit requires field furnished filters.
23 81 19	Self-Contained Air Conditioners
		23 81 19.13	Medium-Capacity Self-Contained Air Conditioners (50LC*D14-26)
		23 81 19.13.A.	General
	1.	Outdoor, rooftop mounted, DDC electrically controlled, heating and cooling unit utilizing hermetic scroll compressors for cooling duty and gas combustion for heating duty.
	2.	Factory assembled, single-piece heating and cooling rooftop unit. Contained within the unit enclosure shall be all factory wiring, piping, controls, and special features required prior to field start-up.
	3.	Unit shall use environmentally safe, Puron refrigerant.
	4.	Unit shall be installed in accordance with the manufacturer’s instructions.
	5.	Unit must be selected and installed in compliance with local, state, and federal codes.
		23 81 19.13.B.	Quality Assurance
	1.	Unit meets and exceeds ASHRAE 90.1 minimum efficiency requirements. 
	2.	Unit meets and exceeds Energy Star and Consortium for Energy Efficiency (CEE) requirements.
	3.	Unit shall be rated in accordance with AHRI Standard 340/360.
	4.	Unit shall be designed to conform to ASHRAE 15.
	5.	Unit shall be ETL-tested and certified in accordance with ANSI Z21.47 Standards and ETL-listed and certified under Canadian standards as a total package for safety requirements.
	6.	Insulation and adhesive shall meet NFPA 90A requirements for flame spread and smoke generation.
	7.	Unit casing shall be capable of withstanding 500-hour salt spray exposure per ASTM B117 (scribed specimen).
	8.	Unit shall be designed and manufactured in accordance with ISO 9001.
	9.	Roof curb shall be designed to conform to NRCA Standards.
	10.	Unit shall be subjected to a completely automated run test on the assembly line. The data for each unit will be stored at the factory, and must be available upon request.
	11.	Unit shall be designed in accordance with UL Standard 1995, including tested to withstand rain.
	12.	Unit shall be constructed to prevent intrusion of snow and tested to prevent snow intrusion into the control box up to 40 mph.
	13.	Unit shake tested to assurance level 1, ASTM D4169 to ensure shipping reliability.
	14.	High Efficient Motors listed shall meet section 313 of the Energy Independence and Security Act of 2007 (EISA 2007)
		23 81 19.13.C.	Delivery, Storage, and Handling
	1.	Unit shall be stored and handled per manufacturer’s recommendations.
	2.	Lifted by crane requires either shipping top panel or spreader bars.
	3.	Unit shall only be stored or positioned in the upright position.
		23 81 19.13.D.	Project Conditions
	1.	As specified in the contract.
		23 81 19.13.E.	Project Conditions
	1.	As specified in the contract.
		23 81 19.13.F.	Operating Characteristics
	1.	Unit shall be capable of starting and running at 125°F (52°C) ambient outdoor temperature, meeting maximum load criteria of AHRI Standard 340/360 at ± 10% voltage.
	2.	Compressor with standard controls shall be capable of operation from 40°F (4°C) , ambient outdoor temperatures. For lower operation an integrated economizer shall be utilized to allow lower temperatures and accommodate indoor air quality initiatives 
	3.	Unit shall discharge supply air vertically or horizontally as shown on contract drawings.
	4.	Unit shall be factory configured and ordered for vertical supply & return configurations.
	5.	Unit shall be factory furnished for either vertical or horizontal configuration without the use of special conversion kits. No field kits conversion is possible.
	6.	Unit shall be capable of mixed operation: vertical supply with horizontal return or horizontal supply with vertical return.
		23 81 19.13.G.	Electrical Requirements
	1.	Main power supply voltage, phase, and frequency must match those required by the manufacturer. 
		23 81 19.13.H.	Unit Cabinet
	1.	Unit cabinet shall be constructed of galvanized steel, and shall be bonderized and coated with a pre-painted baked enamel finish on all externally exposed surfaces.
	2.	Unit cabinet exterior paint shall be: film thickness, (dry) 0.003 inches minimum, gloss (per ASTM D523, 60°F): 60, Hardness: H-2H Pencil hardness.
	3.	Evaporator fan compartment interior cabinet insulation shall conform to AHRI Standards 340/360 minimum exterior sweat criteria. Interior surfaces shall be insulated with a minimum 1/2-in. thick, 1 lb density aluminum foil faced fiberglass insulation. Aluminum foil-faced fiberglass insulation shall also be used in the heat compartment.
	4.	Base of unit shall have a minimum of four locations for factory thru-the-base electrical connections. Connections shall be internal to the cabinet to protect from environmental issues.
	5.	Base Rail
	a.	Unit shall have base rails on a minimum of 2 sides.
	b.	Holes shall be provided in the base rails for rigging shackles to facilitate maneuvering and overhead rigging.
	c.	Holes shall be provided in the base rail for moving the rooftop by fork truck.
	d.	Base rail shall be a minimum of 16 gauge thickness.
	6.	Condensate pan and connections:
	a.	Shall be a sloped condensate drain pan made of a non-corrosive material.
	b.	Shall comply with ASHRAE Standard 62. 
	c.	Shall use a 3/4-in -14 NPT drain connection at the end of the drain pan. Connection shall be made per manufacturer’s recommendations.
	7.	Top panel:
	a.	Shall be a multi-piece top panel linked with water tight flanges and interlocking systems.
	8.	Electrical Connections
	a.	All unit power wiring shall enter unit cabinet at a single, factory-prepared, knockout location.
	b.	Thru-the-base capability
	(1.)	Thru-the-base provisions/connections are available as standard with every unit. When bottom connections are required, field furnished couplings are required.
	(2.)	No basepan penetration, other than those authorized by the manufacturer, is permitted.
	9.	Component access panels (standard)
	a.	Cabinet panels shall be easily removable for servicing.
	b.	Unit shall have one factory installed, tool-less, removable, filter access panel.
	c.	Panels covering control box and filters shall have molded composite handles while the blower access door shall have an integrated flange for easy removal.
	d.	Handles shall be UV modified, composite. permanently attached, and recessed into the panel.
	e.	Screws on the vertical portion of all removable access panel shall engage into heat resistant, molded composite collars.
	f.	Collars shall be removable and easily replaceable using manufacturer recommended parts.
		23 81 19.13.I.	Coils
	1.	Standard Aluminum Fin/Copper Tube Coils:
	a.	Standard evaporator and condenser coils shall have aluminum lanced plate fins mechanically bonded to seamless internally grooved 5/16” diameter copper tubes with all joints brazed.
	b.	Evaporator coils shall be leak tested to 150 psig, pressure tested to 450 psig, and qualified to UL 1995 burst test at 1775 psig.
	c.	Condenser coils shall be leak tested to 150 psig, pressure tested to 650 psig, and qualified to UL 1995 burst test at 1980 psig.
	2.	Optional Pre-coated aluminum-fin condenser coils:
	a.	Shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments.
	b.	Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube.
	c.	Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.
	d.	Corrosion durability of fin stock shall be confirmed through testing to be no less than 1000 hours salt spray per ASTM B117-90.
	e.	Corrosion durability of fin stock shall be confirmed through testing to have no visible corrosion after 48 hour immersion in a room temperature solution of 5% salt, 1% acetic acid.
	f.	Fin stock coating shall pass 2000 hours of the following: one week exposure in the prohesion chamber followed by one week in a QUV. Prohesion chamber: the solution shall contain 3.5% sodium chloride and 0.35% ammonium sulfate. The exposure cycle is one hour of salt fog application at ambient followed by one hour drying at 95°F (35°C).
	3.	Optional Copper-fin evaporator and condenser coils:
	a.	Shall be constructed of copper fins mechanically bonded to copper tubes and copper tube sheets.
	b.	Galvanized steel tube sheets shall not be acceptable.
	c.	A polymer strip shall prevent coil assembly from contacting the sheet metal coil pan to minimize potential for galvanic corrosion between coil and pan.
	d.	Corrosion durability of fin stock shall be confirmed through testing to be no less than 1000 hours salt spray per ASTM B117-90.
	e.	Corrosion durability of fin stock shall be confirmed through testing to have no visible corrosion after 48 hour immersion in a room temperature solution of 5% salt, 1% acetic acid. 
	f.	Fin stock coating shall pass 2000 hours of the following: one week exposure in the prohesion chamber followed by one week in a QUV. Prohesion chamber: the solution shall contain 3.5% sodium chloride and 0.35% ammonium sulfate. The exposure cycle is one hour of salt fog application at ambient followed by one hour drying at 95°F (35°C).
	4.	Optional E-coated aluminum-fin evaporator and condenser coils:
	a.	Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins.
	b.	Coating process shall ensure complete coil encapsulation of tubes, fins and headers.
	c.	Color shall be high gloss black with gloss per ASTM D523-89.
	d.	Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges.
	e.	Superior hardness characteristics of 2H per ASTM D3363-92A and cross-hatch adhesion of 4B-5B per ASTM D3359-93.
	f.	Impact resistance shall be up to 160 in.-lb (ASTM D2794-93).
	g.	Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92).
	h.	Corrosion durability shall be confirmed through testing to be no less than 1000 hours salt spray per ASTM B117-90.
		23 81 19.13.J.	Refrigerant Components
	1.	Refrigerant circuit shall include the following control, safety, and maintenance features:
	a.	Thermostatic Expansion Valve (TXV) shall help provide optimum performance across the entire operating range. Shall contain removable power element to allow change out of power element and bulb without removing the valve body.
	b.	Refrigerant filter drier.
	c.	Service gauge connections on suction and discharge lines.
	d.	Pressure gauge access through a specially designed screen on the side of the unit.
          e.  Single circuit design with tandem compressor and fully activated evaporator coil
	2.	Compressors
	a.	Models shall use one fully hermetic tandem scroll compressors optimized for comfort staging and IEER energy savings. 
	b.	Models shall be available with a single refrigerant circuit and three stage cooling operation on all models.
	c.	Compressor motors shall be cooled by refrigerant gas passing through motor windings.
	d.	Compressors shall be internally protected from high discharge temperature conditions.
	e.	Compressors shall be protected from an over-temperature and over-amperage conditions by an internal, motor overload device.
	f.	Compressor shall be factory mounted on rubber grommets.
	g.	Compressor motors shall have internal line break thermal, current overload and high pressure differential protection.
	h.	Crankcase heaters shall be standard on each compressor and deactivated whenever a compressor is in operation. 
		23 81 19.13.K.	Filter Section
	1.	Filters access is specified in the unit cabinet section of this specification.
	2.	Filters shall be held in place by a preformed slide out filter tray, facilitating easy removal and installation.
	3.	Shall consist of factory-installed, low velocity, throw-away 2-in. thick fiberglass filters.
	4.	Filters shall be standard, commercially available sizes.
	5.	Only one size filter per unit is allowed.
	6.	4-in filter capability is possible with a field installed pre-engineered slide out filter track accessory. 4-in filters are field furnished.
		23 81 19.13.L.	Evaporator Fan and Motor
	1.	Evaporator fan motor:
		a,   Shall have permanently lubricated bearings.
	b.	Shall have inherent automatic-reset thermal overload protection or circuit breaker.
	c.	Shall have a maximum continuous bhp rating for continuous duty operation; no safety factors above that rating shall be required.
	d.   Shall be Variable Frequency duty to match the three stage compression logic.
	e.   Shall contain motor shaft grounding ring to prevent electrical bearing fluting damage by safely divertin harmful shaft voltages and bearing currents to ground.
	2.	Variable Frequency Drive (VFD). For indoor fan motor Staged Air Volume (SAV) operation:
	a.	Shall be installed inside the unit cabinet, mounted, wired and tested.
	b.	Shall contain Electromagnetic Interference (EMI) frequency protection.
	c.	Insulated Gate Bi-Polar Transistors (IGBT) used to produce the output pulse width modulated (PWM) waveform, allowing for quiet motor operation.
	d.	Self-diagnostics with fault and power code LED indicator. Field accessory Display Kit available for further diagnostics and special setup applications.
	e.	RS485 capability standard.
	f.	Electronic thermal overload protection.
	g.	5% swinging chokes for harmonic reduction and improved power factor.
	h.	All printed circuit boards shall be conformal coated.
	i.	Shall not contain visual display to adjust internal setting. Only available as field installed kit.
	2.	Belt-driven Evaporator Fan:
	a.	Belt drive shall include an adjustable-pitch motor pulley and belt break protection system..
	b.	Shall use rigid pillow block bearing system with lubricate fittings at are accessible or lubrication line.
	c.	Blower fan shall be double-inlet type with forward-curved blades.
	d.	Shall be constructed from steel with a corrosion resistant finish and dynamically balanced.
		23 81 19.13.M.	Condenser Fans and Motors
	1.	Condenser fan motors:
	a.	Shall be a totally enclosed – multi-speed ECM motor.
	b.	Shall use permanently lubricated bearings.
	c.	Shall have inherent thermal overload protection with an automatic reset feature.
	d.	Shall use a shaft-down design.
	2.	Condenser Fans:
	a.	Shall be a direct-driven propeller type fan.
	b.	Shall have galvanized aluminum (galvalum) blades riveted to corrosion-resistant steel spiders and shall be dynamically balanced.
		23 81 19.13.N.	Special Features, Options and Accessories
	1.	Integrated EconoMi$er2 and EconoMi$er X standard leak rate models
	a.	Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.
	b.	Independent modules for vertical or horizontal return configuration shall be available. Vertical return modules shall be available as a factory installed option.
	c.	Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.
	d.	Shall include all hardware and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.
	e.	Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.
	f.	Standard leak rate models shall be equipped with leakage dampers, not to exceed 2% leakage at 1 in. wg pressure differential.
	g.	 Economizer controller on EconoMi$er X models shall be the Honeywell W7220 that provides:
	(1.)	2-line LCD interface screen for setup, configuration and troubleshooting
	(2.)	On-board Fault Detection and Diagnostics (FDD) that senses and alerts when the economizer is not operating properly, per California Title 24.  
	(3.)	Sensor failure loss of communication identification
	(4.)	Automatic sensor detection
	(5.)	Capabilities for use with multiple-speed indoor fan systems
	(6.)	Utilize digital sensors: Dry bulb and Enthalpy
	h.	Economizer controller on EconoMi$er2 models with RTU Open models shall be a 4-20mA design controlled directly by the RTU Open controller.  RTU Open meets California Title 24 Fault Detection & Diagnostic (FDD) requirements.
	i.	Shall be capable of introducing up to 100% outdoor air. 
	j.	Shall be equipped with a barometric relief damper capable of relieving up to 100% return air and contain seals that meet ASHRAE 90.1 requirements.
	k.	Shall be designed to close damper(s) during loss-of-power situations with spring return built into motor.
	l.	Dry bulb outdoor air temperature sensor shall be provided as standard.  Enthalpy sensor is also available on factory installed only.  Outdoor air sensor setpoint shall be adjustable and shall range from 40 to 100°F / 4 to 38°C.  Additional sensor options shall be available as accessories.
	m.	The economizer controller shall also provide control of an accessory power exhaust unit function.  Factory set at 100%, with a range of 0% to 100%.
	n.	The economizer shall maintain minimum airflow into the building during occupied period and provide design ventilation rate for full occupancy.
	o.	Dampers shall be completely closed when the unit is in the unoccupied mode
	p.	Economizer controller shall accept a 2-10 Vdc CO2 sensor input for IAQ/DCV control.  In this mode, dampers shall modulate the outdoor air damper to provide ventilation based on the sensor input.  
	q.	Compressor lockout temperature on W7220 is adjustable from -45 to 80F, set at a factory default of 32°F.  Others shall open at 35°F (2C) and closes at 50°F (10°C).
	r.	Actuator shall be direct coupled to economizer gear.  No linkage arms or control rods shall be acceptable.
	s.	Economizer controller shall provide indications when in free cooling mode, in the DCV mode, or the exhaust fan contact is closed
	2.	Integrated EconoMi$er2 and EconoMi$er X Ultra Low Leak rate models
	a.	Integrated, gear driven opposing modulating blade design type capable of simultaneous economizer and compressor operation.
	b.	Independent modules for vertical or horizontal return configuration shall be available. Vertical return modules shall be available as a factory installed option. 
	c.	Damper blades shall be galvanized steel with composite gears. Plastic or composite blades on intake or return shall not be acceptable.
	d.	Shall include all hardware and controls to provide free cooling with outdoor air when temperature and/or humidity are below setpoints.
	e.	Shall be equipped with gear driven dampers for both the outdoor ventilation air and the return air for positive air stream control.
	f.	Ultra Low Leak design meets California Title 24 section 140.4 and ASHRAE 90.1 requirements of 4cfm per sq. ft. on the outside dampers and 10cfm per sq. ft. on the return dampers.
	g.	Economizer controller on EconoMi$er X models shall be the Honeywell W7220 that provides:
	(1.)	2-line LCD interface screen for setup, configuration and troubleshooting
	(2.)	On-board Fault Detection and Diagnostics (FDD) that senses and alerts when the economizer is not operating properly, per California Title 24.  
	(3.)	Sensor failure loss of communication identification
	(4.)	Automatic sensor detection
	(5.)	Capabilities for use with multiple-speed indoor fan systems
	(6.)	Utilize digital sensors: Dry bulb and Enthalpy
	h.	Economizer controller on EconoMi$er2 models with RTU Open models shall be a 4-20mA design controlled directly by the RTU Open controller.  RTU Open meets California Title 24 Fault Detection & Diagnostic (FDD) requirements.
	i.	Shall be capable of introducing up to 100% outdoor air.  
	j.	Shall be equipped with a barometric relief damper capable of relieving up to 100% return air and contain seals that meet ASHRAE 90.1 requirements.  
	k.	Shall be designed to close damper(s) during loss-of-power situations with spring return built into motor.
	l.	Dry bulb outdoor air temperature sensor is also available on factory installed only.  Outdoor air sensor setpoint shall be adjustable and shall range from 40 to 100°F / 4 to 38°C.  Additional sensor options shall be available as accessories.  
	m.	The economizer controller shall also provide control of an accessory power exhaust unit function.  Factory set at 100%, with a range of 0% to 100%. 
	n.	The economizer shall maintain minimum airflow into the building during occupied period and provide design ventilation rate for full occupancy. 
	o.	Dampers shall be completely closed when the unit is in the unoccupied mode.
	p.	Economizer controller shall accept a 2-10 Vdc CO2 sensor input for IAQ/DCV control.  In this mode, dampers shall modulate the outdoor air damper to provide ventilation based on the sensor input.
	q.	Compressor lockout temperature on W7220 is adjustable from -45 F to 80 F, set at a factory default of 32°F.  Others shall open at 35°F (2C) and closes at 50°F (10°C).
	r.	Actuator shall be direct coupled to economizer gear.  No linkage arms or control rods shall be acceptable.
	s.	Economizer controller shall provide indications when in free cooling mode, in the DCV mode, or the exhaust fan contact is closed.
	3.	Condenser Coil Hail Guard Assembly
	a.	Shall protect against damage from hail.
	b.	Shall be louvered style design.
	4.	Unit-Mounted, Non-Fused Disconnect Switch:
	a.	Switch shall be factory-installed, internally mounted. 
	b.	National Electric Code (NEC) and ETL approved non-fused switch shall provide unit power shutoff. 
	c.	Shall be accessible from outside the unit
	d.	Shall provide local shutdown and lockout capability
	e.	Sized only for the unit as ordered from the factory. Does not accommodate field installed devices
	5.	HACR Breaker
	a.	These manual reset devices provide overload and short circuit protection for the unit. Factory wired and mounted with the units, with access cover to help provide environmental protection. On 575V applications, HACR breaker can only be used with WYE power distribution systems. Use on Delta power distribution systems is prohibited.
	b.	Sized only for the unit as ordered from the factory. Does not accommodate field installed devices
	6.	Convenience Outlet:
	a.	Powered convenience outlet.
	(1.)	Outlet shall be powered from main line power to the rooftop unit.
	(2.)	Outlet shall be powered from line side of disconnect by installing contractor, as required by code. If outlet is powered from load side of disconnect, unit electrical ratings shall be ETL certified and rated for additional outlet amperage.
	(3.)	Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle. 
	(4.)	Outlet shall include 15 amp GFI receptacles with independent fuse protection. 
	(5.)	Voltage required to operate convenience outlet shall be provided by a factory-installed step-down transformer. 
	(6.)	Outlet shall be accessible from outside the unit.
	(7.)	Outlet shall include a field-installed “Wet in Use” cover.
	b.	Non-Powered convenience outlet.
	(1.)	Outlet shall be powered from a separate 115/120v power source.
	(2.)	A transformer shall not be included.
	(3.)	Outlet shall be factory-installed and internally mounted with easily accessible 115-v female receptacle.
	(4.)	Outlet shall include 15 amp GFI receptacles with independent fuse protection. 
	(5.)	Outlet shall be accessible from outside the unit.
	(6.)	Outlet shall include a field-installed “Wet in Use” cover.
	7.	Fan/Filter Status Switch:
	a.	Switch shall provide status of indoor evaporator fan (ON/OFF) or filter (CLEAN/DIRTY).
	b.	Status shall be displayed either over communication bus (when used with direct digital controls) or with an indicator light at the thermostat.
	8.	Centrifugal Power Exhaust:
	a.	Power exhaust shall be used in conjunction with an integrated economizer. 
	b.	Independent modules for vertical or horizontal return configurations shall be available.
	c.	Horizontal power exhaust is shall be mounted in return ductwork.
	d.	Power exhaust shall be controlled by economizer controller operation. Exhaust fans shall be energized when dampers open past the 0-100% adjustable setpoint on the economizer control. 
	9.	Roof Curbs (Vertical):
	a.	Full perimeter roof curb with exhaust capability providing separate air streams for energy recovery from the exhaust air without supply air contamination.
	b.	Formed galvanized steel with wood nailer strip and shall be capable of supporting entire unit weight.
	c.	Permits installation and securing of ductwork to curb prior to mounting unit on the curb.
	10.	High-Static Indoor Fan Motor(s) and Drive(s):
	a.	High-static motor(s) and drive(s) shall be factory-installed to provide additional performance range.
	11.	Outdoor Air Enthalpy Sensor:
	a.	The outdoor air enthalpy sensor shall be used to provide single enthalpy control. When used in conjunction with a return air enthalpy sensor, the unit will provide differential enthalpy control. The sensor allows the unit to determine if outside air is suitable for free cooling.
	12.	Return Air Enthalpy Sensor:
	a.	The return air enthalpy sensor shall be used in conjunction with an outdoor air enthalpy sensor to provide differential enthalpy control.
	13.	Indoor Air Quality (CO2) Sensor:
	a.	Shall be able to provide demand ventilation indoor air quality (IAQ) control.
	b.	The IAQ sensor shall be available in duct mount, wall mount, or wall mount with LED display. The setpoint shall have adjustment capability.
	14.	Smoke detectors:
	a.	Shall be a Four-Wire Controller and Detector.
	b.	Shall be environmental compensated with differential sensing for reliable, stable, and drift-free sensitivity.
	c.	Shall use magnet-activated test/reset sensor switches.
	d.	Shall have tool-less connection terminal access.
	e.	Shall have a recessed momentary switch for testing and resetting the detector.
	f.	Controller shall include:
	(1.)	One set of normally open alarm initiation contacts for connection to an initiating device circuit on a fire alarm control panel.
	(2.)	Two Form-C auxiliary alarm relays for interface with rooftop unit or other equipment.
	(3.)	One Form-C supervision (trouble) relay to control the operation of the Trouble LED on a remote test/reset station.
	(4.)	Capable of direct connection to two individual detector modules.
	(5.)	Can be wired to up to 14 other duct smoke detectors for multiple fan shutdown applications.
	15.	Time Guard
	a.	Shall prevent compressor short cycling by providing a 5-minute delay (±2 minutes) before restarting a compressor after shutdown for any reason.
	b.	One device shall be required per compressor.
	16.	Electric Heat:
	a.	Heating Section
	(1.)	Heater element open coil resistance wire, nickel-chrome alloy, 0.29 inches inside diameter, strung through ceramic insulators mounted on metal frame. Coil ends are staked and welded to terminal screw slots.
	(2.)	Heater assemblies are provided with integral fusing for protection of internal heater circuits not exceeding 48 amps each. Auto reset thermo limit controls, magnetic heater contactors (24 v coil) and terminal block all mounted in electric heater control box (minimum 18 ga galvanized steel) attached to end of heater assembly.
	17.	Barometric Hood (Horizontal Economizer Applications)
	a.	Shall be required when a horizontal economizer and barometric relief are required. Barometric relief damper must be installed in the return air (horizontal) duct work. This hood provides weather protection.
	18.	Hinged Access Panels
	a.	Shall provide easy access through integrated quarter turn latches.
	b.	Shall be on major panels of – filter, control box, fan motor and compressor
	19.	Display Kit for Variable Frequency Drive
	a.	Kit allows the ability to access the VFD controller programs to provide special setup capabilities and diagnostics.
	b.	Kit contains display module, mounting bracket and communication cable.
	c.	Display Kit can be permanently installed in the unit or used on any SAV system VFD controller as needed.
	20.	Thermostat:
	a.	Due to the three stage cooling capacity design of these units, a three stage cooling thermostat is required for the unit to perform at listed operating efficiencies.
	b.	Carrier offers a Honeywell branded T7350D (3 Cool/3 Heat) Commercial Programmable Thermostat. This provides:
	-	7-day programmable 365-day clock with holiday programming
	-	Automatic Daylight Saving Time adjustment
	-	Backlit display
	-	Changeover selections: automatic or manual 
	-	Fan configurable: continuous or intermittent during occupied
	21.	Humidi-MiZer Adaptive Dehumidification System:
	a.	The Humidi-MiZer Adaptive Dehumidification System shall be factory installed, certified and tested to provide greater dehumidification of the occupied space by providing two distinct modes of dehumidification operation in addition to its normal design cooling mode:
	(1.)	Subcooling mode further sub cools the hot liquid refrigerant leaving the condenser coil as well as reheat leaving air stream. It can provide both better cooling capacity as well as dehumidification process when both temperature and humidity in the space are not satisfied.

Replaces: GS-50LC-14-26-02PD

Catalog No: GS-50LC-14-26-03PD

Catalog No:  48TC-17-30-V-01PD

Copyright 2014 Carrier Corp. D 7310 W. Morris St. D Indianapolis, IN  46231                   Edition Date: 05/14

Copyright 2013 Carrier Corp. D  7310 W. Morris St. D  Indianapolis, IN  46231                        Edition Date: 12/13

Manufacturer reserves the right to change, at any time, specifications and designs without notice and without obligations.